## Sheet1
BACnet Points List AXM-WEB2
Firmware v1.39c (released 2026-08-27). List generated 2026-10-06 from firmware source.
Object ID | Object Name | Object Description | Object Type | Units
Metering Parameters
1 | Frequency | Frequency | Analog Input | Hz
2 | Phase A Voltage | Phase A Voltage | Analog Input | V
3 | Phase B Voltage | Phase B Voltage | Analog Input | V
4 | Phase C Voltage | Phase C Voltage | Analog Input | V
5 | Average Voltage | Average Voltage | Analog Input | V
6 | Line Voltage AB | Line Voltage AB | Analog Input | V
7 | Line Voltage BC | Line Voltage BC | Analog Input | V
8 | Line Voltage CA | Line Voltage CA | Analog Input | V
9 | Average Line Voltage | Average Line Voltage | Analog Input | V
10 | Phase A Current | Phase A Current | Analog Input | A
11 | Phase B Current | Phase B Current | Analog Input | A
12 | Phase C Current | Phase C Current | Analog Input | A
13 | Average Current | Average Current | Analog Input | A
14 | Neutral Current | Neutral Current | Analog Input | A
15 | Phase A Active Power | Phase A Active Power | Analog Input | kW
16 | Phase B Active Power | Phase B Active Power | Analog Input | kW
17 | Phase C Active Power | Phase C Active Power | Analog Input | kW
18 | Total Active Power | Total Active Power | Analog Input | kW
19 | Phase A Reactive Power | Phase A Reactive Power | Analog Input | kvar
20 | Phase B Reactive Power | Phase B Reactive Power | Analog Input | kvar
21 | Phase C Reactive Power | Phase C Reactive Power | Analog Input | kvar
22 | Total Reactive Power | Total Reactive Power | Analog Input | kvar
23 | Phase A Apparent Power | Phase A Apparent Power | Analog Input | kVA
24 | Phase B Apparent Power | Phase B Apparent Power | Analog Input | kVA
25 | Phase C Apparent Power | Phase C Apparent Power | Analog Input | kVA
26 | Total Apparent Power | Total Apparent Power | Analog Input | kVA
27 | Phase A Power Factor | Phase A Power Factor | Analog Input | PF
28 | Phase B Power Factor | Phase B Power Factor | Analog Input | PF
29 | Phase C Power Factor | Phase C Power Factor | Analog Input | PF
30 | Total Power Factor | Total Power Factor | Analog Input | PF
31 | Voltage Unbalance Factor | Voltage Unbalance Factor | Analog Input | %
32 | Current Unbalance Factor | Current Unbalance Factor | Analog Input | %
33 | Load Type | Load Type | Analog Input | no units
Demand Parameters
34 | Active Power Demand | Active Power Demand | Analog Input | kW
35 | Reactive Power Demand | Reactive Power Demand | Analog Input | kvar
36 | Apparent Power Demand | Apparent Power Demand | Analog Input | kVA
37 | Phase A Current Demand | Phase A Current Demand | Analog Input | A
38 | Phase B Current Demand | Phase B Current Demand | Analog Input | A
39 | Phase C Current Demand | Phase C Current Demand | Analog Input | A
Energy Parameters
40 | Import Active Energy | Import Active Energy | Analog Input | kWh
41 | Export Active Energy | Export Active Energy | Analog Input | kWh
42 | Import Reactive Energy | Import Reactive Energy | Analog Input | kvarh
43 | Export Reactive Energy | Export Reactive Energy | Analog Input | kvarh
44 | Energy Total | Energy Total | Analog Input | kWh
45 | Energy Net | Energy Net | Analog Input | kWh
46 | Reactive Energy Total | Reactive Energy Total | Analog Input | kvarh
47 | Reactive Energy Net | Reactive Energy Net | Analog Input | kvarh
48 | Apparent Energy | Apparent Energy | Analog Input | kVAh
49 | Phase A Import Active Energy | Phase A Import Active Energy | Analog Input | kWh
50 | Phase A Export Active Energy | Phase A Export Active Energy | Analog Input | kWh
51 | Phase B Import Active Energy | Phase B Import Active Energy | Analog Input | kWh
52 | Phase B Export Active Energy | Phase B Export Active Energy | Analog Input | kWh
53 | Phase C Import Active Energy | Phase C Import Active Energy | Analog Input | kWh
54 | Phase C Export Active Energy | Phase C Export Active Energy | Analog Input | kWh
55 | Phase A Import Reactive Energy | Phase A Import Reactive Energy | Analog Input | kvarh
56 | Phase A Export Reactive Energy | Phase A Export Reactive Energy | Analog Input | kvarh
57 | Phase B Import Reactive Energy | Phase B Import Reactive Energy | Analog Input | kvarh
58 | Phase B Export Reactive Energy | Phase B Export Reactive Energy | Analog Input | kvarh
59 | Phase C Import Reactive Energy | Phase C Import Reactive Energy | Analog Input | kvarh
60 | Phase C Export Reactive Energy | Phase C Export Reactive Energy | Analog Input | kvarh
61 | Phase A Apparent Energy | Phase A Apparent Energy | Analog Input | kVAh
62 | Phase B Apparent Energy | Phase B Apparent Energy | Analog Input | kVAh
63 | Phase C Apparent Energy | Phase C Apparent Energy | Analog Input | kVAh
Power Quality Parameters
64 | Phase A Voltage THD | Phase A Voltage THD | Analog Input | %
65 | Phase B Voltage THD | Phase B Voltage THD | Analog Input | %
66 | Phase C Voltage THD | Phase C Voltage THD | Analog Input | %
67 | Average Voltage THD | Average Voltage THD | Analog Input | %
68 | Phase A Current THD | Phase A Current THD | Analog Input | %
69 | Phase B Current THD | Phase B Current THD | Analog Input | %
70 | Phase C Current THD | Phase C Current THD | Analog Input | %
71 | Average Current THD | Average Current THD | Analog Input | %
Demand Parameters (Maximum)
72 | Input Channel 1 Active Power Demand kW | Max Phase A Active Power demand | Analog Input | kW
73 | Input Channel 2 Active Power Demand kW | Max Phase B Active Power demand | Analog Input | kW
74 | Input Channel 3 Active Power Demand kW | Max Phase C Active Power demand | Analog Input | kW
75 | Input Channel 1 Reactive Power Demand kvar | Max Phase A Reactive Power demand | Analog Input | kvar
76 | Input Channel 2 Reactive Power Demand kvar | Max Phase B Reactive Power demand | Analog Input | kvar
77 | Input Channel 3 Reactive Power Demand kvar | Max Phase C Reactive Power demand | Analog Input | kvar
78 | Input Channel 1 Apparent Power Demand kVA | Max Phase A Apparent Power Demand | Analog Input | kVA
79 | Input Channel 2 Apparent Power Demand kVA | Max Phase B Apparent Power Demand | Analog Input | kVA
80 | Input Channel 3 Apparent Power Demand kVA | Max Phase C Apparent Power Demand | Analog Input | kVA
81 | Active Power Demand kW | Max System Active Power demand | Analog Input | kW
82 | Reactive Power Demand kvar | Max System Reactive Power Demand | Analog Input | kvar
83 | Apparent Power Demand kVA | Max System Apparent Power Demand | Analog Input | kVA
I/O Module - Analog Inputs / Analog Outputs
1001 | IO21-AO1 | IO21-AO1 | Analog Input | mA or V
1002 | IO21-AO2 | IO21-AO2 | Analog Input | mA or V
1003 | IO22-AO1 | IO22-AO1 | Analog Input | mA or V
1004 | IO22-AO2 | IO22-AO2 | Analog Input | mA or V
1005 | IO31-AI1 | IO31-AI1 | Analog Input | mA or V
1006 | IO31-AI2 | IO31-AI2 | Analog Input | mA or V
1007 | IO32-AI1 | IO32-AI1 | Analog Input | mA or V
1008 | IO32-AI2 | IO32-AI2 | Analog Input | mA or V
I/O Module - Digital Input Counters
2001 | IO11-DI1-COUNTER | IO11-DI1-COUNTER | Analog Input | none (0)
2002 | IO11-DI2-COUNTER | IO11-DI2-COUNTER | Analog Input | none (0)
2003 | IO11-DI3-COUNTER | IO11-DI3-COUNTER | Analog Input | none (0)
2004 | IO11-DI4-COUNTER | IO11-DI4-COUNTER | Analog Input | none (0)
2005 | IO11-DI5-COUNTER | IO11-DI5-COUNTER | Analog Input | none (0)
2006 | IO11-DI6-COUNTER | IO11-DI6-COUNTER | Analog Input | none (0)
2007 | IO21-DI1-COUNTER | IO21-DI1-COUNTER | Analog Input | none (0)
2008 | IO21-DI2-COUNTER | IO21-DI2-COUNTER | Analog Input | none (0)
2009 | IO21-DI3-COUNTER | IO21-DI3-COUNTER | Analog Input | none (0)
2010 | IO21-DI4-COUNTER | IO21-DI4-COUNTER | Analog Input | none (0)
2011 | IO31-DI1-COUNTER | IO31-DI1-COUNTER | Analog Input | none (0)
2012 | IO31-DI2-COUNTER | IO31-DI2-COUNTER | Analog Input | none (0)
2013 | IO31-DI3-COUNTER | IO31-DI3-COUNTER | Analog Input | none (0)
2014 | IO31-DI4-COUNTER | IO31-DI4-COUNTER | Analog Input | none (0)
2015 | IO12-DI1-COUNTER | IO12-DI1-COUNTER | Analog Input | none (0)
2016 | IO12-DI2-COUNTER | IO12-DI2-COUNTER | Analog Input | none (0)
2017 | IO12-DI3-COUNTER | IO12-DI3-COUNTER | Analog Input | none (0)
2018 | IO12-DI4-COUNTER | IO12-DI4-COUNTER | Analog Input | none (0)
2019 | IO12-DI5-COUNTER | IO12-DI5-COUNTER | Analog Input | none (0)
2020 | IO12-DI6-COUNTER | IO12-DI6-COUNTER | Analog Input | none (0)
2021 | IO22-DI1-COUNTER | IO22-DI1-COUNTER | Analog Input | none (0)
2022 | IO22-DI2-COUNTER | IO22-DI2-COUNTER | Analog Input | none (0)
2023 | IO22-DI3-COUNTER | IO22-DI3-COUNTER | Analog Input | none (0)
2024 | IO22-DI4-COUNTER | IO22-DI4-COUNTER | Analog Input | none (0)
2025 | IO32-DI1-COUNTER | IO32-DI1-COUNTER | Analog Input | none (0)
2026 | IO32-DI2-COUNTER | IO32-DI2-COUNTER | Analog Input | none (0)
2027 | IO32-DI3-COUNTER | IO32-DI3-COUNTER | Analog Input | none (0)
2028 | IO32-DI4-COUNTER | IO32-DI4-COUNTER | Analog Input | none (0)
Binary Input Objects
I/O Module - Digital Input Status
1 | IO11-DI1 | IO11-DI1 | Binary Input | -
2 | IO11-DI2 | IO11-DI2 | Binary Input | -
3 | IO11-DI3 | IO11-DI3 | Binary Input | -
4 | IO11-DI4 | IO11-DI4 | Binary Input | -
5 | IO11-DI5 | IO11-DI5 | Binary Input | -
6 | IO11-DI6 | IO11-DI6 | Binary Input | -
7 | IO21-DI1 | IO21-DI1 | Binary Input | -
8 | IO21-DI2 | IO21-DI2 | Binary Input | -
9 | IO21-DI3 | IO21-DI3 | Binary Input | -
10 | IO21-DI4 | IO21-DI4 | Binary Input | -
11 | IO31-DI1 | IO31-DI1 | Binary Input | -
12 | IO31-DI2 | IO31-DI2 | Binary Input | -
13 | IO31-DI3 | IO31-DI3 | Binary Input | -
14 | IO31-DI4 | IO31-DI4 | Binary Input | -
15 | IO12-DI1 | IO12-DI1 | Binary Input | -
16 | IO12-DI2 | IO12-DI2 | Binary Input | -
17 | IO12-DI3 | IO12-DI3 | Binary Input | -
18 | IO12-DI4 | IO12-DI4 | Binary Input | -
19 | IO12-DI5 | IO12-DI5 | Binary Input | -
20 | IO12-DI6 | IO12-DI6 | Binary Input | -
21 | IO22-DI1 | IO22-DI1 | Binary Input | -
22 | IO22-DI2 | IO22-DI2 | Binary Input | -
23 | IO22-DI3 | IO22-DI3 | Binary Input | -
24 | IO22-DI4 | IO22-DI4 | Binary Input | -
25 | IO32-DI1 | IO32-DI1 | Binary Input | -
26 | IO32-DI2 | IO32-DI2 | Binary Input | -
27 | IO32-DI3 | IO32-DI3 | Binary Input | -
28 | IO32-DI4 | IO32-DI4 | Binary Input | -
Alarm Channel Status
29 | Alarm Channel 1 Status | Alarm Channel 1 Status | Binary Input | -
30 | Alarm Channel 2 Status | Alarm Channel 2 Status | Binary Input | -
31 | Alarm Channel 3 Status | Alarm Channel 3 Status | Binary Input | -
32 | Alarm Channel 4 Status | Alarm Channel 4 Status | Binary Input | -
33 | Alarm Channel 5 Status | Alarm Channel 5 Status | Binary Input | -
34 | Alarm Channel 6 Status | Alarm Channel 6 Status | Binary Input | -
35 | Alarm Channel 7 Status | Alarm Channel 7 Status | Binary Input | -
36 | Alarm Channel 8 Status | Alarm Channel 8 Status | Binary Input | -
37 | Alarm Channel 9 Status | Alarm Channel 9 Status | Binary Input | -
38 | Alarm Channel 10 Status | Alarm Channel 10 Status | Binary Input | -
39 | Alarm Channel 11 Status | Alarm Channel 11 Status | Binary Input | -
40 | Alarm Channel 12 Status | Alarm Channel 12 Status | Binary Input | -
41 | Alarm Channel 13 Status | Alarm Channel 13 Status | Binary Input | -
42 | Alarm Channel 14 Status | Alarm Channel 14 Status | Binary Input | -
43 | Alarm Channel 15 Status | Alarm Channel 15 Status | Binary Input | -
44 | Alarm Channel 16 Status | Alarm Channel 16 Status | Binary Input | -

## Notes
Notes
Source:
AXM-WEB2 firmware v1.39c (tag v1.39c, 2026-08-27). Objects are defined in the firmware BACnet object catalog (analogInputCatalog.h / binaryInputCatalog.h, generated from bacNetConf.xml).
Object counts:
Analog Input: 119 objects (instances 1-83, 1001-1008, 2001-2028)
Binary Input: 44 objects (instances 1-44)
Availability:
I/O module objects are only created when the corresponding I/O module is enabled: AI 1001-1008 require IO21/IO22 (AO) or IO31/IO32 (AI); AI 2001-2028 require the DI channel to be configured as a pulse counter; BI 1-28 require the DI module (IO11/IO12/IO21/IO22/IO31/IO32).
BI 29-44 (Alarm Channel Status) are only created when the attached meter supports alarm channel status.
Units for AI 1001-1008 follow the I/O module AI/AO type setting: milliamperes (2) for 0-20 mA / 4-20 mA, volts (5) for voltage mode.
Default COV increment is 0 for every Analog Input; COV_Increment and Description are writable and persisted.
Units (BACnet Engineering Units enumeration):
square-meters (0)* -> shown as "none (0)"
amperes (3) -> shown as "A"
volts (5) -> shown as "V"
kilovolt-amperes (9) -> shown as "kVA"
kilovolt-amperes-reactive (12) -> shown as "kvar"
power-factor (15) -> shown as "PF"
kilowatt-hours (19) -> shown as "kWh"
hertz (27) -> shown as "Hz"
kilowatts (48) -> shown as "kW"
no-units (95) -> shown as "no units"
percent (98) -> shown as "%"
kilovolt-ampere-hours (240) -> shown as "kVAh"
kilovolt-ampere-hours-reactive (243) -> shown as "kvarh"
* AI 2001-2028 (DI counters) report engineering-units code 0.