## Version history
Version | Changes | Date | External Firmware Version
v1.01 | Inherits the Modbus address table of the AcuDC-260 series. | 2025-07-02 | /
v1.02 | This firmware is the initial release and includes all product-defined features. | 2025-12-09 | v1.02p04
| Update the Baisc Configuration and add the contents for new requirement. o AcuDC-262-1000V-A1 o AcuDC-262-1000V-A2 o AcuDC-262-1000V-A3 Default value of week is set to 6(Weekday for 2000/1/1 is 6) | 2026-01-06 | v1.02p07

## Overview
Block | Sector | Sheet | Start | End | Length(reg num) | Comment
Basic Meter Settings | Basic Meter Settings | Basic Configuration | 0x1000 | 0x103A | 59
Real-Time Clock | Real-Time Clock | Basic Configuration | 0x103F | 0x1045 | 7
Real-Time Parameters (float) | Real-Time Parameters (float) | Readings | 0x3000 | 0x301F | 32
Real-Time Parameters (int) | Real-Time Parameters (int) | Readings | 0x3200 | 0x320F | 16
Energy and Charge (double) | Energy and Charge (double) | Readings | 0x4000 | 0x405F | 96
Max | Max | Max/Min | 0x4136 | 0x41B0 | 123
Min | Min | Max/Min | 0x41E5 | 0x4234 | 80
Custom Reading | Custom Reading | Basic Configuration | 0x6A00 | 0x6A27 | 40
Custom Reading Settings | Custom Reading Settings | Basic Configuration | 0x6B00 | 0x6B28 | 41

## Basic Configuration
| Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg Num | Range | Default
Basic Meter Settings | 0x1000 | 0x1000 | 4096 | 4096 | Meter password | uint16_t | R/W | 1 | 0－9999 | 0
| 0x1001 | 0x1001 | 4097 | 4097 | RS485 baud rate | uint16_t | R/W | 1 | 2400; 4800; 9600; 19200; 38400; 57600; 7680 (76800); 11520 (115200) | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | RS485 parity | uint16_t | R/W | 1 | 0：even 1：odd 2：Non2 3：Non1 | 0
| 0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | uint16_t | R/W | 1 | 0: manual 1: DHCP | 0
| 0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte (high) IP address 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte (high) IP address 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte (high) Subnet mask 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 255 255 255 0
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte (high) Subnet mask 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte (high) Gateway 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 192. 168. 1 .1
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte (high) Gateway 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte (high) DNS primary server 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 8. 8 .8 .8
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte (high) DNS primary server 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte (high) DNS secondary server 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 8.8.4.4
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte (high) DNS secondary server 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1
| 0x100F | 0x100F | 4111 | 4111 | Modbus RTU Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | uint16_t | R/W | 1 | 1-65534 | 502
| 0x1012 | 0x1012 | 4114 | 4114 | PT1 | uint16_t | R/W | 1 | fixed as 1000 for now | 1000
| 0x1013 | 0x1013 | 4115 | 4115 | PT2 | uint16_t | R/W | 1 | fixed as 1000 for now
| 0x1014 | 0x1014 | 4116 | 4116 | Current1 Sensor Nominal Primary Input | uint16_t | R/W | 1 | 20 - 50000 A | 50
| 0x1015 | 0x1015 | 4117 | 4117 | Current1 Sensor Secondary Output Max of type A1(0~100mv) | uint16_t | R/W | 1 | 5-100 (mV) | 75
| 0x1016 | 0x1016 | 4118 | 4118 | Demand calculation method | uint16_t | R/W | 1 | 0: Fixed block 1: Sliding block | 1
| 0x1017 | 0x1017 | 4119 | 4119 | Demand window time | uint16_t | R/W | 1 | 1~30 | 15
| 0x1018 | 0x1018 | 4120 | 4120 | Demand update period | uint16_t | R/W | 1 | 1~30 | 1
| 0x1019 | 0x1019 | 4121 | 4121 | Energy pulse parameter | uint16_t | R/W | 1 | 0: None 1: Energy 2: Charge | 0
| 0x101A | 0x101A | 4122 | 4122 | Energy pulse type | uint16_t | R/W | 1 | 0: EV_IMPORT, 1: EV_EXPORT, 2: EV_NET, // Imp - Exp 3: EV_TOTAL, // Imp + Exp | 0
| 0x101B | 0x101B | 4123 | 4123 | Energy reading type | uint16_t | R/W | 1 | 0: Primary 1: Secondary | 0
| 0x101C | 0x101C | 4124 | 4124 | Real-time reading type | uint16_t | R/W | 1 | 0: Secondary 1: Primary | 0
| 0x101D | 0x101D | 4125 | 4125 | Clear demand | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x101E | 0x101E | 4126 | 4126 | Clear max/min | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x101F | 0x101F | 4127 | 4127 | Clear device run time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1020 | 0x1020 | 4128 | 4128 | Clear energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1021 | 0x1021 | 4129 | 4129 | Factory reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
| 0x1022 | 0x1022 | 4130 | 4130 | Backlight time | uint16_t | R/W | 1 | 0－120 | 0
| 0x1023 | 0x1023 | 4131 | 4131 | Seal status | uint16_t | R | 1 | Sealed: 0x0A | 0
| 0x1024 | 0x1024 | 4132 | 4132 | Device run time (high 16 bits) | uint16_t | R | 1
| 0x1025 | 0x1025 | 4133 | 4133 | Device run time (low 16 bits) | uint16_t | R | 1
| 0x1026 | 0x1026 | 4134 | 4134 | Clear charge | uint16_t | R/W | 1 | 0: None 1: Clearing
| 0x1027 | 0x1027 | 4135 | 4135 | Network reset | uint16_t | R/W | 1 | 0: None 1: Resetting
| 0x1028 | 0x1028 | 4136 | 4136 | Current2 Sensor Nominal Primary Input | uint16_t | R/W | 1 | 20 - 50000 A | 50
| 0x1029 | 0x1029 | 4137 | 4137 | Current2 Sensor Secondary Output Max of type A1(0~100mv) | uint16_t | R/W | 1 | 5-100 (mV) | 75
| 0x102A | 0x102A | 4138 | 4138 | Device load time (high 16 bits) | uint16_t | R | 1
| 0x102B | 0x102B | 4139 | 4139 | Device load time (low 16 bits) | uint16_t | R | 1
| 0x102C | 0x102C | 4140 | 4140 | Clear load time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x102D | 0x102D | 4141 | 4141 | Enable cable loss compensation | uint16_t | R/W | 1 | 0: Disable 1: Enable | 0
| 0x102E | 0x102E | 4142 | 4142 | Cable 1 resistance (high 16 bits) | uint16_t | R/W | 1 | 0 ~ 9999999 | 0
| 0x102F | 0x102F | 4143 | 4143 | Cable 1 resistance (low 16 bits) | uint16_t | R/W | 1 | 0 ~ 9999999 | 0
| 0x1030 | 0x1030 | 4144 | 4144 | Cable 2 resistance (high 16 bits) | uint16_t | R/W | 1 | 0 ~ 9999999 | 0
| 0x1031 | 0x1031 | 4145 | 4145 | Cable 2 resistance (low 16 bits) | uint16_t | R/W | 1 | 0 ~ 9999999 | 0
| 0x1032 | 0x1033 | 4146 | 4147 | Energy pulse constant | uint16_t | R/W | 2 | 1 - 50000000 (0.0001 - 5000) | 1000000 (100)
| 0x1034 | 0x1034 | 4148 | 4148 | Pulse Channel ID | uint16_t | R/W | 1 | 0: Ch1 1: Ch2 2: Sum
| 0x1035 | 0x1035 | 4149 | 4149 | Current1 Sensor Measurement Direction of type A2(4mA~20mA Hall sensor) and type A3(-5V to 5V hall sensor) | uint16_t | R/W | 1 | 0x0000 - None 0x0001 - Unipolar 0x0002 - Mid-bias bipolar 0x0003 - true bipolar | 0x0000
| 0x1036 | 0x1036 | 4150 | 4150 | Current2 Sensor Measurement Direction of type A2(4mA~20mA Hall sensor) and type A3(-5V to 5V hall sensor) | uint16_t | R/W | 1 | 0x0000 - None 0x0001 - Unipolar 0x0002 - Mid-bias bipolar 0x0003 - true bipolar | 0x0000
| 0x1037 | 0x1037 | 4151 | 4151 | Current1 Sensor Secondary Output Min of tyep A3 | uint16_t | R/W | 1 | (Reg value) / 10 | 0
| 0x1038 | 0x1038 | 4152 | 4152 | Current1 Sensor Secondary Output Max of tyep A3 | uint16_t | R/W | 1 | (Reg value) / 10 | 50
| 0x1039 | 0x1039 | 4153 | 4153 | Current2 Sensor Secondary Output Min of tyep A3 | uint16_t | R/W | 1 | (Reg value) / 10 | 0
| 0x103A | 0x103A | 4154 | 4154 | Current2 Sensor Secondary Output Max of tyep A3 | uint16_t | R/W | 1 | (Reg value) / 10 | 50
Real-time clock | 0x103F | 0x103F | 4159 | 4159 | Week | uint16_t | R/W | 1 | 1~7 | 6
| 0x1040 | 0x1040 | 4160 | 4160 | Year | uint16_t | R/W | 1 | 2000~2099 | 2000
| 0x1041 | 0x1041 | 4161 | 4161 | Month | uint16_t | R/W | 1 | 1~12 | 1
| 0x1042 | 0x1042 | 4162 | 4162 | Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x1043 | 0x1043 | 4163 | 4163 | Hour | uint16_t | R/W | 1 | 0~23 | 0
| 0x1044 | 0x1044 | 4164 | 4164 | Minute | uint16_t | R/W | 1 | 0~59 | 0
| 0x1045 | 0x1045 | 4165 | 4165 | Second | uint16_t | R/W | 1 | 0~59 | 0
Custom reading settings | 0x6B00 | 0x6B00 | 27392 | 27392 | Number of byte set | uint16_t | R | 1 |  | 0
| 0x6B01 | 0x6B01 | 27393 | 27393 | 1st reading | uint16_t | R/W | 1 |  | 0
| 0x6B02 | 0x6B02 | 27394 | 27394 | 2nd reading | uint16_t | R/W | 1 |  | 0
| 0x6B03 | 0x6B03 | 27395 | 27395 | 3rd reading | uint16_t | R/W | 1 |  | 0
| 0x6B04 | 0x6B04 | 27396 | 27396 | 4th reading | uint16_t | R/W | 1 |  | 0
| 0x6B05 | 0x6B05 | 27397 | 27397 | 5th reading | uint16_t | R/W | 1 |  | 0
| 0x6B06 | 0x6B06 | 27398 | 27398 | 6th reading | uint16_t | R/W | 1 |  | 0
| 0x6B07 | 0x6B07 | 27399 | 27399 | 7th reading | uint16_t | R/W | 1 |  | 0
| 0x6B08 | 0x6B08 | 27400 | 27400 | 8th reading | uint16_t | R/W | 1 |  | 0
| 0x6B09 | 0x6B09 | 27401 | 27401 | 9th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0A | 0x6B0A | 27402 | 27402 | 10th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0B | 0x6B0B | 27403 | 27403 | 11th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0C | 0x6B0C | 27404 | 27404 | 12th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0D | 0x6B0D | 27405 | 27405 | 13th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0E | 0x6B0E | 27406 | 27406 | 14th reading | uint16_t | R/W | 1 |  | 0
| 0x6B0F | 0x6B0F | 27407 | 27407 | 15th reading | uint16_t | R/W | 1 |  | 0
| 0x6B10 | 0x6B10 | 27408 | 27408 | 16th reading | uint16_t | R/W | 1 |  | 0
| 0x6B11 | 0x6B11 | 27409 | 27409 | 17th reading | uint16_t | R/W | 1 |  | 0
| 0x6B12 | 0x6B12 | 27410 | 27410 | 18th reading | uint16_t | R/W | 1 |  | 0
| 0x6B13 | 0x6B13 | 27411 | 27411 | 19th reading | uint16_t | R/W | 1 |  | 0
| 0x6B14 | 0x6B14 | 27412 | 27412 | 20th reading | uint16_t | R/W | 1 |  | 0
| 0x6B15 | 0x6B15 | 27413 | 27413 | 21st reading | uint16_t | R/W | 1 |  | 0
| 0x6B16 | 0x6B16 | 27414 | 27414 | 22nd reading | uint16_t | R/W | 1 |  | 0
| 0x6B17 | 0x6B17 | 27415 | 27415 | 23rd reading | uint16_t | R/W | 1 |  | 0
| 0x6B18 | 0x6B18 | 27416 | 27416 | 24th reading | uint16_t | R/W | 1 |  | 0
| 0x6B19 | 0x6B19 | 27417 | 27417 | 25th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1A | 0x6B1A | 27418 | 27418 | 26th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1B | 0x6B1B | 27419 | 27419 | 27th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1C | 0x6B1C | 27420 | 27420 | 28th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1D | 0x6B1D | 27421 | 27421 | 29th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1E | 0x6B1E | 27422 | 27422 | 30th reading | uint16_t | R/W | 1 |  | 0
| 0x6B1F | 0x6B1F | 27423 | 27423 | 31st reading | uint16_t | R/W | 1 |  | 0
| 0x6B20 | 0x6B20 | 27424 | 27424 | 32nd reading | uint16_t | R/W | 1 |  | 0
| 0x6B21 | 0x6B21 | 27425 | 27425 | 33rd reading | uint16_t | R/W | 1 |  | 0
| 0x6B22 | 0x6B22 | 27426 | 27426 | 34th reading | uint16_t | R/W | 1 |  | 0
| 0x6B23 | 0x6B23 | 27427 | 27427 | 35th reading | uint16_t | R/W | 1 |  | 0
| 0x6B24 | 0x6B24 | 27428 | 27428 | 36th reading | uint16_t | R/W | 1 |  | 0
| 0x6B25 | 0x6B25 | 27429 | 27429 | 37th reading | uint16_t | R/W | 1 |  | 0
| 0x6B26 | 0x6B26 | 27430 | 27430 | 38th reading | uint16_t | R/W | 1 |  | 0
| 0x6B27 | 0x6B27 | 27431 | 27431 | 39th reading | uint16_t | R/W | 1 |  | 0
| 0x6B28 | 0x6B28 | 27432 | 27432 | 40th reading | uint16_t | R/W | 1 |  | 0
Custom reading | 0x6A00 | 0x6A00 | 27136 | 27136 | 1st reading | uint16_t | R | 1
| 0x6A01 | 0x6A01 | 27137 | 27137 | 2nd reading | uint16_t | R | 1
| 0x6A02 | 0x6A02 | 27138 | 27138 | 3rd reading | uint16_t | R | 1
| 0x6A03 | 0x6A03 | 27139 | 27139 | 4th reading | uint16_t | R | 1
| 0x6A04 | 0x6A04 | 27140 | 27140 | 5th reading | uint16_t | R | 1
| 0x6A05 | 0x6A05 | 27141 | 27141 | 6th reading | uint16_t | R | 1
| 0x6A06 | 0x6A06 | 27142 | 27142 | 7th reading | uint16_t | R | 1
| 0x6A07 | 0x6A07 | 27143 | 27143 | 8th reading | uint16_t | R | 1
| 0x6A08 | 0x6A08 | 27144 | 27144 | 9th reading | uint16_t | R | 1
| 0x6A09 | 0x6A09 | 27145 | 27145 | 10th reading | uint16_t | R | 1
| 0x6A0A | 0x6A0A | 27146 | 27146 | 11th reading | uint16_t | R | 1
| 0x6A0B | 0x6A0B | 27147 | 27147 | 12th reading | uint16_t | R | 1
| 0x6A0C | 0x6A0C | 27148 | 27148 | 13th reading | uint16_t | R | 1
| 0x6A0D | 0x6A0D | 27149 | 27149 | 14th reading | uint16_t | R | 1
| 0x6A0E | 0x6A0E | 27150 | 27150 | 15th reading | uint16_t | R | 1
| 0x6A0F | 0x6A0F | 27151 | 27151 | 16th reading | uint16_t | R | 1
| 0x6A10 | 0x6A10 | 27152 | 27152 | 17th reading | uint16_t | R | 1
| 0x6A11 | 0x6A11 | 27153 | 27153 | 18th reading | uint16_t | R | 1
| 0x6A12 | 0x6A12 | 27154 | 27154 | 19th reading | uint16_t | R | 1
| 0x6A13 | 0x6A13 | 27155 | 27155 | 20th reading | uint16_t | R | 1
| 0x6A14 | 0x6A14 | 27156 | 27156 | 21st reading | uint16_t | R | 1
| 0x6A15 | 0x6A15 | 27157 | 27157 | 22nd reading | uint16_t | R | 1
| 0x6A16 | 0x6A16 | 27158 | 27158 | 23rd reading | uint16_t | R | 1
| 0x6A17 | 0x6A17 | 27159 | 27159 | 24th reading | uint16_t | R | 1
| 0x6A18 | 0x6A18 | 27160 | 27160 | 25th reading | uint16_t | R | 1
| 0x6A19 | 0x6A19 | 27161 | 27161 | 26th reading | uint16_t | R | 1
| 0x6A1A | 0x6A1A | 27162 | 27162 | 27th reading | uint16_t | R | 1
| 0x6A1B | 0x6A1B | 27163 | 27163 | 28th reading | uint16_t | R | 1
| 0x6A1C | 0x6A1C | 27164 | 27164 | 29th reading | uint16_t | R | 1
| 0x6A1D | 0x6A1D | 27165 | 27165 | 30th reading | uint16_t | R | 1
| 0x6A1E | 0x6A1E | 27166 | 27166 | 31st reading | uint16_t | R | 1
| 0x6A1F | 0x6A1F | 27167 | 27167 | 32nd reading | uint16_t | R | 1
| 0x6A20 | 0x6A20 | 27168 | 27168 | 33rd reading | uint16_t | R | 1
| 0x6A21 | 0x6A21 | 27169 | 27169 | 34th reading | uint16_t | R | 1
| 0x6A22 | 0x6A22 | 27170 | 27170 | 35th reading | uint16_t | R | 1
| 0x6A23 | 0x6A23 | 27171 | 27171 | 36th reading | uint16_t | R | 1
| 0x6A24 | 0x6A24 | 27172 | 27172 | 37th reading | uint16_t | R | 1
| 0x6A25 | 0x6A25 | 27173 | 27173 | 38th reading | uint16_t | R | 1
| 0x6A26 | 0x6A26 | 27174 | 27174 | 39th reading | uint16_t | R | 1
| 0x6A27 | 0x6A27 | 27175 | 27175 | 40th reading | uint16_t | R | 1

## MaxMin
| Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg Num | Range | Default
Max | 0x4136 | 0x4137 | 16694 | 16695 | V Max Value | float | R | 2
| 0x4138 | 0x413D | 16696 | 16701 | V Max Timestamp ( year： uint16_t month： uint16_t day： uint16_t hour： uint16_t min： uint16_t sec： uint16_t ) | timestamp | R | 6
| 0x413E | 0x413F | 16702 | 16703 | I1 Max Value | float | R | 2
| 0x4140 | 0x4145 | 16704 | 16709 | I1 Max Timestamp | timestamp | R | 6
| 0x4146 | 0x4147 | 16710 | 16711 | I2 Max Value | float | R | 2
| 0x4148 | 0x414D | 16712 | 16717 | I2 Max Timestamp | timestamp | R | 6
| 0x414E | 0x414F | 16718 | 16719 | Isum Max Value | float | R | 2
| 0x4150 | 0x4155 | 16720 | 16725 | Isum Max Timestamp | timestamp | R | 6
| 0x4156 | 0x4157 | 16726 | 16727 | P1 Max Value | float | R | 2
| 0x4158 | 0x415D | 16728 | 16733 | P1 Max Timestamp | timestamp | R | 6
| 0x415E | 0x415F | 16734 | 16735 | P2 Max Value | float | R | 2
| 0x4160 | 0x4165 | 16736 | 16741 | P2 Max Timestamp | timestamp | R | 6
| 0x4166 | 0x4167 | 16742 | 16743 | Psum Max Value | float | R | 2
| 0x4168 | 0x416D | 16744 | 16749 | Psum Max Timestamp | timestamp | R | 6
| 0x416E | 0x416F | 16750 | 16751 | Ripple factor U Max Value | float | R | 2
| 0x4170 | 0x4175 | 16752 | 16757 | Ripple factor U Max Timestamp | timestamp | R | 6
| 0x4176 | 0x4177 | 16758 | 16759 | Ripple factor I1 Max Value | float | R | 2
| 0x4178 | 0x417D | 16760 | 16765 | Ripple factor I1 Max Timestamp | timestamp | R | 6
| 0x417E | 0x417F | 16766 | 16767 | Ripple factor I2 Max Value | float | R | 2
| 0x4180 | 0x4185 | 16768 | 16773 | Ripple factor I2 Max Timestamp | timestamp | R | 6
| 0x4186 | 0x4187 | 16774 | 16775 | Demand I1 Max Value | float | R | 2
| 0x4188 | 0x418D | 16776 | 16781 | Demand I1 Max Timestamp | timestamp | R | 6
| 0x418E | 0x418F | 16782 | 16783 | Demand I2 Max Value | float | R | 2
| 0x4190 | 0x4195 | 16784 | 16789 | Demand I2 Max Timestamp | timestamp | R | 6
| 0x4196 | 0x4197 | 16790 | 16791 | Demand Isum Max Value | float | R | 2
| 0x4198 | 0x419D | 16792 | 16797 | Demand Isum Max Timestamp | timestamp | R | 6
| 0x419E | 0x419F | 16798 | 16799 | Demand P1 Max Value | float | R | 2
| 0x41A0 | 0x41A5 | 16800 | 16805 | Demand P1 Max Timestamp | timestamp | R | 6
| 0x41A6 | 0x41A7 | 16806 | 16807 | Demand P2 Max Value | float | R | 2
| 0x41A8 | 0x41AD | 16808 | 16813 | Demand P2 Max Timestamp | timestamp | R | 6
| 0x41AE | 0x41AF | 16814 | 16815 | Demand Psum Max Value | float | R | 2
| 0x41B0 | 0x41B5 | 16816 | 16821 | Demand Psum Max Timestamp | timestamp | R | 6
| 0x41B6 | 0x41B7 | 16822 | 16823 | V1 Compensated Max Value | float | R | 2
| 0x41B8 | 0x41BD | 16824 | 16829 | V1 Compensated Max Timestamp | timestamp | R | 6
| 0x41BE | 0x41BF | 16830 | 16831 | V2 Compensated Max Value | float | R | 2
| 0x41C0 | 0x41C5 | 16832 | 16837 | V2 Compensated Max Timestamp | timestamp | R | 6
Min | 0x41E5 | 0x41E6 | 16869 | 16870 | V Min Value | float | R | 2
| 0x41E7 | 0x41EC | 16871 | 16876 | V Min Timestamp ( year： uint16_t month： uint16_t day： uint16_t hour： uint16_t min： uint16_t sec： uint16_t ) | timestamp | R | 6
| 0x41ED | 0x41EE | 16877 | 16878 | I1 Min Value | float | R | 2
| 0x41EF | 0x41F4 | 16879 | 16884 | I1 Min Timestamp | timestamp | R | 6
| 0x41F5 | 0x41F6 | 16885 | 16886 | I2 Min Value | float | R | 2
| 0x41F7 | 0x41FC | 16887 | 16892 | I2 Min Timestamp | timestamp | R | 6
| 0x41FD | 0x41FE | 16893 | 16894 | Isum Min Value | float | R | 2
| 0x41FF | 0x4204 | 16895 | 16900 | Isum Min Timestamp | timestamp | R | 6
| 0x4205 | 0x4206 | 16901 | 16902 | P1 Min Value | float | R | 2
| 0x4207 | 0x420C | 16903 | 16908 | P1 Min Timestamp | timestamp | R | 6
| 0x420D | 0x420E | 16909 | 16910 | P2 Min Value | float | R | 2
| 0x420F | 0x4214 | 16911 | 16916 | P2 Min Timestamp | timestamp | R | 6
| 0x4215 | 0x4216 | 16917 | 16918 | Psum Min Value | float | R | 2
| 0x4217 | 0x421C | 16919 | 16924 | Psum Min Timestamp | timestamp | R | 6
| 0x421D | 0x421E | 16925 | 16926 | Ripple factor U Min Value | float | R | 2
| 0x421F | 0x4224 | 16927 | 16932 | Ripple factor U Min Timestamp | timestamp | R | 6
| 0x4225 | 0x4226 | 16933 | 16934 | Ripple factor I1 Min Value | float | R | 2
| 0x4227 | 0x422C | 16935 | 16940 | Ripple factor I1 Min Timestamp | timestamp | R | 6
| 0x422D | 0x422E | 16941 | 16942 | Ripple factor I2 Min Value | float | R | 2
| 0x422F | 0x4234 | 16943 | 16948 | Ripple factor I2 Min Timestamp | timestamp | R | 6
| 0x4235 | 0x4236 | 16949 | 16950 | V1 Compensated Min Value | float | R | 2
| 0x4237 | 0x423C | 16951 | 16956 | V1 Compensated Min Timestamp | timestamp | R | 6
| 0x423D | 0x423E | 16957 | 16958 | V2 Compensated Min Value | float | R | 2
| 0x423F | 0x4244 | 16959 | 16964 | V2 Compensated Min Timestamp | timestamp | R | 6

## Readings
| Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg Num | Range | Default
Real-time Parameters (float) | 0x3000 | 0x3001 | 12288 | 12289 | V Source | float | R | 2
| 0x3002 | 0x3003 | 12290 | 12291 | Current 1 | float | R | 2
| 0x3004 | 0x3005 | 12292 | 12293 | Current 2 | float | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Current Sum | float | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Power 1 | float | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Power 2 | float | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Power Sum | float | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Voltage Ripple Factor | float | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Current Ripple Factor 1 | float | R | 2
| 0x3012 | 0x3013 | 12306 | 12307 | Current Ripple Factor 2 | float | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | Demand Current 1 | float | R | 2
| 0x3016 | 0x3017 | 12310 | 12311 | Demand Current 2 | float | R | 2
| 0x3018 | 0x3019 | 12312 | 12313 | Demand Current Sum | float | R | 2
| 0x301A | 0x301B | 12314 | 12315 | Demand Power 1 | float | R | 2
| 0x301C | 0x301D | 12316 | 12317 | Demand Power 2 | float | R | 2
| 0x301E | 0x301F | 12318 | 12319 | Demand Power Sum | float | R | 2
| 0x3020 | 0x3021 | 12320 | 12321 | V Load - Ch 1 | float | R | 2
| 0x3022 | 0x3023 | 12322 | 12323 | V Load - Ch 2 | float | R | 2
Real-time Parameters (float) 20ms | 0x3100 | 0x3101 | 12544 | 12545 | V Source | float | R | 2
| 0x3102 | 0x3103 | 12546 | 12547 | Current 1 | float | R | 2
| 0x3104 | 0x3105 | 12548 | 12549 | Current 2 | float | R | 2
| 0x3106 | 0x3107 | 12550 | 12551 | Current Sum | float | R | 2
| 0x3108 | 0x3109 | 12552 | 12553 | Power 1 | float | R | 2
| 0x310A | 0x310B | 12554 | 12555 | Power 2 | float | R | 2
| 0x310C | 0x310D | 12556 | 12557 | Power Sum | float | R | 2
| 0x310E | 0x310F | 12558 | 12559 | Voltage Ripple Factor | float | R | 2
| 0x3110 | 0x3111 | 12560 | 12561 | Current Ripple Factor 1 | float | R | 2
| 0x3112 | 0x3113 | 12562 | 12563 | Current Ripple Factor 2 | float | R | 2
| 0x3114 | 0x3115 | 12564 | 12565 | V Load - Ch 1 | float | R | 2
| 0x3116 | 0x3117 | 12566 | 12567 | V Load - Ch 2 | float | R | 2
Real-time Parameters (Int) | 0x3200 | 0x3200 | 12800 | 12800 | V Source | int16_t | R | 1
| 0x3201 | 0x3201 | 12801 | 12801 | Current 1 | int16_t | R | 1
| 0x3202 | 0x3202 | 12802 | 12802 | Current 2 | int16_t | R | 1
| 0x3203 | 0x3203 | 12803 | 12803 | Current Sum | int16_t | R | 1
| 0x3204 | 0x3204 | 12804 | 12804 | Power 1 | int16_t | R | 1
| 0x3205 | 0x3205 | 12805 | 12805 | Power 2 | int16_t | R | 1
| 0x3206 | 0x3206 | 12806 | 12806 | Power Sum | int16_t | R | 1
| 0x3207 | 0x3207 | 12807 | 12807 | Voltage Ripple Factor | int16_t | R | 1
| 0x3208 | 0x3208 | 12808 | 12808 | Current Ripple Factor 1 | int16_t | R | 1
| 0x3209 | 0x3209 | 12809 | 12809 | Current Ripple Factor 2 | int16_t | R | 1
| 0x320A | 0x320A | 12810 | 12810 | Demand Current 1 | int16_t | R | 1
| 0x320B | 0x320B | 12811 | 12811 | Demand Current 2 | int16_t | R | 1
| 0x320C | 0x320C | 12812 | 12812 | Demand Current Sum | int16_t | R | 1
| 0x320D | 0x320D | 12813 | 12813 | Demand Power 1 | int16_t | R | 1
| 0x320E | 0x320E | 12814 | 12814 | Demand Power 2 | int16_t | R | 1
| 0x320F | 0x320F | 12815 | 12815 | Demand Power Sum | int16_t | R | 1
| 0x3210 | 0x3210 | 12816 | 12816 | V Load - Ch 1 | int16_t | R | 1
| 0x3211 | 0x3211 | 12817 | 12817 | V Load - Ch 2 | int16_t | R | 1
Energy & Charge | 0x4000 | 0x4003 | 16384 | 16387 | Import Energy 1 | double | R/W | 4
| 0x4004 | 0x4007 | 16388 | 16391 | Export Energy 1 | double | R/W | 4
| 0x4008 | 0x400B | 16392 | 16395 | Net Energy 1 | double | R/W | 4
| 0x400C | 0x400F | 16396 | 16399 | Total Energy 1 | double | R/W | 4
| 0x4010 | 0x4013 | 16400 | 16403 | Import Energy 2 | double | R/W | 4
| 0x4014 | 0x4017 | 16404 | 16407 | Export Energy 2 | double | R/W | 4
| 0x4018 | 0x401B | 16408 | 16411 | Net Energy 2 | double | R/W | 4
| 0x401C | 0x401F | 16412 | 16415 | Total Energy 2 | double | R/W | 4
| 0x4020 | 0x4023 | 16416 | 16419 | Import Energy Sum | double | R/W | 4
| 0x4024 | 0x4027 | 16420 | 16423 | Export Energy Sum | double | R/W | 4
| 0x4028 | 0x402B | 16424 | 16427 | Net Energy Sum | double | R/W | 4
| 0x402C | 0x402F | 16428 | 16431 | Total Energy Sum | double | R/W | 4
| 0x4030 | 0x4033 | 16432 | 16435 | Import Charge 1 | double | R/W | 4
| 0x4034 | 0x4037 | 16436 | 16439 | Export Charge 1 | double | R/W | 4
| 0x4038 | 0x403B | 16440 | 16443 | Net Charge 1 | double | R/W | 4
| 0x403C | 0x403F | 16444 | 16447 | Total Charge 1 | double | R/W | 4
| 0x4040 | 0x4043 | 16448 | 16451 | Import Charge 2 | double | R/W | 4
| 0x4044 | 0x4047 | 16452 | 16455 | Export Charge 2 | double | R/W | 4
| 0x4048 | 0x404B | 16456 | 16459 | Net Charge 2 | double | R/W | 4
| 0x404C | 0x404F | 16460 | 16463 | Total Charge 2 | double | R/W | 4
| 0x4050 | 0x4053 | 16464 | 16467 | Import Charge Sum | double | R/W | 4
| 0x4054 | 0x4057 | 16468 | 16471 | Export Charge Sum | double | R/W | 4
| 0x4058 | 0x405B | 16472 | 16475 | Net Charge Sum | double | R/W | 4
| 0x405C | 0x405F | 16476 | 16479 | Total Charge Sum | double | R/W | 4