## Version History
Version | Changes | Date | External Firmware Version
v1.01 - v1.02 | Address table defined according to the functional specifications of the product. | 2024-07-26 | /
v1.03 | 1. In the sheet "Readings",add the register map of "Real-time Parameters (float) -High Speed" 2. In the sheet "Readings" add the register map of "Real-Time Parameters (int)-High Speed" | 2025-05-16 | v1.03p02
v1.04 | 1.In the sheet "Basic configuration",make the 0x1015 register to reserved. | 2026-03-20 | v1.04p02

## Overview
Block | Sector | Sheet | Start | End | Length(reg num) | Comments
Basic Meter Settings | Basic Meter Settings | Basic Configuration | 0x1000 | 0x1023 | 36
Real-time clock | Real-Time Clock | Basic Configuration | 0x103F | 0x1045 | 7
Clear & Reset | Clear & Reset | Basic Configuration | 0x2000 | 0x2007 | 8
Real-Time Parameters (float) | Real-Time Parameters (float) | Readings | 0x3000 | 0x3015 | 22
Real-Time Parameters (float)-High Speed | Real-Time Parameters (float)-High Speed | Readings | 0x3100 | 0x3109 | 10
Real-Time Parameters (int) | Real-Time Parameters (int) | Readings | 0x3200 | 0x320A | 11
Real-Time Parameters (int)-High Speed | Real-Time Parameters (int)-High Speed | Readings | 0x3300 | 0x3304 | 5
Energy and Charge | Energy and Charge | Readings | 0x4000 | 0x401F | 32
Max | Max | Max/Min | 0x4136 | 0x4162 | 45
Demand Max | Demand Max | Max/Min | 0x4163 | 0x4186 | 36
Min | Min | Max/Min | 0x4187 | 0x41B3 | 45
Custom reading | Custom Reading | Basic Configuration | 0x6A00 | 0x6AC7 | 200
Custom reading settings | Custom Reading Settings | Basic Configuration | 0x6B00 | 0x6B32 | 51

## Basic Configuration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg Num | Range | Default
Basic Meter Settings | 0x1000 | 0x1000 | 4096 | 4096 | Meter password | uint16_t | R/W | 1 | 0－9999 | 0
| 0x1001 | 0x1001 | 4097 | 4097 | RS485 baud rate | uint16_t | R/W | 1 | 2400－115200 | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | RS485 parity | uint16_t | R/W | 1 | 0：even 1：odd 2：Non2 3：Non1 | 0
| 0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | uint16_t | R/W | 1 | 0: manual 1: DHCP | 0
| 0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte (high) IP address 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte (high) IP address 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte (high) Subnet mask 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 255 255 255 0
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte (high) Subnet mask 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte (high) Gateway 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 192 168 1 1
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte (high) Gateway 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte (high) DNS primary server 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 8 8 8 8
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte (high) DNS primary server 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte (high) DNS secondary server 2nd byte (low) | uint16_t | R/W | 1 | 0~255 | 8.8.4.4
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte (high) DNS secondary server 4th byte (low) | uint16_t | R/W | 1 | 0~255
| 0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1
| 0x100F | 0x100F | 4111 | 4111 | Modbus RTU Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | uint16_t | R/W | 1 | 1-65534 | 502
| 0x1012 | 0x1012 | 4114 | 4114 | PT1 | uint16_t | R | 1 | fixed as 1000 for now | 1000
| 0x1013 | 0x1013 | 4115 | 4115 | PT2 | uint16_t | R | 1 | fixed as 1000 for now | 1000
| 0x1014 | 0x1014 | 4116 | 4116 | CT1 | uint16_t | R | 1 | fixed as 650A | 650
| 0x1015 | 0x1015 | 4117 | 4117 | Reserved |  |  | 1
| 0x1016 | 0x1016 | 4118 | 4118 | Demand calculation method | uint16_t | R/W | 1 | 0: Fixed block 1: Sliding block | 1
| 0x1017 | 0x1017 | 4119 | 4119 | Demand window time | uint16_t | R/W | 1 | 1~30 | 15
| 0x1018 | 0x1018 | 4120 | 4120 | Demand update period | uint16_t | R/W | 1 | 1~30 | 1
| 0x1019 | 0x1019 | 4121 | 4121 | Energy pulse parameter | uint16_t | R/W | 1 | 0: None 1: Import Energy 2: Export Energy 3: NET Energy 4: TOTAL Energy | 0
| 0x101A | 0x101B | 4122 | 4123 | Energy pulse constant | uint16_t | R/W | 2 | 0.1—100000.000 internal actual value is *1000 in integers. | 1
| 0x101C | 0x101C | 4124 | 4124 | Backlight time | uint16_t | R/W | 1 | 0－120 | 1
| 0x101D | 0x101D | 4125 | 4125 | Seal status | uint16_t | R | 1 | Sealed: 0x0A | 0
| 0x101E | 0x101E | 4126 | 4126 | Device run time (high 16 bits) | uint16_t | R/W | 1 | uint in second | 0
| 0x101F | 0x101F | 4127 | 4127 | Device run time (low 16 bits) | uint16_t | R/W | 1 |  | 0
| 0x1020 | 0x1020 | 4128 | 4128 | Device load time (high 16 bits) | uint16_t | R/W | 1 | uint in second | 0
| 0x1021 | 0x1021 | 4129 | 4129 | Device load time (low 16 bits) | uint16_t | R/W | 1 |  | 0
| 0x1022 | 0x1022 | 4130 | 4130 | Enable cable loss compensation | uint16_t | R/W | 1 | 0: Disable 1: Enable | 0
| 0x1023 | 0x1023 | 4131 | 4131 | Cable resistance | uint16_t | R/W | 1 | 0 ~ 65535(in 0.0001 Ohm) | 0
Real-time clock
| 0x103F | 0x103F | 4159 | 4159 | Week | uint16_t | R/W | 1 | 1~7 | 1
| 0x1040 | 0x1040 | 4160 | 4160 | Year | uint16_t | R/W | 1 | 2000~2099 | 2024
| 0x1041 | 0x1041 | 4161 | 4161 | Month | uint16_t | R/W | 1 | 1~12 | 1
| 0x1042 | 0x1042 | 4162 | 4162 | Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x1043 | 0x1043 | 4163 | 4163 | Hour | uint16_t | R/W | 1 | 0~23 | 0
| 0x1044 | 0x1044 | 4164 | 4164 | Minute | uint16_t | R/W | 1 | 0~59 | 0
| 0x1045 | 0x1045 | 4165 | 4165 | Second | uint16_t | R/W | 1 | 0~59 | 0
Clear & Reset | 0x2000 | 0x2000 | 8192 | 8192 | Clear energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2001 | 0x2001 | 8193 | 8193 | Clear charge | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2002 | 0x2002 | 8194 | 8194 | Clear demand | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2003 | 0x2003 | 8195 | 8195 | Clear max/min | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2004 | 0x2004 | 8196 | 8196 | Clear device run time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2005 | 0x2005 | 8197 | 8197 | Clear load time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x2006 | 0x2006 | 8198 | 8198 | Factory reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
| 0x2007 | 0x2007 | 8199 | 8199 | Network reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
Custom reading | 0x6A00 | 0x6A00 | 27136 | 27136 | 1st reading | uint16_t | R | 1 |  | 0
| 0x6A01 | 0x6A01 | 27137 | 27137 | 2nd reading | uint16_t | R | 1 |  | 0
| 0x6A02 | 0x6A02 | 27138 | 27138 | 3rd reading | uint16_t | R | 1 |  | 0
| 0x6A03 | 0x6A03 | 27139 | 27139 | 4th reading | uint16_t | R | 1 |  | 0
| 0x6A04 | 0x6A04 | 27140 | 27140 | 5th reading | uint16_t | R | 1 |  | 0
| 0x6A05 | 0x6A05 | 27141 | 27141 | 6th reading | uint16_t | R | 1 |  | 0
| 0x6A06 | 0x6A06 | 27142 | 27142 | 7th reading | uint16_t | R | 1 |  | 0
| 0x6A07 | 0x6A07 | 27143 | 27143 | 8th reading | uint16_t | R | 1 |  | 0
| 0x6A08 | 0x6A08 | 27144 | 27144 | 9th reading | uint16_t | R | 1 |  | 0
| 0x6A09 | 0x6A09 | 27145 | 27145 | 10th reading | uint16_t | R | 1 |  | 0
| 0x6A0A | 0x6A0A | 27146 | 27146 | 11th reading | uint16_t | R | 1 |  | 0
| 0x6A0B | 0x6A0B | 27147 | 27147 | 12th reading | uint16_t | R | 1 |  | 0
| 0x6A0C | 0x6A0C | 27148 | 27148 | 13th reading | uint16_t | R | 1 |  | 0
| 0x6A0D | 0x6A0D | 27149 | 27149 | 14th reading | uint16_t | R | 1 |  | 0
| 0x6A0E | 0x6A0E | 27150 | 27150 | 15th reading | uint16_t | R | 1 |  | 0
| 0x6A0F | 0x6A0F | 27151 | 27151 | 16th reading | uint16_t | R | 1 |  | 0
| 0x6A10 | 0x6A10 | 27152 | 27152 | 17th reading | uint16_t | R | 1 |  | 0
| 0x6A11 | 0x6A11 | 27153 | 27153 | 18th reading | uint16_t | R | 1 |  | 0
| 0x6A12 | 0x6A12 | 27154 | 27154 | 19th reading | uint16_t | R | 1 |  | 0
| 0x6A13 | 0x6A13 | 27155 | 27155 | 20th reading | uint16_t | R | 1 |  | 0
| 0x6A14 | 0x6A14 | 27156 | 27156 | 21st reading | uint16_t | R | 1 |  | 0
| 0x6A15 | 0x6A15 | 27157 | 27157 | 22nd reading | uint16_t | R | 1 |  | 0
| 0x6A16 | 0x6A16 | 27158 | 27158 | 23rd reading | uint16_t | R | 1 |  | 0
| 0x6A17 | 0x6A17 | 27159 | 27159 | 24th reading | uint16_t | R | 1 |  | 0
| 0x6A18 | 0x6A18 | 27160 | 27160 | 25th reading | uint16_t | R | 1 |  | 0
| 0x6A19 | 0x6A19 | 27161 | 27161 | 26th reading | uint16_t | R | 1 |  | 0
| 0x6A1A | 0x6A1A | 27162 | 27162 | 27th reading | uint16_t | R | 1 |  | 0
| 0x6A1B | 0x6A1B | 27163 | 27163 | 28th reading | uint16_t | R | 1 |  | 0
| 0x6A1C | 0x6A1C | 27164 | 27164 | 29th reading | uint16_t | R | 1 |  | 0
| 0x6A1D | 0x6A1D | 27165 | 27165 | 30th reading | uint16_t | R | 1 |  | 0
| 0x6A1E | 0x6A1E | 27166 | 27166 | 31st reading | uint16_t | R | 1 |  | 0
| 0x6A1F | 0x6A1F | 27167 | 27167 | 32nd reading | uint16_t | R | 1 |  | 0
| 0x6A20 | 0x6A20 | 27168 | 27168 | 33rd reading | uint16_t | R | 1 |  | 0
| 0x6A21 | 0x6A21 | 27169 | 27169 | 34th reading | uint16_t | R | 1 |  | 0
| 0x6A22 | 0x6A22 | 27170 | 27170 | 35th reading | uint16_t | R | 1 |  | 0
| 0x6A23 | 0x6A23 | 27171 | 27171 | 36th reading | uint16_t | R | 1 |  | 0
| 0x6A24 | 0x6A24 | 27172 | 27172 | 37th reading | uint16_t | R | 1 |  | 0
| 0x6A25 | 0x6A25 | 27173 | 27173 | 38th reading | uint16_t | R | 1 |  | 0
| 0x6A26 | 0x6A26 | 27174 | 27174 | 39th reading | uint16_t | R | 1 |  | 0
| 0x6A27 | 0x6A27 | 27175 | 27175 | 40th reading | uint16_t | R | 1 |  | 0
| 0x6A28 | 0x6A28 | 27176 | 27176 | 41st reading | uint16_t | R | 1 |  | 0
| 0x6A29 | 0x6A29 | 27177 | 27177 | 42nd reading | uint16_t | R | 1 |  | 0
| 0x6A2A | 0x6A2A | 27178 | 27178 | 43rd reading | uint16_t | R | 1 |  | 0
| 0x6A2B | 0x6A2B | 27179 | 27179 | 44th reading | uint16_t | R | 1 |  | 0
| 0x6A2C | 0x6A2C | 27180 | 27180 | 45th reading | uint16_t | R | 1 |  | 0
| 0x6A2D | 0x6A2D | 27181 | 27181 | 46th reading | uint16_t | R | 1 |  | 0
| 0x6A2E | 0x6A2E | 27182 | 27182 | 47th reading | uint16_t | R | 1 |  | 0
| 0x6A2F | 0x6A2F | 27183 | 27183 | 48th reading | uint16_t | R | 1 |  | 0
| 0x6A30 | 0x6A30 | 27184 | 27184 | 49th reading | uint16_t | R | 1 |  | 0
| 0x6A31 | 0x6A31 | 27185 | 27185 | 50th reading | uint16_t | R | 1 |  | 0
| 0x6A32 | 0x6A32 | 27186 | 27186 | 51st reading | uint16_t | R | 1 |  | 0
| 0x6A33 | 0x6A33 | 27187 | 27187 | 52nd reading | uint16_t | R | 1 |  | 0
| 0x6A34 | 0x6A34 | 27188 | 27188 | 53rd reading | uint16_t | R | 1 |  | 0
| 0x6A35 | 0x6A35 | 27189 | 27189 | 54th reading | uint16_t | R | 1 |  | 0
| 0x6A36 | 0x6A36 | 27190 | 27190 | 55th reading | uint16_t | R | 1 |  | 0
| 0x6A37 | 0x6A37 | 27191 | 27191 | 56th reading | uint16_t | R | 1 |  | 0
| 0x6A38 | 0x6A38 | 27192 | 27192 | 57th reading | uint16_t | R | 1 |  | 0
| 0x6A39 | 0x6A39 | 27193 | 27193 | 58th reading | uint16_t | R | 1 |  | 0
| 0x6A3A | 0x6A3A | 27194 | 27194 | 59th reading | uint16_t | R | 1 |  | 0
| 0x6A3B | 0x6A3B | 27195 | 27195 | 60th reading | uint16_t | R | 1 |  | 0
| 0x6A3C | 0x6A3C | 27196 | 27196 | 61st reading | uint16_t | R | 1 |  | 0
| 0x6A3D | 0x6A3D | 27197 | 27197 | 62nd reading | uint16_t | R | 1 |  | 0
| 0x6A3E | 0x6A3E | 27198 | 27198 | 63rd reading | uint16_t | R | 1 |  | 0
| 0x6A3F | 0x6A3F | 27199 | 27199 | 64th reading | uint16_t | R | 1 |  | 0
| 0x6A40 | 0x6A40 | 27200 | 27200 | 65th reading | uint16_t | R | 1 |  | 0
66th-200th are reserved. | 0x6A41 | 0x6A41 | 27201 | 27201 | 66th reading | uint16_t | R | 1 |  | 0
| 0x6A42 | 0x6A42 | 27202 | 27202 | 67th reading | uint16_t | R | 1 |  | 0
| 0x6A43 | 0x6A43 | 27203 | 27203 | 68th reading | uint16_t | R | 1 |  | 0
| 0x6A44 | 0x6A44 | 27204 | 27204 | 69th reading | uint16_t | R | 1 |  | 0
| 0x6A45 | 0x6A45 | 27205 | 27205 | 70th reading | uint16_t | R | 1 |  | 0
| 0x6A46 | 0x6A46 | 27206 | 27206 | 71st reading | uint16_t | R | 1 |  | 0
| 0x6A47 | 0x6A47 | 27207 | 27207 | 72nd reading | uint16_t | R | 1 |  | 0
| 0x6A48 | 0x6A48 | 27208 | 27208 | 73rd reading | uint16_t | R | 1 |  | 0
| 0x6A49 | 0x6A49 | 27209 | 27209 | 74th reading | uint16_t | R | 1 |  | 0
| 0x6A4A | 0x6A4A | 27210 | 27210 | 75th reading | uint16_t | R | 1 |  | 0
| 0x6A4B | 0x6A4B | 27211 | 27211 | 76th reading | uint16_t | R | 1 |  | 0
| 0x6A4C | 0x6A4C | 27212 | 27212 | 77th reading | uint16_t | R | 1 |  | 0
| 0x6A4D | 0x6A4D | 27213 | 27213 | 78th reading | uint16_t | R | 1 |  | 0
| 0x6A4E | 0x6A4E | 27214 | 27214 | 79th reading | uint16_t | R | 1 |  | 0
| 0x6A4F | 0x6A4F | 27215 | 27215 | 80th reading | uint16_t | R | 1 |  | 0
| 0x6A50 | 0x6A50 | 27216 | 27216 | 81st reading | uint16_t | R | 1 |  | 0
| 0x6A51 | 0x6A51 | 27217 | 27217 | 82nd reading | uint16_t | R | 1 |  | 0
| 0x6A52 | 0x6A52 | 27218 | 27218 | 83rd reading | uint16_t | R | 1 |  | 0
| 0x6A53 | 0x6A53 | 27219 | 27219 | 84th reading | uint16_t | R | 1 |  | 0
| 0x6A54 | 0x6A54 | 27220 | 27220 | 85th reading | uint16_t | R | 1 |  | 0
| 0x6A55 | 0x6A55 | 27221 | 27221 | 86th reading | uint16_t | R | 1 |  | 0
| 0x6A56 | 0x6A56 | 27222 | 27222 | 87th reading | uint16_t | R | 1 |  | 0
| 0x6A57 | 0x6A57 | 27223 | 27223 | 88th reading | uint16_t | R | 1 |  | 0
| 0x6A58 | 0x6A58 | 27224 | 27224 | 89th reading | uint16_t | R | 1 |  | 0
| 0x6A59 | 0x6A59 | 27225 | 27225 | 90th reading | uint16_t | R | 1 |  | 0
| 0x6A5A | 0x6A5A | 27226 | 27226 | 91st reading | uint16_t | R | 1 |  | 0
| 0x6A5B | 0x6A5B | 27227 | 27227 | 92nd reading | uint16_t | R | 1 |  | 0
| 0x6A5C | 0x6A5C | 27228 | 27228 | 93rd reading | uint16_t | R | 1 |  | 0
| 0x6A5D | 0x6A5D | 27229 | 27229 | 94th reading | uint16_t | R | 1 |  | 0
| 0x6A5E | 0x6A5E | 27230 | 27230 | 95th reading | uint16_t | R | 1 |  | 0
| 0x6A5F | 0x6A5F | 27231 | 27231 | 96th reading | uint16_t | R | 1 |  | 0
| 0x6A60 | 0x6A60 | 27232 | 27232 | 97th reading | uint16_t | R | 1 |  | 0
| 0x6A61 | 0x6A61 | 27233 | 27233 | 98th reading | uint16_t | R | 1 |  | 0
| 0x6A62 | 0x6A62 | 27234 | 27234 | 99th reading | uint16_t | R | 1 |  | 0
| 0x6A63 | 0x6A63 | 27235 | 27235 | 100th reading | uint16_t | R | 1 |  | 0
| 0x6A64 | 0x6A64 | 27236 | 27236 | 101st reading | uint16_t | R | 1 |  | 0
| 0x6A65 | 0x6A65 | 27237 | 27237 | 102nd reading | uint16_t | R | 1 |  | 0
| 0x6A66 | 0x6A66 | 27238 | 27238 | 103rd reading | uint16_t | R | 1 |  | 0
| 0x6A67 | 0x6A67 | 27239 | 27239 | 104th reading | uint16_t | R | 1 |  | 0
| 0x6A68 | 0x6A68 | 27240 | 27240 | 105th reading | uint16_t | R | 1 |  | 0
| 0x6A69 | 0x6A69 | 27241 | 27241 | 106th reading | uint16_t | R | 1 |  | 0
| 0x6A6A | 0x6A6A | 27242 | 27242 | 107th reading | uint16_t | R | 1 |  | 0
| 0x6A6B | 0x6A6B | 27243 | 27243 | 108th reading | uint16_t | R | 1 |  | 0
| 0x6A6C | 0x6A6C | 27244 | 27244 | 109th reading | uint16_t | R | 1 |  | 0
| 0x6A6D | 0x6A6D | 27245 | 27245 | 110th reading | uint16_t | R | 1 |  | 0
| 0x6A6E | 0x6A6E | 27246 | 27246 | 111th reading | uint16_t | R | 1 |  | 0
| 0x6A6F | 0x6A6F | 27247 | 27247 | 112th reading | uint16_t | R | 1 |  | 0
| 0x6A70 | 0x6A70 | 27248 | 27248 | 113th reading | uint16_t | R | 1 |  | 0
| 0x6A71 | 0x6A71 | 27249 | 27249 | 114th reading | uint16_t | R | 1 |  | 0
| 0x6A72 | 0x6A72 | 27250 | 27250 | 115th reading | uint16_t | R | 1 |  | 0
| 0x6A73 | 0x6A73 | 27251 | 27251 | 116th reading | uint16_t | R | 1 |  | 0
| 0x6A74 | 0x6A74 | 27252 | 27252 | 117th reading | uint16_t | R | 1 |  | 0
| 0x6A75 | 0x6A75 | 27253 | 27253 | 118th reading | uint16_t | R | 1 |  | 0
| 0x6A76 | 0x6A76 | 27254 | 27254 | 119th reading | uint16_t | R | 1 |  | 0
| 0x6A77 | 0x6A77 | 27255 | 27255 | 120th reading | uint16_t | R | 1 |  | 0
| 0x6A78 | 0x6A78 | 27256 | 27256 | 121st reading | uint16_t | R | 1 |  | 0
| 0x6A79 | 0x6A79 | 27257 | 27257 | 122nd reading | uint16_t | R | 1 |  | 0
| 0x6A7A | 0x6A7A | 27258 | 27258 | 123rd reading | uint16_t | R | 1 |  | 0
| 0x6A7B | 0x6A7B | 27259 | 27259 | 124th reading | uint16_t | R | 1 |  | 0
| 0x6A7C | 0x6A7C | 27260 | 27260 | 125th reading | uint16_t | R | 1 |  | 0
| 0x6A7D | 0x6A7D | 27261 | 27261 | 126th reading | uint16_t | R | 1 |  | 0
| 0x6A7E | 0x6A7E | 27262 | 27262 | 127th reading | uint16_t | R | 1 |  | 0
| 0x6A7F | 0x6A7F | 27263 | 27263 | 128th reading | uint16_t | R | 1 |  | 0
| 0x6A80 | 0x6A80 | 27264 | 27264 | 129th reading | uint16_t | R | 1 |  | 0
| 0x6A81 | 0x6A81 | 27265 | 27265 | 130th reading | uint16_t | R | 1 |  | 0
| 0x6A82 | 0x6A82 | 27266 | 27266 | 131st reading | uint16_t | R | 1 |  | 0
| 0x6A83 | 0x6A83 | 27267 | 27267 | 132nd reading | uint16_t | R | 1 |  | 0
| 0x6A84 | 0x6A84 | 27268 | 27268 | 133rd reading | uint16_t | R | 1 |  | 0
| 0x6A85 | 0x6A85 | 27269 | 27269 | 134th reading | uint16_t | R | 1 |  | 0
| 0x6A86 | 0x6A86 | 27270 | 27270 | 135th reading | uint16_t | R | 1 |  | 0
| 0x6A87 | 0x6A87 | 27271 | 27271 | 136th reading | uint16_t | R | 1 |  | 0
| 0x6A88 | 0x6A88 | 27272 | 27272 | 137th reading | uint16_t | R | 1 |  | 0
| 0x6A89 | 0x6A89 | 27273 | 27273 | 138th reading | uint16_t | R | 1 |  | 0
| 0x6A8A | 0x6A8A | 27274 | 27274 | 139th reading | uint16_t | R | 1 |  | 0
| 0x6A8B | 0x6A8B | 27275 | 27275 | 140th reading | uint16_t | R | 1 |  | 0
| 0x6A8C | 0x6A8C | 27276 | 27276 | 141st reading | uint16_t | R | 1 |  | 0
| 0x6A8D | 0x6A8D | 27277 | 27277 | 142nd reading | uint16_t | R | 1 |  | 0
| 0x6A8E | 0x6A8E | 27278 | 27278 | 143rd reading | uint16_t | R | 1 |  | 0
| 0x6A8F | 0x6A8F | 27279 | 27279 | 144th reading | uint16_t | R | 1 |  | 0
| 0x6A90 | 0x6A90 | 27280 | 27280 | 145th reading | uint16_t | R | 1 |  | 0
| 0x6A91 | 0x6A91 | 27281 | 27281 | 146th reading | uint16_t | R | 1 |  | 0
| 0x6A92 | 0x6A92 | 27282 | 27282 | 147th reading | uint16_t | R | 1 |  | 0
| 0x6A93 | 0x6A93 | 27283 | 27283 | 148th reading | uint16_t | R | 1 |  | 0
| 0x6A94 | 0x6A94 | 27284 | 27284 | 149th reading | uint16_t | R | 1 |  | 0
| 0x6A95 | 0x6A95 | 27285 | 27285 | 150th reading | uint16_t | R | 1 |  | 0
| 0x6A96 | 0x6A96 | 27286 | 27286 | 151st reading | uint16_t | R | 1 |  | 0
| 0x6A97 | 0x6A97 | 27287 | 27287 | 152nd reading | uint16_t | R | 1 |  | 0
| 0x6A98 | 0x6A98 | 27288 | 27288 | 153rd reading | uint16_t | R | 1 |  | 0
| 0x6A99 | 0x6A99 | 27289 | 27289 | 154th reading | uint16_t | R | 1 |  | 0
| 0x6A9A | 0x6A9A | 27290 | 27290 | 155th reading | uint16_t | R | 1 |  | 0
| 0x6A9B | 0x6A9B | 27291 | 27291 | 156th reading | uint16_t | R | 1 |  | 0
| 0x6A9C | 0x6A9C | 27292 | 27292 | 157th reading | uint16_t | R | 1 |  | 0
| 0x6A9D | 0x6A9D | 27293 | 27293 | 158th reading | uint16_t | R | 1 |  | 0
| 0x6A9E | 0x6A9E | 27294 | 27294 | 159th reading | uint16_t | R | 1 |  | 0
| 0x6A9F | 0x6A9F | 27295 | 27295 | 160th reading | uint16_t | R | 1 |  | 0
| 0x6AA0 | 0x6AA0 | 27296 | 27296 | 161st reading | uint16_t | R | 1 |  | 0
| 0x6AA1 | 0x6AA1 | 27297 | 27297 | 162nd reading | uint16_t | R | 1 |  | 0
| 0x6AA2 | 0x6AA2 | 27298 | 27298 | 163rd reading | uint16_t | R | 1 |  | 0
| 0x6AA3 | 0x6AA3 | 27299 | 27299 | 164th reading | uint16_t | R | 1 |  | 0
| 0x6AA4 | 0x6AA4 | 27300 | 27300 | 165th reading | uint16_t | R | 1 |  | 0
| 0x6AA5 | 0x6AA5 | 27301 | 27301 | 166th reading | uint16_t | R | 1 |  | 0
| 0x6AA6 | 0x6AA6 | 27302 | 27302 | 167th reading | uint16_t | R | 1 |  | 0
| 0x6AA7 | 0x6AA7 | 27303 | 27303 | 168th reading | uint16_t | R | 1 |  | 0
| 0x6AA8 | 0x6AA8 | 27304 | 27304 | 169th reading | uint16_t | R | 1 |  | 0
| 0x6AA9 | 0x6AA9 | 27305 | 27305 | 170th reading | uint16_t | R | 1 |  | 0
| 0x6AAA | 0x6AAA | 27306 | 27306 | 171st reading | uint16_t | R | 1 |  | 0
| 0x6AAB | 0x6AAB | 27307 | 27307 | 172nd reading | uint16_t | R | 1 |  | 0
| 0x6AAC | 0x6AAC | 27308 | 27308 | 173rd reading | uint16_t | R | 1 |  | 0
| 0x6AAD | 0x6AAD | 27309 | 27309 | 174th reading | uint16_t | R | 1 |  | 0
| 0x6AAE | 0x6AAE | 27310 | 27310 | 175th reading | uint16_t | R | 1 |  | 0
| 0x6AAF | 0x6AAF | 27311 | 27311 | 176th reading | uint16_t | R | 1 |  | 0
| 0x6AB0 | 0x6AB0 | 27312 | 27312 | 177th reading | uint16_t | R | 1 |  | 0
| 0x6AB1 | 0x6AB1 | 27313 | 27313 | 178th reading | uint16_t | R | 1 |  | 0
| 0x6AB2 | 0x6AB2 | 27314 | 27314 | 179th reading | uint16_t | R | 1 |  | 0
| 0x6AB3 | 0x6AB3 | 27315 | 27315 | 180th reading | uint16_t | R | 1 |  | 0
| 0x6AB4 | 0x6AB4 | 27316 | 27316 | 181st reading | uint16_t | R | 1 |  | 0
| 0x6AB5 | 0x6AB5 | 27317 | 27317 | 182nd reading | uint16_t | R | 1 |  | 0
| 0x6AB6 | 0x6AB6 | 27318 | 27318 | 183rd reading | uint16_t | R | 1 |  | 0
| 0x6AB7 | 0x6AB7 | 27319 | 27319 | 184th reading | uint16_t | R | 1 |  | 0
| 0x6AB8 | 0x6AB8 | 27320 | 27320 | 185th reading | uint16_t | R | 1 |  | 0
| 0x6AB9 | 0x6AB9 | 27321 | 27321 | 186th reading | uint16_t | R | 1 |  | 0
| 0x6ABA | 0x6ABA | 27322 | 27322 | 187th reading | uint16_t | R | 1 |  | 0
| 0x6ABB | 0x6ABB | 27323 | 27323 | 188th reading | uint16_t | R | 1 |  | 0
| 0x6ABC | 0x6ABC | 27324 | 27324 | 189th reading | uint16_t | R | 1 |  | 0
| 0x6ABD | 0x6ABD | 27325 | 27325 | 190th reading | uint16_t | R | 1 |  | 0
| 0x6ABE | 0x6ABE | 27326 | 27326 | 191st reading | uint16_t | R | 1 |  | 0
| 0x6ABF | 0x6ABF | 27327 | 27327 | 192nd reading | uint16_t | R | 1 |  | 0
| 0x6AC0 | 0x6AC0 | 27328 | 27328 | 193rd reading | uint16_t | R | 1 |  | 0
| 0x6AC1 | 0x6AC1 | 27329 | 27329 | 194th reading | uint16_t | R | 1 |  | 0
| 0x6AC2 | 0x6AC2 | 27330 | 27330 | 195th reading | uint16_t | R | 1 |  | 0
| 0x6AC3 | 0x6AC3 | 27331 | 27331 | 196th reading | uint16_t | R | 1 |  | 0
| 0x6AC4 | 0x6AC4 | 27332 | 27332 | 197th reading | uint16_t | R | 1 |  | 0
| 0x6AC5 | 0x6AC5 | 27333 | 27333 | 198th reading | uint16_t | R | 1 |  | 0
| 0x6AC6 | 0x6AC6 | 27334 | 27334 | 199th reading | uint16_t | R | 1 |  | 0
| 0x6AC7 | 0x6AC7 | 27335 | 27335 | 200th reading | uint16_t | R | 1 |  | 0
Custom reading settings
| 0x6B00 | 0x6B00 | 27392 | 27392 | The number of bytes has been set | uint16 | R/W | 1
| 0x6B01 | 0x6B01 | 27393 | 27393 | 1st register id | uint16 | R/W | 1
| 0x6B02 | 0x6B02 | 27394 | 27394 | 2nd register id | uint16 | R/W | 1
| 0x6B03 | 0x6B03 | 27395 | 27395 | 3rd register id | uint16 | R/W | 1
| 0x6B04 | 0x6B04 | 27396 | 27396 | 4th register id | uint16 | R/W | 1
| 0x6B05 | 0x6B05 | 27397 | 27397 | 5th register id | uint16 | R/W | 1
| 0x6B06 | 0x6B06 | 27398 | 27398 | 6th register id | uint16 | R/W | 1
| 0x6B07 | 0x6B07 | 27399 | 27399 | 7th register id | uint16 | R/W | 1
| 0x6B08 | 0x6B08 | 27400 | 27400 | 8th register id | uint16 | R/W | 1
| 0x6B09 | 0x6B09 | 27401 | 27401 | 9th register id | uint16 | R/W | 1
| 0x6B0A | 0x6B0A | 27402 | 27402 | 10th register id | uint16 | R/W | 1
| 0x6B0B | 0x6B0B | 27403 | 27403 | 11th register id | uint16 | R/W | 1
| 0x6B0C | 0x6B0C | 27404 | 27404 | 12th register id | uint16 | R/W | 1
| 0x6B0D | 0x6B0D | 27405 | 27405 | 13th register id | uint16 | R/W | 1
| 0x6B0E | 0x6B0E | 27406 | 27406 | 14th register id | uint16 | R/W | 1
| 0x6B0F | 0x6B0F | 27407 | 27407 | 15th register id | uint16 | R/W | 1
| 0x6B10 | 0x6B10 | 27408 | 27408 | 16th register id | uint16 | R/W | 1
| 0x6B11 | 0x6B11 | 27409 | 27409 | 17th register id | uint16 | R/W | 1
| 0x6B12 | 0x6B12 | 27410 | 27410 | 18th register id | uint16 | R/W | 1
| 0x6B13 | 0x6B13 | 27411 | 27411 | 19th register id | uint16 | R/W | 1
| 0x6B14 | 0x6B14 | 27412 | 27412 | 20th register id | uint16 | R/W | 1
| 0x6B15 | 0x6B15 | 27413 | 27413 | 21st register id | uint16 | R/W | 1
| 0x6B16 | 0x6B16 | 27414 | 27414 | 22nd register id | uint16 | R/W | 1
| 0x6B17 | 0x6B17 | 27415 | 27415 | 23rd register id | uint16 | R/W | 1
| 0x6B18 | 0x6B18 | 27416 | 27416 | 24th register id | uint16 | R/W | 1
| 0x6B19 | 0x6B19 | 27417 | 27417 | 25th register id | uint16 | R/W | 1
| 0x6B1A | 0x6B1A | 27418 | 27418 | 26th register id | uint16 | R/W | 1
| 0x6B1B | 0x6B1B | 27419 | 27419 | 27th register id | uint16 | R/W | 1
| 0x6B1C | 0x6B1C | 27420 | 27420 | 28th register id | uint16 | R/W | 1
| 0x6B1D | 0x6B1D | 27421 | 27421 | 29th register id | uint16 | R/W | 1
| 0x6B1E | 0x6B1E | 27422 | 27422 | 30th register id | uint16 | R/W | 1
31th-50th are reserved. | 0x6B1F | 0x6B1F | 27423 | 27423 | 31st register id | uint16 | R/W | 1
| 0x6B20 | 0x6B20 | 27424 | 27424 | 32nd register id | uint16 | R/W | 1
| 0x6B21 | 0x6B21 | 27425 | 27425 | 33rd register id | uint16 | R/W | 1
| 0x6B22 | 0x6B22 | 27426 | 27426 | 34th register id | uint16 | R/W | 1
| 0x6B23 | 0x6B23 | 27427 | 27427 | 35th register id | uint16 | R/W | 1
| 0x6B24 | 0x6B24 | 27428 | 27428 | 36th register id | uint16 | R/W | 1
| 0x6B25 | 0x6B25 | 27429 | 27429 | 37th register id | uint16 | R/W | 1
| 0x6B26 | 0x6B26 | 27430 | 27430 | 38th register id | uint16 | R/W | 1
| 0x6B27 | 0x6B27 | 27431 | 27431 | 39th register id | uint16 | R/W | 1
| 0x6B28 | 0x6B28 | 27432 | 27432 | 40th register id | uint16 | R/W | 1
| 0x6B29 | 0x6B29 | 27433 | 27433 | 41st register id | uint16 | R/W | 1
| 0x6B2A | 0x6B2A | 27434 | 27434 | 42nd register id | uint16 | R/W | 1
| 0x6B2B | 0x6B2B | 27435 | 27435 | 43rd register id | uint16 | R/W | 1
| 0x6B2C | 0x6B2C | 27436 | 27436 | 44th register id | uint16 | R/W | 1
| 0x6B2D | 0x6B2D | 27437 | 27437 | 45th register id | uint16 | R/W | 1
| 0x6B2E | 0x6B2E | 27438 | 27438 | 46th register id | uint16 | R/W | 1
| 0x6B2F | 0x6B2F | 27439 | 27439 | 47th register id | uint16 | R/W | 1
| 0x6B30 | 0x6B30 | 27440 | 27440 | 48th register id | uint16 | R/W | 1
| 0x6B31 | 0x6B31 | 27441 | 27441 | 49th register id | uint16 | R/W | 1
| 0x6B32 | 0x6B32 | 27442 | 27442 | 50th register id | uint16 | R/W | 1

## Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default
Real-time Parameters (float) | 0x3000 | 0x3001 | 12288 | 12289 | V(Measured or Compensated) | float | R | 2
| 0x3002 | 0x3003 | 12290 | 12291 | Current | float | R | 2
| 0x3004 | 0x3005 | 12292 | 12293 | Power | float | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Voltage Ripple Factor | float | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Current Ripple Factor | float | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Demand Current import | float | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Demand Current export | float | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Demand Power import | float | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Demand Power export | float | R | 2
| 0x3012 | 0x3013 | 12306 | 12307 | V(Measured) | float | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | V(Compensated) | float | R | 2
Real-time Parameters (float) -High Speed | 0x3100 | 0x3101 | 12544 | 12545 | V(Measured or Compensated) | float | R | 2
| 0x3102 | 0x3103 | 12546 | 12547 | Current | float | R | 2
| 0x3104 | 0x3105 | 12548 | 12549 | Power | float | R | 2
| 0x3106 | 0x3107 | 12550 | 12551 | V(Measured) | float | R | 2
| 0x3108 | 0x3109 | 12552 | 12553 | V(Compensated) | float | R | 2
Real-time Parameters (Int) | 0x3200 | 0x3200 | 12800 | 12800 | V(Measured or Compensated) | int16_t | R | 1 | 10x amplification
| 0x3201 | 0x3201 | 12801 | 12801 | Current | int16_t | R | 1 | 10x amplification
| 0x3202 | 0x3202 | 12802 | 12802 | Power | int16_t | R | 1 | 10x amplification
| 0x3203 | 0x3203 | 12803 | 12803 | Voltage Ripple Factor | int16_t | R | 1 | 1000x amplification
| 0x3204 | 0x3204 | 12804 | 12804 | Current Ripple Factor | int16_t | R | 1 | 1000x amplification
| 0x3205 | 0x3205 | 12805 | 12805 | Demand Current import | int16_t | R | 1 | 100x amplification
| 0x3206 | 0x3206 | 12806 | 12806 | Demand Current export | int16_t | R | 1 | 100x amplification
| 0x3207 | 0x3207 | 12807 | 12807 | Demand Power import | int16_t | R | 1 | 100x amplification
| 0x3208 | 0x3208 | 12808 | 12808 | Demand Power export | int16_t | R | 1 | 100x amplification
| 0x3209 | 0x3209 | 12809 | 12809 | V(Measured) | int16_t | R | 1 | 10x amplification
| 0x320A | 0x320A | 12810 | 12810 | V(Compensated) | int16_t | R | 1 | 10x amplification
Real-time Parameters (Int) - High Speed | 0x3300 | 0x3300 | 13056 | 13056 | V(Measured or Compensated) | int16_t | R | 1 | 10x amplification
| 0x3301 | 0x3301 | 13057 | 13057 | Current | int16_t | R | 1 | 100x amplification
| 0x3302 | 0x3302 | 13058 | 13058 | Power | int16_t | R | 1 | 100x amplification
| 0x3303 | 0x3303 | 13059 | 13059 | V(Measured) | int16_t | R | 1 | 10x amplification
| 0x3304 | 0x3304 | 13060 | 13060 | V(Compensated) | int16_t | R | 1 | 10x amplification
Energy & Charge | 0x4000 | 0x4003 | 16384 | 16387 | Import Energy | double | R/W | 4
| 0x4004 | 0x4007 | 16388 | 16391 | Export Energy | double | R/W | 4
| 0x4008 | 0x400B | 16392 | 16395 | Net Energy | double | R/W | 4
| 0x400C | 0x400F | 16396 | 16399 | Total Energy | double | R/W | 4
| 0x4010 | 0x4013 | 16400 | 16403 | Import Charge | double | R/W | 4
| 0x4014 | 0x4017 | 16404 | 16407 | Export Charge | double | R/W | 4
| 0x4018 | 0x401B | 16408 | 16411 | Net Charge | double | R/W | 4
| 0x401C | 0x401F | 16412 | 16415 | Total Charge | double | R/W | 4

## Max, Min
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | Range | Default
Max | 0x4136 | 0x4137 | 16694 | 16695 | V Max Value | float | R | 2
| 0x4138 | 0x413E | 16696 | 16702 | V Max Timestamp ( year： uint16_t month： uint16_t day： uint16_t hour： uint16_t min： uint16_t sec： uint16_t millesecond: uint16_t ) | timestamp | R | 7 | 7th reg is the millesecond value
| 0x413F | 0x4140 | 16703 | 16704 | I Max Value | float | R | 2
| 0x4141 | 0x4147 | 16705 | 16711 | I Max Timestamp | timestamp | R | 7
| 0x4148 | 0x4149 | 16712 | 16713 | P Max Value | float | R | 2
| 0x414A | 0x4150 | 16714 | 16720 | P Max Timestamp | timestamp | R | 7
| 0x4151 | 0x4152 | 16721 | 16722 | Ripple factor U Max Value | float | R | 2
| 0x4153 | 0x4159 | 16723 | 16729 | Ripple factor U Max Timestamp | timestamp | R | 7
| 0x415A | 0x415B | 16730 | 16731 | Ripple factor I Max Value | float | R | 2
| 0x415C | 0x4162 | 16732 | 16738 | Ripple factor I Max Timestamp | timestamp | R | 7
Demand Max | 0x4163 | 0x4164 | 16739 | 16740 | Demand I import Max Value | float | R | 2
| 0x4165 | 0x416B | 16741 | 16747 | Demand I import Max Timestamp ( year： uint16_t month： uint16_t day： uint16_t hour： uint16_t min： uint16_t sec： uint16_t millesecond: uint16_t ) | timestamp | R | 7
| 0x416C | 0x416D | 16748 | 16749 | Demand I export Max Value | float | R | 2
| 0x416E | 0x4174 | 16750 | 16756 | Demand I export Max Timestamp | timestamp | R | 7
| 0x4175 | 0x4176 | 16757 | 16758 | Demand P import Max Value | float | R | 2
| 0x4177 | 0x417D | 16759 | 16765 | Demand P import Max Timestamp | timestamp | R | 7
| 0x417E | 0x417F | 16766 | 16767 | Demand P export Max Value | float | R | 2
| 0x4180 | 0x4186 | 16768 | 16774 | Demand P export Max Timestamp | timestamp | R | 7
Min | 0x4187 | 0x4188 | 16775 | 16776 | V Min Value | float | R | 2
| 0x4189 | 0x418F | 16777 | 16783 | V Min Timestamp ( year： uint16_t month： uint16_t day： uint16_t hour： uint16_t min： uint16_t sec： uint16_t millesecond: uint16_t ) | timestamp | R | 7
| 0x4190 | 0x4191 | 16784 | 16785 | I Min Value | float | R | 2
| 0x4192 | 0x4198 | 16786 | 16792 | I Min Timestamp | timestamp | R | 7
| 0x4199 | 0x419A | 16793 | 16794 | P Min Value | float | R | 2
| 0x419B | 0x41A1 | 16795 | 16801 | P Min Timestamp | timestamp | R | 7
| 0x41A2 | 0x41A3 | 16802 | 16803 | Ripple factor U Min Value | float | R | 2
| 0x41A4 | 0x41AA | 16804 | 16810 | Ripple factor U Min Timestamp | timestamp | R | 7
| 0x41AB | 0x41AC | 16811 | 16812 | Ripple factor I Min Value | float | R | 2
| 0x41AD | 0x41B3 | 16813 | 16819 | Ripple factor I Min Timestamp | timestamp | R | 7