## Real-time Parameters
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Real-time Parameter | 0x2000 | 0x2001 | 8192 | 8193 | Total Current | float | R | 2
(0x03 Read) | 0x2002 | 0x2003 | 8194 | 8195 | Phase A Current | float | R | 2
| 0x2004 | 0x2005 | 8196 | 8197 | Phase B Current | float | R | 2
| 0x2006 | 0x2007 | 8198 | 8199 | Phase C Current | float | R | 2
| 0x2008 | 0x2009 | 8200 | 8201 | Phase Average Voltage | float | R | 2
| 0x200A | 0x200B | 8202 | 8203 | Phase A Voltage | float | R | 2
| 0x200C | 0x200D | 8204 | 8205 | Phase B Voltage | float | R | 2
| 0x200E | 0x200F | 8206 | 8207 | Phase C Voltage | float | R | 2
| 0x2010 | 0x2011 | 8208 | 8209 | Line Average Voltage | float | R | 2
| 0x2012 | 0x2013 | 8210 | 8211 | Line AB Voltage | float | R | 2
| 0x2014 | 0x2015 | 8212 | 8213 | Line BC Voltage | float | R | 2
| 0x2016 | 0x2017 | 8214 | 8215 | Line CA Voltage | float | R | 2
| 0x2018 | 0x2019 | 8216 | 8217 | Frequency | float | R | 2
| 0x201A | 0x201B | 8218 | 8219 | Total Active Power | float | R | 2
| 0x201C | 0x201D | 8220 | 8221 | Phase A Active Power | float | R | 2
| 0x201E | 0x201F | 8222 | 8223 | Phase B Active Power | float | R | 2
| 0x2020 | 0x2021 | 8224 | 8225 | Phase C Active Power | float | R | 2
| 0x2022 | 0x2023 | 8226 | 8227 | Total Apparent Power | float | R | 2
| 0x2024 | 0x2025 | 8228 | 8229 | Phase A Apparent Power | float | R | 2
| 0x2026 | 0x2027 | 8230 | 8231 | Phase B Apparent Power | float | R | 2
| 0x2028 | 0x2029 | 8232 | 8233 | Phase C Apparent Power | float | R | 2
| 0x202A | 0x202B | 8234 | 8235 | Total Reactive Power | float | R | 2
| 0x202C | 0x202D | 8236 | 8237 | Phase A Reactive Power | float | R | 2
| 0x202E | 0x202F | 8238 | 8239 | Phase B Reactive Power | float | R | 2
| 0x2030 | 0x2031 | 8240 | 8241 | Phase C Reactive Power | float | R | 2
| 0x2032 | 0x2033 | 8242 | 8243 | Power Factor | float | R | 2
| 0x2034 | 0x2035 | 8244 | 8245 | PF phase A | float | R | 2
| 0x2036 | 0x2037 | 8246 | 8247 | PF phase B | float | R | 2
| 0x2038 | 0x2039 | 8248 | 8249 | PF phase C | float | R | 2
| 0x203A | 0x203B | 8250 | 8251 | Phase Angle of V1 to V1 | float | R | 2
| 0x203C | 0x203D | 8252 | 8253 | Phase Angle of V2 to V1 | float | R | 2
| 0x203E | 0x203F | 8254 | 8255 | Phase Angle of V3 to V1 | float | R | 2
| 0x2040 | 0x2041 | 8256 | 8257 | Phase Angle of I1 to V1 | float | R | 2
| 0x2042 | 0x2043 | 8258 | 8259 | Phase Angle of I2 to V1 | float | R | 2
| 0x2044 | 0x2045 | 8260 | 8261 | Phase Angle of I3 to V1 | float | R | 2
Energy Reading | 0x2046 | 0x2047 | 8262 | 8263 | Total Active Energy Exported | int32 | R/W | 2
(0x03 Read, 0x10 Write) | 0x2048 | 0x2049 | 8264 | 8265 | Total Active Energy Exported in Phase A | int32 | R/W | 2
| 0x204A | 0x204B | 8266 | 8267 | Total Active Energy Exported in Phase B | int32 | R/W | 2
| 0x204C | 0x204D | 8268 | 8269 | Total Active Energy Exported in Phase C | int32 | R/W | 2
| 0x204E | 0x204F | 8270 | 8271 | Total Active Energy Imported | int32 | R/W | 2
| 0x2050 | 0x2051 | 8272 | 8273 | Total Active Energy Imported in Phase A | int32 | R/W | 2
| 0x2052 | 0x2053 | 8274 | 8275 | Total Active Energy Imported in Phase B | int32 | R/W | 2
| 0x2054 | 0x2055 | 8276 | 8277 | Total Active Energy Imported in Phase C | int32 | R/W | 2
| 0x2056 | 0x2057 | 8278 | 8279 | Total Apparent Power Exported | int32 | R/W | 2
| 0x2058 | 0x2059 | 8280 | 8281 | Total Apparent Power Exported in Phase A | int32 | R/W | 2
| 0x205A | 0x205B | 8282 | 8283 | Total Apparent Power Exported in Phase B | int32 | R/W | 2
| 0x205C | 0x205D | 8284 | 8285 | Total Apparent Power Exported in Phase C | int32 | R/W | 2
| 0x205E | 0x205F | 8286 | 8287 | Total Apparent Power Imported | int32 | R/W | 2
| 0x2060 | 0x2061 | 8288 | 8289 | Total Apparent Power Imported in Phase A | int32 | R/W | 2
| 0x2062 | 0x2063 | 8290 | 8291 | Total Apparent Power Imported in Phase B | int32 | R/W | 2
| 0x2064 | 0x2065 | 8292 | 8293 | Total Apparent Power Imported in Phase C | int32 | R/W | 2
| 0x2066 | 0x2067 | 8294 | 8295 | Total Reactive Imported Q1 | int32 | R/W | 2
| 0x2068 | 0x2069 | 8296 | 8297 | Total Reactive Imported Q1 Phase A | int32 | R/W | 2
| 0x206A | 0x206B | 8298 | 8299 | Total Reactive Imported Q1 Phase B | int32 | R/W | 2
| 0x206C | 0x206D | 8300 | 8301 | Total Reactive Imported Q1 Phase C | int32 | R/W | 2
| 0x206E | 0x206F | 8302 | 8303 | Total Reactive Imported Q2 | int32 | R/W | 2
| 0x2070 | 0x2071 | 8304 | 8305 | Total Reactive Imported Q2 Phase A | int32 | R/W | 2
| 0x2072 | 0x2073 | 8306 | 8307 | Total Reactive Imported Q2 Phase B | int32 | R/W | 2
| 0x2074 | 0x2075 | 8308 | 8309 | Total Reactive Imported Q2 Phase C | int32 | R/W | 2
| 0x2076 | 0x2077 | 8310 | 8311 | Total Reactive Imported Q3 | int32 | R/W | 2
| 0x2078 | 0x2079 | 8312 | 8313 | Total Reactive Imported Q3 Phase A | int32 | R/W | 2
| 0x207A | 0x207B | 8314 | 8315 | Total Reactive Imported Q3 Phase B | int32 | R/W | 2
| 0x207C | 0x207D | 8316 | 8317 | Total Reactive Imported Q3 Phase C | int32 | R/W | 2
| 0x207E | 0x207F | 8318 | 8319 | Total Reactive Imported Q4 | int32 | R/W | 2
| 0x2080 | 0x2081 | 8320 | 8321 | Total Reactive Imported Q4 Phase A | int32 | R/W | 2
| 0x2082 | 0x2083 | 8322 | 8323 | Total Reactive Imported Q4 Phase B | int32 | R/W | 2
| 0x2084 | 0x2085 | 8324 | 8325 | Total Reactive Imported Q4 Phase C | int32 | R/W | 2

## Self-defined Measured Parameter
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Real-time Parameter | 0x1200 | 0x1201 | 4608 | 4609 | Neutral Current | float | R | 2 | 0~9999A
(0x03 Read) | 0x1202 | 0x1203 | 4610 | 4611 | Phase Voltage | float | R | 2 | 0~9999V
| 0x1204 | 0x1205 | 4612 | 4613 | Temperature of chips | float | R | 2 | -40°C ~ 80°C
| 0x1206 | 0x1207 | 4614 | 4615 | Load type | float | R | 2 | 67(‘C’); 76(‘L’); 82(‘R’)
| 0x1208 | 0x1209 | 4616 | 4617 | system active power demand | float | R | 2
| 0x120A | 0x120B | 4618 | 4619 | system Reactive power demand | float | R | 2
| 0x120C | 0x120D | 4620 | 4621 | system apparent power demand | float | R | 2
| 0x120E | 0x120F | 4622 | 4623 | Phase A current demand | float | R | 2
| 0x1210 | 0x1211 | 4624 | 4625 | Phase B current demand | float | R | 2
| 0x1212 | 0x1213 | 4626 | 4627 | Phase C current demand | float | R | 2
| 0x1214 | 0x1215 | 4628 | 4629 | System Active Power Demand Prediction | float | R | 2
| 0x1216 | 0x1217 | 4630 | 4631 | System Reactive Power Demand Prediction | float | R | 2
| 0x1218 | 0x1219 | 4632 | 4633 | System Apparent Power Demand Prediction | float | R | 2
| 0x121A | 0x121B | 4634 | 4635 | Phase A Current Deamnd Prediction | float | R | 2
| 0x121C | 0x121D | 4636 | 4637 | Phase B Current Deamnd Prediction | float | R | 2
| 0x121E | 0x121F | 4638 | 4639 | Phase C Current Deamnd Prediction | float | R | 2
| 0x1220 | 0x1221 | 4640 | 4641 | Residual Current | float | R | 2

## Self-defined Energy Data
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Energy reading | 0x1300 | 0x1301 | 4864 | 4865 | Total Active Energy | int32 | R/W | 2 | 0~+999999999
(0x03 Read, 0x10 Write) | 0x1302 | 0x1303 | 4866 | 4867 | Total Active Energy tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1304 | 0x1305 | 4868 | 4869 | Total Active Energy tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1306 | 0x1307 | 4870 | 4871 | Total Active Energy tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1308 | 0x1309 | 4872 | 4873 | Total Active Energy tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x130A | 0x130B | 4874 | 4875 | Net Active Energy | int32 | R/W | 2 | -999999999~+999999999
| 0x130C | 0x130D | 4876 | 4877 | Net Active Energy tariff 1 | int32 | R/W | 2 | -999999999~+999999999
| 0x130E | 0x130F | 4878 | 4879 | Net Active Energy tariff 2 | int32 | R/W | 2 | -999999999~+999999999
| 0x1310 | 0x1311 | 4880 | 4881 | Net Active Energy tariff 3 | int32 | R/W | 2 | -999999999~+999999999
| 0x1312 | 0x1313 | 4882 | 4883 | Net Active Energy tariff 4 | int32 | R/W | 2 | -999999999~+999999999
| 0x1314 | 0x1315 | 4884 | 4885 | Imported Active Energy tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1316 | 0x1317 | 4886 | 4887 | Imported Active Energy tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1318 | 0x1319 | 4888 | 4889 | Imported Active Energy tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x131A | 0x131B | 4890 | 4891 | Imported Active Energy tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x131C | 0x131D | 4892 | 4893 | Exported Active Energy tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x131E | 0x131F | 4894 | 4895 | Exported Active Energy tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1320 | 0x1321 | 4896 | 4897 | Exported Active Energy tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1322 | 0x1323 | 4898 | 4899 | Exported Active Energy tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x1324 | 0x1325 | 4900 | 4901 | Total Reactive Energy Imported | int32 | R/W | 2 | 0~+999999999
| 0x1326 | 0x1327 | 4902 | 4903 | Total Reactive Energy Imported tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1328 | 0x1329 | 4904 | 4905 | Total Reactive Energy Imported tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x132A | 0x132B | 4906 | 4907 | Total Reactive Energy Imported tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x132C | 0x132D | 4908 | 4909 | Total Reactive Energy Imported tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x132E | 0x132F | 4910 | 4911 | Total Reactive Energy Exported | int32 | R/W | 2 | 0~+999999999
| 0x1330 | 0x1331 | 4912 | 4913 | Exported Reactive Energy tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1332 | 0x1333 | 4914 | 4915 | Exportdd Reactive Energy tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1334 | 0x1335 | 4916 | 4917 | Exported Reactive Energy tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1336 | 0x1337 | 4918 | 4919 | Exported Reactive Energy tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x1338 | 0x1339 | 4920 | 4921 | Total Reactive Energy | int32 | R/W | 2 | 0~+999999999
| 0x133A | 0x133B | 4922 | 4923 | Total Reactive Energy tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x133C | 0x133D | 4924 | 4925 | Total Reactive Energy tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x133E | 0x133F | 4926 | 4927 | Total Reactive Energy tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1340 | 0x1341 | 4928 | 4929 | Total Reactive Energy tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x1342 | 0x1343 | 4930 | 4931 | Net Reactive Energy | int32 | R/W | 2 | -999999999~+999999999
| 0x1344 | 0x1345 | 4932 | 4933 | Net Reactive Energy tariff 1 | int32 | R/W | 2 | -999999999~+999999999
| 0x1346 | 0x1347 | 4934 | 4935 | Net Reactive Energy tariff 2 | int32 | R/W | 2 | -999999999~+999999999
| 0x1348 | 0x1349 | 4936 | 4937 | Net Reactive Energy tariff 3 | int32 | R/W | 2 | -999999999~+999999999
| 0x134A | 0x134B | 4938 | 4939 | Net Reactive Energy tariff 4 | int32 | R/W | 2 | -999999999~+999999999
| 0x134C | 0x134D | 4940 | 4941 | Total Reactive Energy Imported Q1 tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x134E | 0x134F | 4942 | 4943 | Total Reactive Energy Imported Q1 tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1350 | 0x1351 | 4944 | 4945 | Total Reactive Energy Imported Q1 tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1352 | 0x1353 | 4946 | 4947 | Total Reactive Energy Imported Q1 tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x1354 | 0x1355 | 4948 | 4949 | Total Reactive Energy Imported Q2 tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1356 | 0x1357 | 4950 | 4951 | Total Reactive Energy Imported Q2 tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1358 | 0x1359 | 4952 | 4953 | Total Reactive Energy Imported Q2 tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x135A | 0x135B | 4954 | 4955 | Total Reactive Energy Imported Q2 tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x135C | 0x135D | 4956 | 4957 | Total Reactive Energy Exported Q3 tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x135E | 0x135F | 4958 | 4959 | Total Reactive Energy Exported Q3 tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1360 | 0x1361 | 4960 | 4961 | Total Reactive Energy Exported Q3 tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x1362 | 0x1363 | 4962 | 4963 | Total Reactive Energy Exported Q3 tariff 4 | int32 | R/W | 2 | 0~+999999999
| 0x1364 | 0x1365 | 4964 | 4965 | Total Reactive Energy Exported Q4 tariff 1 | int32 | R/W | 2 | 0~+999999999
| 0x1366 | 0x1367 | 4966 | 4967 | Total Reactive Energy Exported Q4 tariff 2 | int32 | R/W | 2 | 0~+999999999
| 0x1368 | 0x1369 | 4968 | 4969 | Total Reactive Energy Exported Q4 tariff 3 | int32 | R/W | 2 | 0~+999999999
| 0x136A | 0x136B | 4970 | 4971 | Total Reactive Energy Exported Q4 tariff 4 | int32 | R/W | 2 | 0~+999999999

## Energy Monthly Display Data
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Prior Month Accumulated Energy Data | 0x1400 | 0x1401 | 5120 | 5121 | Total Active Energy Imported | int32 | R | 2 | 0~+999999999
(0x03 Read) | 0x1402 | 0x1403 | 5122 | 5123 | Total Active Energy Imported in phase A | int32 | R | 2 | 0~+999999999
| 0x1404 | 0x1405 | 5124 | 5125 | Total Active Energy Imported in phase B | int32 | R | 2 | 0~+999999999
| 0x1406 | 0x1407 | 5126 | 5127 | Total Active Energy Imported in phase C | int32 | R | 2 | 0~+999999999
| 0x1408 | 0x1409 | 5128 | 5129 | Total Active Energy Imported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x140A | 0x140B | 5130 | 5131 | Total Active Energy Imported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x140C | 0x140D | 5132 | 5133 | Total Active Energy Imported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x140E | 0x140F | 5134 | 5135 | Total Active Energy Imported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1410 | 0x1411 | 5136 | 5137 | Total Active Energy Exported | int32 | R | 2 | 0~+999999999
| 0x1412 | 0x1413 | 5138 | 5139 | Total Active Energy Exported in phase A | int32 | R | 2 | 0~+999999999
| 0x1414 | 0x1415 | 5140 | 5141 | Total Active Energy Exported in phase B | int32 | R | 2 | 0~+999999999
| 0x1416 | 0x1417 | 5142 | 5143 | Total Active Energy Exported in phase C | int32 | R | 2 | 0~+999999999
| 0x1418 | 0x1419 | 5144 | 5145 | Total Active Energy Exported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x141A | 0x141B | 5146 | 5147 | Total Active Energy Exported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x141C | 0x141D | 5148 | 5149 | Total Active Energy Exported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x141E | 0x141F | 5150 | 5151 | Total Active Energy Exported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1420 | 0x1421 | 5152 | 5153 | Total Active Energy | int32 | R | 2 | 0~+999999999
| 0x1422 | 0x1423 | 5154 | 5155 | Total Active Energy tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1424 | 0x1425 | 5156 | 5157 | Total Active Energy tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1426 | 0x1427 | 5158 | 5159 | Total Active Energy tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1428 | 0x1429 | 5160 | 5161 | Total Active Energy tariff 4 | int32 | R | 2 | 0~+999999999
| 0x142A | 0x142B | 5162 | 5163 | Net Active Energy | int32 | R | 2 | -999999999~+999999999
| 0x142C | 0x142D | 5164 | 5165 | Net Active Energy tariff 1 | int32 | R | 2 | -999999999~+999999999
| 0x142E | 0x142F | 5166 | 5167 | Net Active Energy tariff 2 | int32 | R | 2 | -999999999~+999999999
| 0x1430 | 0x1431 | 5168 | 5169 | Net Active Energy tariff 3 | int32 | R | 2 | -999999999~+999999999
| 0x1432 | 0x1433 | 5170 | 5171 | Net Active Energy tariff 4 | int32 | R | 2 | -999999999~+999999999
| 0x1434 | 0x1435 | 5172 | 5173 | Total Reactive energy Imported Q1 | int32 | R | 2 | 0~+999999999
| 0x1436 | 0x1437 | 5174 | 5175 | Total Reactive energy Imported Q1 in phase A | int32 | R | 2 | 0~+999999999
| 0x1438 | 0x1439 | 5176 | 5177 | Total Reactive energy Imported Q1 in phase B | int32 | R | 2 | 0~+999999999
| 0x143A | 0x143B | 5178 | 5179 | Total Reactive energy Imported Q1 in phase C | int32 | R | 2 | 0~+999999999
| 0x143C | 0x143D | 5180 | 5181 | Total Reactive energy Imported Q1 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x143E | 0x143F | 5182 | 5183 | Total Reactive energy Imported Q1 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1440 | 0x1441 | 5184 | 5185 | Total Reactive energy Imported Q1 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1442 | 0x1443 | 5186 | 5187 | Total Reactive energy Imported Q1 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1444 | 0x1445 | 5188 | 5189 | Total Reactive energy Imported Q2 | int32 | R | 2 | 0~+999999999
| 0x1446 | 0x1447 | 5190 | 5191 | Total Reactive energy Imported Q2 phase A | int32 | R | 2 | 0~+999999999
| 0x1448 | 0x1449 | 5192 | 5193 | Total Reactive energy Imported Q2 phase B | int32 | R | 2 | 0~+999999999
| 0x144A | 0x144B | 5194 | 5195 | Total Reactive energy Imported Q2 phase C | int32 | R | 2 | 0~+999999999
| 0x144C | 0x144D | 5196 | 5197 | Total Reactive energy Imported Q2 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x144E | 0x144F | 5198 | 5199 | Total Reactive energy Imported Q2 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1450 | 0x1451 | 5200 | 5201 | Total Reactive energy Imported Q2 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1452 | 0x1453 | 5202 | 5203 | Total Reactive energy Imported Q2 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1454 | 0x1455 | 5204 | 5205 | Total Reactive energy Exported Q3 | int32 | R | 2 | 0~+999999999
| 0x1456 | 0x1457 | 5206 | 5207 | Total Reactive energy Exported Q3 phase A | int32 | R | 2 | 0~+999999999
| 0x1458 | 0x1459 | 5208 | 5209 | Total Reactive energy Exported Q3 phase B | int32 | R | 2 | 0~+999999999
| 0x145A | 0x145B | 5210 | 5211 | Total Reactive energy Exported Q3 phase C | int32 | R | 2 | 0~+999999999
| 0x145C | 0x145D | 5212 | 5213 | Total Reactive energy Exported Q3 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x145E | 0x145F | 5214 | 5215 | Total Reactive energy Exported Q3 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1460 | 0x1461 | 5216 | 5217 | Total Reactive energy Exported Q3 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1462 | 0x1463 | 5218 | 5219 | Total Reactive energy Exported Q3 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1464 | 0x1465 | 5220 | 5221 | Total VAR-hours Exported energy d Q4 | int32 | R | 2 | 0~+999999999
| 0x1466 | 0x1467 | 5222 | 5223 | Total Reactive energy Exported Q4 phase A | int32 | R | 2 | 0~+999999999
| 0x1468 | 0x1469 | 5224 | 5225 | Total Reactive energy Exported Q4 phase B | int32 | R | 2 | 0~+999999999
| 0x146A | 0x146B | 5226 | 5227 | Total Reactive energy Exported Q4 phase C | int32 | R | 2 | 0~+999999999
| 0x146C | 0x146D | 5228 | 5229 | Total Reactive energy Exported Q4 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x146E | 0x146F | 5230 | 5231 | Total Reactive energy Exported Q4 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1470 | 0x1471 | 5232 | 5233 | Total Reactive energy Exported Q4 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1472 | 0x1473 | 5234 | 5235 | Total Reactive energy Exported Q4 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1474 | 0x1475 | 5236 | 5237 | Total Reactive energy Imported | int32 | R | 2 | 0~+999999999
| 0x1476 | 0x1477 | 5238 | 5239 | Total Reactive energy Imported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1478 | 0x1479 | 5240 | 5241 | Total Reactive energy Imported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x147A | 0x147B | 5242 | 5243 | Total Reactive energy Imported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x147C | 0x147D | 5244 | 5245 | Total Reactive energy Imported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x147E | 0x147F | 5246 | 5247 | Total Reactive energy Exported | int32 | R | 2 | 0~+999999999
| 0x1480 | 0x1481 | 5248 | 5249 | Total Reactive energy Exported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1482 | 0x1483 | 5250 | 5251 | Total Reactive energy Exported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1484 | 0x1485 | 5252 | 5253 | Total Reactive energy Exported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1486 | 0x1487 | 5254 | 5255 | Total Reactive energy Exported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1488 | 0x1489 | 5256 | 5257 | Total Reactive Energy | int32 | R | 2 | 0~+999999999
| 0x148A | 0x148B | 5258 | 5259 | Total Reactive Energy tariff 1 | int32 | R | 2 | 0~+999999999
| 0x148C | 0x148D | 5260 | 5261 | Total Reactive Energy tariff 2 | int32 | R | 2 | 0~+999999999
| 0x148E | 0x148F | 5262 | 5263 | Total Reactive Energy tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1490 | 0x1491 | 5264 | 5265 | Total Reactive Energy tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1492 | 0x1493 | 5266 | 5267 | Net Reactive Energy | int32 | R | 2 | -999999999~+999999999
| 0x1494 | 0x1495 | 5268 | 5269 | Net Reactive Energy tariff 1 | int32 | R | 2 | -999999999~+999999999
| 0x1496 | 0x1497 | 5270 | 5271 | Net Reactive Energy tariff 2 | int32 | R | 2 | -999999999~+999999999
| 0x1498 | 0x1499 | 5272 | 5273 | Net Reactive Energy tariff 3 | int32 | R | 2 | -999999999~+999999999
| 0x149A | 0x149B | 5274 | 5275 | Net Reactive Energy tariff 4 | int32 | R | 2 | -999999999~+999999999
| 0x149C | 0x149D | 5276 | 5277 | Total Apparent Energy Imported | int32 | R | 2 | 0~+999999999
| 0x149E | 0x149F | 5278 | 5279 | Total Apparent Energy Imported phase A | int32 | R | 2 | 0~+999999999
| 0x14A0 | 0x14A1 | 5280 | 5281 | Total Apparent Energy Imported phase B | int32 | R | 2 | 0~+999999999
| 0x14A2 | 0x14A3 | 5282 | 5283 | Total Apparent Energy Imported phase C | int32 | R | 2 | 0~+999999999
| 0x14A4 | 0x14A5 | 5284 | 5285 | Total Apparent Energy Exported | int32 | R | 2 | 0~+999999999
| 0x14A6 | 0x14A7 | 5286 | 5287 | Total Apparent Energy Exported phase A | int32 | R | 2 | 0~+999999999
| 0x14A8 | 0x14A9 | 5288 | 5289 | Total Apparent Energy Exported phase B | int32 | R | 2 | 0~+999999999
| 0x14AA | 0x14AB | 5290 | 5291 | Total Apparent Energy Exported phase C | int32 | R | 2 | 0~+999999999
Prior Two-month Accumulated Energy Data | 0x1500 | 0x1501 | 5376 | 5377 | Total Active Energy Imported | int32 | R | 2 | 0~+999999999
(0x03 Read) | 0x1502 | 0x1503 | 5378 | 5379 | Total Active Energy Imported in phase A | int32 | R | 2 | 0~+999999999
| 0x1504 | 0x1505 | 5380 | 5381 | Total Active Energy Imported in phase B | int32 | R | 2 | 0~+999999999
| 0x1506 | 0x1507 | 5382 | 5383 | Total Active Energy Imported in phase C | int32 | R | 2 | 0~+999999999
| 0x1508 | 0x1509 | 5384 | 5385 | Total Active Energy Imported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x150A | 0x150B | 5386 | 5387 | Total Active Energy Imported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x150C | 0x150D | 5388 | 5389 | Total Active Energy Imported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x150E | 0x150F | 5390 | 5391 | Total Active Energy Imported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1510 | 0x1511 | 5392 | 5393 | Total Active Energy Exported | int32 | R | 2 | 0~+999999999
| 0x1512 | 0x1513 | 5394 | 5395 | Total Active Energy Exported in phase A | int32 | R | 2 | 0~+999999999
| 0x1514 | 0x1515 | 5396 | 5397 | Total Active Energy Exported in phase B | int32 | R | 2 | 0~+999999999
| 0x1516 | 0x1517 | 5398 | 5399 | Total Active Energy Exported in phase C | int32 | R | 2 | 0~+999999999
| 0x1518 | 0x1519 | 5400 | 5401 | Total Active Energy Exported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x151A | 0x151B | 5402 | 5403 | Total Active Energy Exported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x151C | 0x151D | 5404 | 5405 | Total Active Energy Exported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x151E | 0x151F | 5406 | 5407 | Total Active Energy Exported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1520 | 0x1521 | 5408 | 5409 | Total Active Energy | int32 | R | 2 | 0~+999999999
| 0x1522 | 0x1523 | 5410 | 5411 | Total Active Energy tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1524 | 0x1525 | 5412 | 5413 | Total Active Energy tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1526 | 0x1527 | 5414 | 5415 | Total Active Energy tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1528 | 0x1529 | 5416 | 5417 | Total Active Energy tariff 4 | int32 | R | 2 | 0~+999999999
| 0x152A | 0x152B | 5418 | 5419 | Net Active Energy | int32 | R | 2 | -999999999~+999999999
| 0x152C | 0x152D | 5420 | 5421 | Net Active Energy tariff 1 | int32 | R | 2 | -999999999~+999999999
| 0x152E | 0x152F | 5422 | 5423 | Net Active Energy tariff 2 | int32 | R | 2 | -999999999~+999999999
| 0x1530 | 0x1531 | 5424 | 5425 | Net Active Energy tariff 3 | int32 | R | 2 | -999999999~+999999999
| 0x1532 | 0x1533 | 5426 | 5427 | Net Active Energy tariff 4 | int32 | R | 2 | -999999999~+999999999
| 0x1534 | 0x1535 | 5428 | 5429 | Total Reactive energy Imported Q1 | int32 | R | 2 | 0~+999999999
| 0x1536 | 0x1537 | 5430 | 5431 | Total Reactive energy Imported Q1 in phase A | int32 | R | 2 | 0~+999999999
| 0x1538 | 0x1539 | 5432 | 5433 | Total Reactive energy Imported Q1 in phase B | int32 | R | 2 | 0~+999999999
| 0x153A | 0x153B | 5434 | 5435 | Total Reactive energy Imported Q1 in phase C | int32 | R | 2 | 0~+999999999
| 0x153C | 0x153D | 5436 | 5437 | Total Reactive energy Imported Q1 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x153E | 0x153F | 5438 | 5439 | Total Reactive energy Imported Q1 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1540 | 0x1541 | 5440 | 5441 | Total Reactive energy Imported Q1 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1542 | 0x1543 | 5442 | 5443 | Total Reactive energy Imported Q1 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1544 | 0x1545 | 5444 | 5445 | Total Reactive energy Imported Q2 | int32 | R | 2 | 0~+999999999
| 0x1546 | 0x1547 | 5446 | 5447 | Total Reactive energy Imported Q2 phase A | int32 | R | 2 | 0~+999999999
| 0x1548 | 0x1549 | 5448 | 5449 | Total Reactive energy Imported Q2 phase B | int32 | R | 2 | 0~+999999999
| 0x154A | 0x154B | 5450 | 5451 | Total Reactive energy Imported Q2 phase C | int32 | R | 2 | 0~+999999999
| 0x154C | 0x154D | 5452 | 5453 | Total Reactive energy Imported Q2 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x154E | 0x154F | 5454 | 5455 | Total Reactive energy Imported Q2 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1550 | 0x1551 | 5456 | 5457 | Total Reactive energy Imported Q2 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1552 | 0x1553 | 5458 | 5459 | Total Reactive energy Imported Q2 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1554 | 0x1555 | 5460 | 5461 | Total Reactive energy Exported Q3 | int32 | R | 2 | 0~+999999999
| 0x1556 | 0x1557 | 5462 | 5463 | Total Reactive energy Exported Q3 phase A | int32 | R | 2 | 0~+999999999
| 0x1558 | 0x1559 | 5464 | 5465 | Total Reactive energy Exported Q3 phase B | int32 | R | 2 | 0~+999999999
| 0x155A | 0x155B | 5466 | 5467 | Total Reactive energy Exported Q3 phase C | int32 | R | 2 | 0~+999999999
| 0x155C | 0x155D | 5468 | 5469 | Total Reactive energy Exported Q3 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x155E | 0x155F | 5470 | 5471 | Total Reactive energy Exported Q3 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1560 | 0x1561 | 5472 | 5473 | Total Reactive energy Exported Q3 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1562 | 0x1563 | 5474 | 5475 | Total Reactive energy Exported Q3 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1564 | 0x1565 | 5476 | 5477 | Total VAR-hours Exported energy d Q4 | int32 | R | 2 | 0~+999999999
| 0x1566 | 0x1567 | 5478 | 5479 | Total Reactive energy Exported Q4 phase A | int32 | R | 2 | 0~+999999999
| 0x1568 | 0x1569 | 5480 | 5481 | Total Reactive energy Exported Q4 phase B | int32 | R | 2 | 0~+999999999
| 0x156A | 0x156B | 5482 | 5483 | Total Reactive energy Exported Q4 phase C | int32 | R | 2 | 0~+999999999
| 0x156C | 0x156D | 5484 | 5485 | Total Reactive energy Exported Q4 tariff 1 | int32 | R | 2 | 0~+999999999
| 0x156E | 0x156F | 5486 | 5487 | Total Reactive energy Exported Q4 tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1570 | 0x1571 | 5488 | 5489 | Total Reactive energy Exported Q4 tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1572 | 0x1573 | 5490 | 5491 | Total Reactive energy Exported Q4 tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1574 | 0x1575 | 5492 | 5493 | Total Reactive energy Imported | int32 | R | 2 | 0~+999999999
| 0x1576 | 0x1577 | 5494 | 5495 | Total Reactive energy Imported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1578 | 0x1579 | 5496 | 5497 | Total Reactive energy Imported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x157A | 0x157B | 5498 | 5499 | Total Reactive energy Imported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x157C | 0x157D | 5500 | 5501 | Total Reactive energy Imported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x157E | 0x157F | 5502 | 5503 | Total Reactive energy Exported | int32 | R | 2 | 0~+999999999
| 0x1580 | 0x1581 | 5504 | 5505 | Total Reactive energy Exported tariff 1 | int32 | R | 2 | 0~+999999999
| 0x1582 | 0x1583 | 5506 | 5507 | Total Reactive energy Exported tariff 2 | int32 | R | 2 | 0~+999999999
| 0x1584 | 0x1585 | 5508 | 5509 | Total Reactive energy Exported tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1586 | 0x1587 | 5510 | 5511 | Total Reactive energy Exported tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1588 | 0x1589 | 5512 | 5513 | Total Reactive Energy | int32 | R | 2 | 0~+999999999
| 0x158A | 0x158B | 5514 | 5515 | Total Reactive Energy tariff 1 | int32 | R | 2 | 0~+999999999
| 0x158C | 0x158D | 5516 | 5517 | Total Reactive Energy tariff 2 | int32 | R | 2 | 0~+999999999
| 0x158E | 0x158F | 5518 | 5519 | Total Reactive Energy tariff 3 | int32 | R | 2 | 0~+999999999
| 0x1590 | 0x1591 | 5520 | 5521 | Total Reactive Energy tariff 4 | int32 | R | 2 | 0~+999999999
| 0x1592 | 0x1593 | 5522 | 5523 | Net Reactive Energy | int32 | R | 2 | -999999999~+999999999
| 0x1594 | 0x1595 | 5524 | 5525 | Net Reactive Energy tariff 1 | int32 | R | 2 | -999999999~+999999999
| 0x1596 | 0x1597 | 5526 | 5527 | Net Reactive Energy tariff 2 | int32 | R | 2 | -999999999~+999999999
| 0x1598 | 0x1599 | 5528 | 5529 | Net Reactive Energy tariff 3 | int32 | R | 2 | -999999999~+999999999
| 0x159A | 0x159B | 5530 | 5531 | Net Reactive Energy tariff 4 | int32 | R | 2 | -999999999~+999999999
| 0x159C | 0x159D | 5532 | 5533 | Total Apparent Energy Imported | int32 | R | 2 | 0~+999999999
| 0x159E | 0x159F | 5534 | 5535 | Total Apparent Energy Imported phase A | int32 | R | 2 | 0~+999999999
| 0x15A0 | 0x15A1 | 5536 | 5537 | Total Apparent Energy Imported phase B | int32 | R | 2 | 0~+999999999
| 0x15A2 | 0x15A3 | 5538 | 5539 | Total Apparent Energy Imported phase C | int32 | R | 2 | 0~+999999999
| 0x15A4 | 0x15A5 | 5540 | 5541 | Total Apparent Energy Exported | int32 | R | 2 | 0~+999999999
| 0x15A6 | 0x15A7 | 5542 | 5543 | Total Apparent Energy Exported phase A | int32 | R | 2 | 0~+999999999
| 0x15A8 | 0x15A9 | 5544 | 5545 | Total Apparent Energy Exported phase B | int32 | R | 2 | 0~+999999999
| 0x15AA | 0x15AB | 5546 | 5547 | Total Apparent Energy Exported phase C | int32 | R | 2 | 0~+999999999

## Demand Peak and Happening Time
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Current Demand Peak and Happening Time | 0x1600 | 0x1601 | 5632 | 5633 | Total Imported Active Power Demand Peak | Float | R | 2 | Xx.xxxx kw
(Current Month) | 0x1602 | 0x1604 | 5634 | 5636 | Total Imported Active Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
(0x03 Read) | 0x1605 | 0x1606 | 5637 | 5638 | Imported Active Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1607 | 0x1609 | 5639 | 5641 | Imported Active Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x160A | 0x160B | 5642 | 5643 | Imported Active Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kw
| 0x160C | 0x160E | 5644 | 5646 | Imported Active Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x160F | 0x1610 | 5647 | 5648 | Imported Active Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1611 | 0x1613 | 5649 | 5651 | Imported Active Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1614 | 0x1615 | 5652 | 5653 | Imported Active Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1616 | 0x1618 | 5654 | 5656 | Imported Active Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1619 | 0x161A | 5657 | 5658 | Total Exported Active Power Demand Peak | Float | R | 2 | Xx.xxxx kw
| 0x161B | 0x161D | 5659 | 5661 | Total Exported Active Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x161E | 0x161F | 5662 | 5663 | Exported Active Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1620 | 0x1622 | 5664 | 5666 | Exported Active Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1623 | 0x1624 | 5667 | 5668 | Exported Active Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1625 | 0x1627 | 5669 | 5671 | Exported Active Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1628 | 0x1629 | 5672 | 5673 | Exported Active Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kw
| 0x162A | 0x162C | 5674 | 5676 | Exported Active Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x162D | 0x162E | 5677 | 5678 | Exported Active Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kw
| 0x162F | 0x1631 | 5679 | 5681 | Exported Active Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1632 | 0x1633 | 5682 | 5683 | Total Imported Reactive Power Demand Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1634 | 0x1636 | 5684 | 5686 | Total Imported Reactive Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1637 | 0x1638 | 5687 | 5688 | Imported Reactive Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1639 | 0x163B | 5689 | 5691 | Imported Reactive Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x163C | 0x163D | 5692 | 5693 | Imported Reactive Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x163E | 0x1640 | 5694 | 5696 | Imported Reactive Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1641 | 0x1642 | 5697 | 5698 | Imported Reactive Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1643 | 0x1645 | 5699 | 5701 | Imported Reactive Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1646 | 0x1647 | 5702 | 5703 | Imported Reactive Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1648 | 0x164A | 5704 | 5706 | Imported Reactive Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x164B | 0x164C | 5707 | 5708 | Total Exported Reactive Power Demand Peak | Float | R | 2 | Xx.xxxx kvar
| 0x164D | 0x164F | 5709 | 5711 | Total Exported Reactive Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1650 | 0x1651 | 5712 | 5713 | Exported Reactive Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1652 | 0x1654 | 5714 | 5716 | Exported Reactive Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1655 | 0x1656 | 5717 | 5718 | Exported Reactive Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1657 | 0x1659 | 5719 | 5721 | Exported Reactive Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x165A | 0x165B | 5722 | 5723 | Exported Reactive Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x165C | 0x165E | 5724 | 5726 | Exported Reactive Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x165F | 0x1660 | 5727 | 5728 | Exported Reactive Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1661 | 0x1663 | 5729 | 5731 | Exported Reactive Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1664 | 0x1665 | 5732 | 5733 | Total Apparent Power Demand Peak | Float | R | 2 | Xx.xxxx kVA
| 0x1666 | 0x1668 | 5734 | 5736 | Total Apparent Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1669 | 0x166A | 5737 | 5738 | Phase A Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x166B | 0x166D | 5739 | 5741 | Phase A Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x166E | 0x166F | 5742 | 5743 | Phase B Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x1670 | 0x1672 | 5744 | 5746 | Phase B Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1673 | 0x1674 | 5747 | 5748 | Phase C Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x1675 | 0x1677 | 5749 | 5751 | Phase C Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
Current Demand Peak and Happening Time | 0x1800 | 0x1801 | 6144 | 6145 | Total Imported Active Power Demand Peak | Float | R | 2 | Xx.xxxx kw
(Previous Month) | 0x1802 | 0x1804 | 6146 | 6148 | Total Imported Active Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
(0x03 Read) | 0x1805 | 0x1806 | 6149 | 6150 | Imported Active Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1807 | 0x1809 | 6151 | 6153 | Imported Active Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x180A | 0x180B | 6154 | 6155 | Imported Active Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kw
| 0x180C | 0x180E | 6156 | 6158 | Imported Active Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x180F | 0x1810 | 6159 | 6160 | Imported Active Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1811 | 0x1813 | 6161 | 6163 | Imported Active Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1814 | 0x1815 | 6164 | 6165 | Imported Active Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1816 | 0x1818 | 6166 | 6168 | Imported Active Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1819 | 0x181A | 6169 | 6170 | Total Exported Active Power Demand Peak | Float | R | 2 | Xx.xxxx kw
| 0x181B | 0x181D | 6171 | 6173 | Total Exported Active Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x181E | 0x181F | 6174 | 6175 | Exported Active Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1820 | 0x1822 | 6176 | 6178 | Exported Active Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1823 | 0x1824 | 6179 | 6180 | Exported Active Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kw
| 0x1825 | 0x1827 | 6181 | 6183 | Exported Active Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1828 | 0x1829 | 6184 | 6185 | Exported Active Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kw
| 0x182A | 0x182C | 6186 | 6188 | Exported Active Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x182D | 0x182E | 6189 | 6190 | Exported Active Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kw
| 0x182F | 0x1831 | 6191 | 6193 | Exported Active Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1832 | 0x1833 | 6194 | 6195 | Total Imported Reactive Power Demand Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1834 | 0x1836 | 6196 | 6198 | Total Imported Reactive Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1837 | 0x1838 | 6199 | 6200 | Imported Reactive Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1839 | 0x183B | 6201 | 6203 | Imported Reactive Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x183C | 0x183D | 6204 | 6205 | Imported Reactive Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x183E | 0x1840 | 6206 | 6208 | Imported Reactive Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1841 | 0x1842 | 6209 | 6210 | Imported Reactive Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1843 | 0x1845 | 6211 | 6213 | Imported Reactive Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1846 | 0x1847 | 6214 | 6215 | Imported Reactive Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1848 | 0x184A | 6216 | 6218 | Imported Reactive Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x184B | 0x184C | 6219 | 6220 | Total Exported Reactive Power Demand Peak | Float | R | 2 | Xx.xxxx kvar
| 0x184D | 0x184F | 6221 | 6223 | Total Exported Reactive Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1850 | 0x1851 | 6224 | 6225 | Exported Reactive Power Demand 1 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1852 | 0x1854 | 6226 | 6228 | Exported Reactive Power Demand 1 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1855 | 0x1856 | 6229 | 6230 | Exported Reactive Power Demand 2 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1857 | 0x1859 | 6231 | 6233 | Exported Reactive Power Demand 2 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x185A | 0x185B | 6234 | 6235 | Exported Reactive Power Demand 3 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x185C | 0x185E | 6236 | 6238 | Exported Reactive Power Demand 3 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x185F | 0x1860 | 6239 | 6240 | Exported Reactive Power Demand 4 Peak | Float | R | 2 | Xx.xxxx kvar
| 0x1861 | 0x1863 | 6241 | 6243 | Exported Reactive Power Demand 4 Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1864 | 0x1865 | 6244 | 6245 | Total Apparent Power Demand Peak | Float | R | 2 | Xx.xxxx kVA
| 0x1866 | 0x1868 | 6246 | 6248 | Total Apparent Power Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1869 | 0x186A | 6249 | 6250 | Phase A Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x186B | 0x186D | 6251 | 6253 | Phase A Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x186E | 0x186F | 6254 | 6255 | Phase B Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x1870 | 0x1872 | 6256 | 6258 | Phase B Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)
| 0x1873 | 0x1874 | 6259 | 6260 | Phase C Current Demand Peak | Float | R | 2 | Xx.xxxx A
| 0x1875 | 0x1877 | 6261 | 6263 | Phase C Current Demand Peak Happening Time | Dword | R | 3 | YY/MM/DD/hh/mm/ss (Second always is 0)

## Dual Source Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Dual Source Energy Data | 0x3200 | 0x3201 | 12800 | 12801 | Grid-Ep | Dword | R/W | 2 | 0~999999999
(0x03 Read, 0x10 Write) | 0x3202 | 0x3203 | 12802 | 12803 | Alternate-Ep | Dword | R/W | 2 | 0~999999999
| 0x3204 | 0x3205 | 12804 | 12805 | Grid-Eq | Dword | R/W | 2 | 0~999999999
| 0x3206 | 0x3207 | 12806 | 12807 | Alternate-Eq | Dword | R/W | 2 | 0~999999999
| 0x3208 | 0x3209 | 12808 | 12809 | Grid-Es | Dword | R/W | 2 | 0~999999999
| 0x320A | 0x320B | 12810 | 12811 | Alternate-Es | Dword | R/W | 2 | 0~999999999
Dual Source Energy Parameter | 0x3000 | 0x3000 | 12288 | 12288 | Enable | word | R/W | 1 | 0: Disable 1: Enable | 0
(0x03 Read, 0x10 Write) | 0x3001 | 0x3001 | 12289 | 12289 | Energy source | word | R/W | 1 | 0: From Grid 1: From alternative source | 0
Dual Source Energy Command | 0x3100 | 0x3100 | 12544 | 12544 | Clear dual-source energy | Word | W | 1 | 0x0A: Valid | 0
(0x10 Write) | 0x3101 | 0x3101 | 12545 | 12545 | Clear Dual-source change log | Word | W | 1 | 0x0A: Valid | 0
Dual Source Change Log | 0x3300 | 0x3302 | 13056 | 13058 | timestamp | Word | R | 3 | YYMMDDhhmmss
(0x03 Read) | 0x3303 | 0x3303 | 13059 | 13059 | Direction | Word | R | 1 | 0: To Grid 1: To Alternative source
| 0x3304 | 0x3305 | 13060 | 13061 | Ep to grid when source is changed | Word | R | 2
| 0x3306 | 0x3307 | 13062 | 13063 | Ep to Alternative source when source is changed | Word | R | 2
| 0x3308 | 0x3309 | 13064 | 13065 | Eq to grid when source is changed | Word | R | 2
| 0x330A | 0x330B | 13066 | 13067 | Eq to Alternative source when source is changed | Word | R | 2
| 0x330C | 0x330D | 13068 | 13069 | Es to grid when source is changed | Word | R | 2
| 0x330E | 0x330F | 13070 | 13071 | Es to Alternative source when source is changed | Word | R | 2
| 0x3310 | 0x331F | 13072 | 13087 | Last 2nd change log (same as above) | Word | R | 16
| 0x3320 | 0x332F | 13088 | 13103 | Last 3rd change log (same as above) | Word | R | 16

## Max Min
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Max | 0x4000 | 0x4001 | 16384 | 16385 | I total | float | R | 2
(0x03 Read) | 0x4002 | 0x4004 | 16386 | 16388 | Time | uint16 | R | 3 | YYMMDDHHMMSS
| 0x4005 | 0x4006 | 16389 | 16390 | I1 | float | R | 2
| 0x4007 | 0x4009 | 16391 | 16393 | Time | uint16 | R | 3
| 0x400A | 0x400B | 16394 | 16395 | I2 | float | R | 2
| 0x400C | 0x400E | 16396 | 16398 | Time | uint16 | R | 3
| 0x400F | 0x4010 | 16399 | 16400 | I3 | float | R | 2
| 0x4011 | 0x4013 | 16401 | 16403 | Time | uint16 | R | 3
| 0x4014 | 0x4015 | 16404 | 16405 | V avg | float | R | 2
| 0x4016 | 0x4018 | 16406 | 16408 | Time | uint16 | R | 3
| 0x4019 | 0x401A | 16409 | 16410 | V1 | float | R | 2
| 0x401B | 0x401D | 16411 | 16413 | Time | uint16 | R | 3
| 0x401E | 0x401F | 16414 | 16415 | V2 | float | R | 2
| 0x4020 | 0x4022 | 16416 | 16418 | Time | uint16 | R | 3
| 0x4023 | 0x4024 | 16419 | 16420 | V3 | float | R | 2
| 0x4025 | 0x4027 | 16421 | 16423 | Time | uint16 | R | 3
| 0x4028 | 0x4029 | 16424 | 16425 | VL avg | float | R | 2
| 0x402A | 0x402C | 16426 | 16428 | Time | uint16 | R | 3
| 0x402D | 0x402E | 16429 | 16430 | V12 | float | R | 2
| 0x402F | 0x4031 | 16431 | 16433 | Time | uint16 | R | 3
| 0x4032 | 0x4033 | 16434 | 16435 | V23 | float | R | 2
| 0x4034 | 0x4036 | 16436 | 16438 | Time | uint16 | R | 3
| 0x4037 | 0x4038 | 16439 | 16440 | V31 | float | R | 2
| 0x4039 | 0x403B | 16441 | 16443 | Time | uint16 | R | 3
| 0x403C | 0x403D | 16444 | 16445 | Freq | float | R | 2
| 0x403E | 0x4040 | 16446 | 16448 | Time | uint16 | R | 3
| 0x4041 | 0x4042 | 16449 | 16450 | P | float | R | 2
| 0x4043 | 0x4045 | 16451 | 16453 | Time | uint16 | R | 3
| 0x4046 | 0x4047 | 16454 | 16455 | P1 | float | R | 2
| 0x4048 | 0x404A | 16456 | 16458 | Time | uint16 | R | 3
| 0x404B | 0x404C | 16459 | 16460 | P2 | float | R | 2
| 0x404D | 0x404F | 16461 | 16463 | Time | uint16 | R | 3
| 0x4050 | 0x4051 | 16464 | 16465 | P3 | float | R | 2
| 0x4052 | 0x4054 | 16466 | 16468 | Time | uint16 | R | 3
| 0x4055 | 0x4056 | 16469 | 16470 | S | float | R | 2
| 0x4057 | 0x4059 | 16471 | 16473 | Time | uint16 | R | 3
| 0x405A | 0x405B | 16474 | 16475 | S1 | float | R | 2
| 0x405C | 0x405E | 16476 | 16478 | Time | uint16 | R | 3
| 0x405F | 0x4060 | 16479 | 16480 | S2 | float | R | 2
| 0x4061 | 0x4063 | 16481 | 16483 | Time | uint16 | R | 3
| 0x4064 | 0x4065 | 16484 | 16485 | S3 | float | R | 2
| 0x4066 | 0x4068 | 16486 | 16488 | Time | uint16 | R | 3
| 0x4069 | 0x406A | 16489 | 16490 | Q | float | R | 2
| 0x406B | 0x406D | 16491 | 16493 | Time | uint16 | R | 3
| 0x406E | 0x406F | 16494 | 16495 | Q1 | float | R | 2
| 0x4070 | 0x4072 | 16496 | 16498 | Time | uint16 | R | 3
| 0x4073 | 0x4074 | 16499 | 16500 | Q2 | float | R | 2
| 0x4075 | 0x4077 | 16501 | 16503 | Time | uint16 | R | 3
| 0x4078 | 0x4079 | 16504 | 16505 | Q3 | float | R | 2
| 0x407A | 0x407C | 16506 | 16508 | Time | uint16 | R | 3
Min | 0x4100 | 0x4101 | 16640 | 16641 | I total | float | R | 2
(0x03 Read) | 0x4102 | 0x4104 | 16642 | 16644 | Time | uint16 | R | 3
| 0x4105 | 0x4106 | 16645 | 16646 | I1 | float | R | 2
| 0x4107 | 0x4109 | 16647 | 16649 | Time | uint16 | R | 3
| 0x410A | 0x410B | 16650 | 16651 | I2 | float | R | 2
| 0x410C | 0x410E | 16652 | 16654 | Time | uint16 | R | 3
| 0x410F | 0x4110 | 16655 | 16656 | I3 | float | R | 2
| 0x4111 | 0x4113 | 16657 | 16659 | Time | uint16 | R | 3
| 0x4114 | 0x4115 | 16660 | 16661 | V avg | float | R | 2
| 0x4116 | 0x4118 | 16662 | 16664 | Time | uint16 | R | 3
| 0x4119 | 0x411A | 16665 | 16666 | V1 | float | R | 2
| 0x411B | 0x411D | 16667 | 16669 | Time | uint16 | R | 3
| 0x411E | 0x411F | 16670 | 16671 | V2 | float | R | 2
| 0x4120 | 0x4122 | 16672 | 16674 | Time | uint16 | R | 3
| 0x4123 | 0x4124 | 16675 | 16676 | V3 | float | R | 2
| 0x4125 | 0x4127 | 16677 | 16679 | Time | uint16 | R | 3
| 0x4128 | 0x4129 | 16680 | 16681 | VL avg | float | R | 2
| 0x412A | 0x412C | 16682 | 16684 | Time | uint16 | R | 3
| 0x412D | 0x412E | 16685 | 16686 | V12 | float | R | 2
| 0x412F | 0x4131 | 16687 | 16689 | Time | uint16 | R | 3
| 0x4132 | 0x4133 | 16690 | 16691 | V23 | float | R | 2
| 0x4134 | 0x4136 | 16692 | 16694 | Time | uint16 | R | 3
| 0x4137 | 0x4138 | 16695 | 16696 | V31 | float | R | 2
| 0x4139 | 0x413B | 16697 | 16699 | Time | uint16 | R | 3
| 0x413C | 0x413D | 16700 | 16701 | Freq | float | R | 2
| 0x413E | 0x4140 | 16702 | 16704 | Time | uint16 | R | 3
| 0x4141 | 0x4142 | 16705 | 16706 | P | float | R | 2
| 0x4143 | 0x4145 | 16707 | 16709 | Time | uint16 | R | 3
| 0x4146 | 0x4147 | 16710 | 16711 | P1 | float | R | 2
| 0x4148 | 0x414A | 16712 | 16714 | Time | uint16 | R | 3
| 0x414B | 0x414C | 16715 | 16716 | P2 | float | R | 2
| 0x414D | 0x414F | 16717 | 16719 | Time | uint16 | R | 3
| 0x4150 | 0x4151 | 16720 | 16721 | P3 | float | R | 2
| 0x4152 | 0x4154 | 16722 | 16724 | Time | uint16 | R | 3
| 0x4155 | 0x4156 | 16725 | 16726 | S | float | R | 2
| 0x4157 | 0x4159 | 16727 | 16729 | Time | uint16 | R | 3
| 0x415A | 0x415B | 16730 | 16731 | S1 | float | R | 2
| 0x415C | 0x415E | 16732 | 16734 | Time | uint16 | R | 3
| 0x415F | 0x4160 | 16735 | 16736 | S2 | float | R | 2
| 0x4161 | 0x4163 | 16737 | 16739 | Time | uint16 | R | 3
| 0x4164 | 0x4165 | 16740 | 16741 | S3 | float | R | 2
| 0x4166 | 0x4168 | 16742 | 16744 | Time | uint16 | R | 3
| 0x4169 | 0x416A | 16745 | 16746 | Q | float | R | 2
| 0x416B | 0x416D | 16747 | 16749 | Time | uint16 | R | 3
| 0x416E | 0x416F | 16750 | 16751 | Q1 | float | R | 2
| 0x4170 | 0x4172 | 16752 | 16754 | Time | uint16 | R | 3
| 0x4173 | 0x4174 | 16755 | 16756 | Q2 | float | R | 2
| 0x4175 | 0x4177 | 16757 | 16759 | Time | uint16 | R | 3
| 0x4178 | 0x4179 | 16760 | 16761 | Q3 | float | R | 2
| 0x417A | 0x417C | 16762 | 16764 | Time | uint16 | R | 3

## Reset Event & Unseal Record
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Demand Reset Event | 0x1B00 | 0x1B01 | 6912 | 6913 | Total Times of Demand Reset | word | R | 2 | 0~0xFFFFFFFF
(0x03 Read) | 0x1B02 | 0x1B04 | 6914 | 6916 | Last Demand Reset Happening Time | word | R | 3 | YYMMDDhhmmss
| 0x1B05 | 0x1B07 | 6917 | 6919 | 2nd last, same as Last demand reset | word | R | 3
| 0x1B08 | 0x1B0A | 6920 | 6922 | 3rd last, same as Last demand reset | word | R | 3
Meter Unseal Record | 0x1C00 | 0x1C01 | 7168 | 7169 | Total times of Meter Unseal | word | R | 2 | 0~0xFFFFFFFF
(0x03 Read) | 0x1C02 | 0x1C04 | 7170 | 7172 | Last Meter Unseal Happening Time | word | R | 3 | YY/MM/DD/hh/mm/ss
| 0x1C05 | 0x1C07 | 7173 | 7175 | Last Meter Reseal Happening Time | word | R | 3
| 0x1C08 | 0x1C0D | 7176 | 7181 | 2nd last, same as Last Unseal Record | word | R | 6
| 0x1C0E | 0x1C13 | 7182 | 7187 | 3rd last, same as Last Unseal Record | word | R | 6
Event Reset | 0x1D00 | 0x1D01 | 7424 | 7425 | Total times of Event Reset (Total Reset and Each Parameter Reset) | word | R | 2 | 0~0xFFFFFFFF
(0x03 Read) | 0x1D02 | 0x1D04 | 7426 | 7428 | Last Event Reset Happening Time | word | R | 3 | YY/MM/DD/hh/mm/ss
| 0x1D05 | 0x1D05 | 7429 | 7429 | Last Event Reset Marking Code | word | R | 1 | 1: Reset Event Record; 2: Reset Demand Record; 3: Reset Meter Opening Record; 4: Reset Alarm; 5: Reset Meter Operation Time; 6: Reset Time of Meter Operation with Load;
| 0x1D06 | 0x1D09 | 7430 | 7433 | 2nd last, same as last event reset | word | R | 4
| 0x1D0A | 0x1D0D | 7434 | 7437 | 3rd last, same as last event reset | word | R | 4
Meter Reset | 0x1E00 | 0x1E01 | 7680 | 7681 | Total times of Meter Reset | word | R | 2 | 0~0xFFFFFFFF
(0x03 Read) | 0x1E02 | 0x1E04 | 7682 | 7684 | Last Meter Reset happening Time | word | R | 3 | YY/MM/DD/hh/mm/ss
| 0x1E05 | 0x1E07 | 7685 | 7687 | 2nd Last Meter Reset happening Time | word | R | 3 | YY/MM/DD/hh/mm/ss
| 0x1E08 | 0x1E0A | 7688 | 7690 | 3rd Last Meter Reset happening Time | word | R | 3 | YY/MM/DD/hh/mm/ss

## Read Only Area
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Read Only Area | 0x100 | 0x100 | 256 | 256 | The Result of Wiring Check | word | R | 1 | Refer to “The Result of Wiring Check”
(0x03 Read) | 0x101 | 0x101 | 257 | 257 | Seals status | word | R | 1 | 0x0A: Seal sealed Others: Seal opened
| 0x102 | 0x10F | 258 | 271 | Reserved | word | R | 14

## SunSpec
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
SunSpec System Information | 0x1000 | 0x1001 | 4096 | 4097 | SunSpec_ID | Uint16 | R | 2 | 0x53756e53 | 1
(0x03 Read, 0x10 Write) | 0x1002 | 0x1002 | 4098 | 4098 | ID | Uint16 | R | 1 | 1 | 1
| 0x1003 | 0x1003 | 4099 | 4099 | Lenth | Uint16 | R | 1 | 65 | 65
| 0x1004 | 0x1013 | 4100 | 4115 | Manufacturer | string | R | 16 | Well known value registered with SunSpec for compliance | Accuenergy/ Eaton /Carlo Gavazzi
| 0x1014 | 0x1023 | 4116 | 4131 | Model | string | R | 16 | Manufacturer specific value (32 chars) | AcuRev1300 /PXM350 /EM50
| 0x1024 | 0x102B | 4132 | 4139 | Options | string | R | 8 | Manufacturer specific value (16 chars) | AcuRev130X /HF3X /EM50
| 0x102C | 0x1033 | 4140 | 4147 | Version | string | R | 8 | Manufacturer specific value (16 chars) | H: 1.10 S: 1.01
| 0x1034 | 0x1043 | 4148 | 4163 | Serial Number | string | R | 16 | Manufacturer specific value (32 chars)
| 0x1044 | 0x1044 | 4164 | 4164 | Device Address | uint16 | R/W | 1 | Modbus device address
SunSpec Measured Data | 0x1045 | 0x1045 | 4165 | 4165 | ID | Uint16 | R | 1 | Meter (Single Phase)single phase (AN or AB) meter –201 split single phase (ABN) meter –202 wye-connect three phase (abcn) meter—203 delta-connect three phase (abc) meter –204
(0x03 Read, 0x10 Write) | 0x1046 | 0x1046 | 4166 | 4166 | Lenth | Uint16 | R | 1 | 105
| 0x1047 | 0x1047 | 4167 | 4167 | Amps (total): Sunspec; Total Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0x1048 | 0x1048 | 4168 | 4168 | Amps Phase A: Sunspec; Phase A Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0x1049 | 0x1049 | 4169 | 4169 | Amps Phase B: Sunspec; Phase B Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0x104A | 0x104A | 4170 | 4170 | Amps Phase C: Sunspec; Phase C Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0x104B | 0x104B | 4171 | 4171 | Current scale factor: Sunspec; CT Ratio: Acurev 1300 | sunssf | R | 1 | -3~+5 (used as exponent of a power of 10)
| 0x104C | 0x104C | 4172 | 4172 | Voltage LN (average): Sunspec; Phase Average Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x104D | 0x104D | 4173 | 4173 | Phase Voltage AN: Sunspec; Phase A Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x104E | 0x104E | 4174 | 4174 | Phase Voltage BN: Sunspec; Phase B Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x104F | 0x104F | 4175 | 4175 | Phase Voltage CN: Sunspec; Phase C Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x1050 | 0x1050 | 4176 | 4176 | Voltage LL (average): Sunspec; Line Average Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x1051 | 0x1051 | 4177 | 4177 | Phase Voltage AB: Sunspec; Line AB Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x1052 | 0x1052 | 4178 | 4178 | Phase Voltage BC: Sunspec; Line BC Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x1053 | 0x1053 | 4179 | 4179 | Phase Voltage CA: Sunspec; Line CA Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0x1054 | 0x1054 | 4180 | 4180 | Voltage scale factor: Sunspec | sunssf | R | 1 | -2~2(used as exponent of a power of 10)
| 0x1055 | 0x1055 | 4181 | 4181 | Frequency | int16 | R | 1 | 45Hz—65Hz
| 0x1056 | 0x1056 | 4182 | 4182 | Frequency scale factor | sunssf | R | 1 | -2(used as exponent of a power of 10)
| 0x1057 | 0x1057 | 4183 | 4183 | Total Real Power: Sunspec; Total Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0x1058 | 0x1058 | 4184 | 4184 | Watts phase A: Sunspec; Phase A Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0x1059 | 0x1059 | 4185 | 4185 | Watts phase B: Sunspec; Phase B Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0x105A | 0x105A | 4186 | 4186 | Watts phase C: Sunspec; Phase C Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0x105B | 0x105B | 4187 | 4187 | Real Power scale factor: Sunspec | sunssf | R | 1 | -1~ 4(used as exponent of a power of 10)
| 0x105C | 0x105C | 4188 | 4188 | AC Apparent Power VA: Sunspec; Total Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0x105D | 0x105D | 4189 | 4189 | VA phase A: Sunspec; Phase A Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0x105E | 0x105E | 4190 | 4190 | VA phase B: Sunspec; Phase B Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0x105F | 0x105F | 4191 | 4191 | VA phaseCA: Sunspec; Phase C Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0x1060 | 0x1060 | 4192 | 4192 | Apparent Power scale factor: Sunspec; | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10)
| 0x1061 | 0x1061 | 4193 | 4193 | Reactive Power VAR: Sunspec; Total Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0x1062 | 0x1062 | 4194 | 4194 | VAR phase A: Sunspec; Phase A Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0x1063 | 0x1063 | 4195 | 4195 | VAR phase B: Sunspec; Phase B Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0x1064 | 0x1064 | 4196 | 4196 | VAR phase C: Sunspec; Phase C Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0x1065 | 0x1065 | 4197 | 4197 | Reactive Power scale factor: Sunspec | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10)
| 0x1066 | 0x1066 | 4198 | 4198 | Power Factor | int16 | R | 1 | -1000 ~ 1000
| 0x1067 | 0x1067 | 4199 | 4199 | PF phase A | int16 | R | 1 | -1000 ~ 1000
| 0x1068 | 0x1068 | 4200 | 4200 | PF phase B | int16 | R | 1 | -1000 ~ 1000
| 0x1069 | 0x1069 | 4201 | 4201 | PF phase C | int16 | R | 1 | -1000 ~ 1000
| 0x106A | 0x106A | 4202 | 4202 | Power Factor scale factor: Sunspec | sunssf | R | 1 | -3(used as exponent of a power of 10)
| 0x106B | 0x106C | 4203 | 4204 | Total Real Energy Exported: Sunspec Total Active Energy Exported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x106D | 0x106E | 4205 | 4206 | Total Watt-hours Exported in phase A: Sunspec; Total Active Energy Exported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x106F | 0x1070 | 4207 | 4208 | Total Watt-hours Exported in phase B: Sunspec; Total Active Energy Exported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x1071 | 0x1072 | 4209 | 4210 | Total Watt-hours Exported in phase C: Sunspec; Total Active Energy Exported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x1073 | 0x1074 | 4211 | 4212 | Total Real Energy Imported: Sunspec; Total Active Energy Imported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x1075 | 0x1076 | 4213 | 4214 | Total Watt-hours Imported phase A: Sunspec; Total Active Energy Imported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x1077 | 0x1078 | 4215 | 4216 | Total Watt-hours Imported phase B: Sunspec; Total Active Energy Imported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x1079 | 0x107A | 4217 | 4218 | Total Watt-hours Imported phase C: Sunspec; Total Active Energy Imported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kWh
| 0x107B | 0x107B | 4219 | 4219 | TotWh_SF: Sunspec | sunssf | R | 1 | -3 ~ 0(used as exponent of a power of 10)
| 0x107C | 0x107D | 4220 | 4221 | Total VA-hours Exported: Sunspec; Total Apparent Power Exported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x107E | 0x107F | 4222 | 4223 | Total VA-hours Exported phase A: Sunspec; Total Apparent Power Exported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x1080 | 0x1081 | 4224 | 4225 | Total VA-hours Exported phase B: Sunspec; Total Apparent Power Exported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x1082 | 0x1083 | 4226 | 4227 | Total VA-hours Exported phase C: Sunspec; Total Apparent Power Exported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x1084 | 0x1085 | 4228 | 4229 | Total VA-hours Imported: Sunspec; Total Apparent Power Imported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x1086 | 0x1087 | 4230 | 4231 | Total VA-hours Imported phase A: Sunspec; Total Apparent Power Imported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x1088 | 0x1089 | 4232 | 4233 | Total VA-hours Imported phase B: Sunspec; Total Apparent Power Imported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x108A | 0x108B | 4234 | 4235 | Total VA-hours Imported phase C: Sunspec; Total Apparent Power Imported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kVah
| 0x108C | 0x108C | 4236 | 4236 | TotVAh_SF: Sunspec | sunssf | R | 1 | -3 ~ 0(used as exponent of a power of 10)
| 0x108D | 0x108E | 4237 | 4238 | Total VAR-hours Imported Q1: Sunspec; Total Reactive Imported Q1: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x108F | 0x1090 | 4239 | 4240 | Total VAR-hours Imported Q1 Phase A: Sunspec; Total Reactive Imported Q1 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x1091 | 0x1092 | 4241 | 4242 | Total VAR-hours Imported Q1 Phase B: Sunspec; Total Reactive Imported Q1 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x1093 | 0x1094 | 4243 | 4244 | Total VAR-hours Imported Q1 Phase C: Sunspec; Total Reactive Imported Q1 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x1095 | 0x1096 | 4245 | 4246 | Total VAR-hours Imported Q2: Sunspec; Total Reactive Imported Q2: Acurev 1300 | acc32 | R/W | 2 | 0-999999999k varh
| 0x1097 | 0x1098 | 4247 | 4248 | Total VAR-hours Imported Q2 Phase A: Sunspec; Total Reactive Imported Q2 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x1099 | 0x109A | 4249 | 4250 | Total VAR-hours Imported Q2 Phase B: Sunspec; Total Reactive Imported Q2 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x109B | 0x109C | 4251 | 4252 | Total VAR-hours Imported Q2 Phase C: Sunspec; Total Reactive Imported Q2 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x109D | 0x109E | 4253 | 4254 | Total VAR-hours Imported Q3: Sunspec; Total Reactive Imported Q3: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x109F | 0x10A0 | 4255 | 4256 | Total VAR-hours Imported Q3 Phase A: Sunspec; Total Reactive Imported Q3 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10A1 | 0x10A2 | 4257 | 4258 | Total VAR-hours Imported Q3 Phase B: Sunspec; Total Reactive Imported Q3 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10A3 | 0x10A4 | 4259 | 4260 | Total VAR-hours Imported Q3 Phase C: Sunspec; Total Reactive Imported Q3 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10A5 | 0x10A6 | 4261 | 4262 | Total VAR-hours Imported Q4: Sunspec; Total Reactive Imported Q4: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10A7 | 0x10A8 | 4263 | 4264 | Total VAR-hours Imported Q4 Phase A: Sunspec; Total Reactive Imported Q4 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10A9 | 0x10AA | 4265 | 4266 | Total VAR-hours Imported Q4 Phase B: Sunspec; Total Reactive Imported Q4 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10AB | 0x10AC | 4267 | 4268 | Total VAR-hours Imported Q4 Phase C: Sunspec; Total Reactive Imported Q4 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 kvarh
| 0x10AD | 0x10AD | 4269 | 4269 | TotVArh_SF: Sunspec; | sunssf | R | 1 | All the energy use the same SF
| 0x10AE | 0x10AF | 4270 | 4271 | Meter Event Flags | bitfield32 | R | 2 | 0
| 0x10B0 | 0x10B0 | 4272 | 4272 | SunSpec_end_ID: Sunspec | Uint16 |  | 1 | 0xFFFF
| 0x10B1 | 0x10B1 | 4273 | 4273 | SunSpec_end_lenth: Sunspec | Uint16 |  | 1 | 0x0000

## New SunSpec
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
SunSpec System Information | 0xC350 | 0xC351 | 50000 | 50001 | SunSpec_ID | Uint16 | R | 2 | 0x53756e53 | 1
(0x03 Read, 0x10 Write) | 0xC352 | 0xC352 | 50002 | 50002 | ID | Uint16 | R | 1 | 1 | 1
| 0xC353 | 0xC353 | 50003 | 50003 | Lenth | Uint16 | R | 1 | 65 | 65
| 0xC354 | 0xC363 | 50004 | 50019 | Manufacturer | string | R | 16 | Well known value registered with SunSpec for compliance | Accuenergy/ Eaton /Carlo Gavazzi
| 0xC364 | 0xC373 | 50020 | 50035 | Model | string | R | 16 | Manufacturer specific value (32 chars) | AcuRev1300 /PXM350 /EM50
| 0xC374 | 0xC37B | 50036 | 50043 | Options | string | R | 8 | Manufacturer specific value (16 chars) | AcuRev130X /HF3X /EM50
| 0xC37C | 0xC383 | 50044 | 50051 | Version | string | R | 8 | Manufacturer specific value (16 chars) | H: 1.10 S:1.01
| 0xC384 | 0xC393 | 50052 | 50067 | Serial Number | string | R | 16 | Manufacturer specific value (32 chars)
| 0xC394 | 0xC394 | 50068 | 50068 | Device Address | uint16 | R/W | 1 | Modbus device address
SunSpec Measured Data | 0xC395 | 0xC395 | 50069 | 50069 | ID | Uint16 | R | 1 | Meter (Single Phase)single phase (AN or AB) meter –201 split single phase (ABN) meter –202 wye-connect three phase (abcn) meter—203 delta-connect three phase (abc) meter –204
(0x03 Read, 0x10 Write) | 0xC396 | 0xC396 | 50070 | 50070 | Lenth | Uint16 | R | 1 | 105
| 0xC397 | 0xC397 | 50071 | 50071 | Amps (total): Sunspec; Total Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0xC398 | 0xC398 | 50072 | 50072 | Amps Phase A: Sunspec; Phase A Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0xC399 | 0xC399 | 50073 | 50073 | Amps Phase B: Sunspec; Phase B Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0xC39A | 0xC39A | 50074 | 50074 | Amps Phase C: Sunspec; Phase C Current: Acurev 1300 | int16 | R | 1 | 0~9999 A
| 0xC39B | 0xC39B | 50075 | 50075 | Current scale factor: Sunspec; CT Ratio: Acurev 1300 | sunssf | R | 1 | -3~+5 (used as exponent of a power of 10)
| 0xC39C | 0xC39C | 50076 | 50076 | Voltage LN (average): Sunspec; Phase Average Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC39D | 0xC39D | 50077 | 50077 | Phase Voltage AN: Sunspec; Phase A Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC39E | 0xC39E | 50078 | 50078 | Phase Voltage BN: Sunspec; Phase B Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC39F | 0xC39F | 50079 | 50079 | Phase Voltage CN: Sunspec; Phase C Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC3A0 | 0xC3A0 | 50080 | 50080 | Voltage LL (average): Sunspec; Line Average Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC3A1 | 0xC3A1 | 50081 | 50081 | Phase Voltage AB: Sunspec; Line AB Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC3A2 | 0xC3A2 | 50082 | 50082 | Phase Voltage BC: Sunspec; Line BC Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC3A3 | 0xC3A3 | 50083 | 50083 | Phase Voltage CA: Sunspec; Line CA Voltage: Acurev 1300 | int16 | R | 1 | 0~9999 V
| 0xC3A4 | 0xC3A4 | 50084 | 50084 | Voltage scale factor: Sunspec | sunssf | R | 1 | -2~2(used as exponent of a power of 10)
| 0xC3A5 | 0xC3A5 | 50085 | 50085 | Frequency | int16 | R | 1 | 45Hz—65Hz
| 0xC3A6 | 0xC3A6 | 50086 | 50086 | Frequency scale factor | sunssf | R | 1 | -2(used as exponent of a power of 10)
| 0xC3A7 | 0xC3A7 | 50087 | 50087 | Total Real Power: Sunspec; Total Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0xC3A8 | 0xC3A8 | 50088 | 50088 | Watts phase A: Sunspec; Phase A Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0xC3A9 | 0xC3A9 | 50089 | 50089 | Watts phase B: Sunspec; Phase B Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0xC3AA | 0xC3AA | 50090 | 50090 | Watts phase C: Sunspec; Phase C Active Power: Acurev 1300 | int16 | R | 1 | 0~9999 W
| 0xC3AB | 0xC3AB | 50091 | 50091 | Real Power scale factor: Sunspec | sunssf | R | 1 | -1~ 4(used as exponent of a power of 10)
| 0xC3AC | 0xC3AC | 50092 | 50092 | AC Apparent Power VA: Sunspec; Total Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0xC3AD | 0xC3AD | 50093 | 50093 | VA phase A: Sunspec; Phase A Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0xC3AE | 0xC3AE | 50094 | 50094 | VA phase B: Sunspec; Phase B Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0xC3AF | 0xC3AF | 50095 | 50095 | VA phaseCA: Sunspec; Phase C Apparent Power: Acurev 1300 | int16 | R | 1 | 0~9999 VA
| 0xC3B0 | 0xC3B0 | 50096 | 50096 | Apparent Power scale factor: Sunspec; | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10)
| 0xC3B1 | 0xC3B1 | 50097 | 50097 | Reactive Power VAR: Sunspec; Total Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0xC3B2 | 0xC3B2 | 50098 | 50098 | VAR phase A: Sunspec; Phase A Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0xC3B3 | 0xC3B3 | 50099 | 50099 | VAR phase B: Sunspec; Phase B Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0xC3B4 | 0xC3B4 | 50100 | 50100 | VAR phase C: Sunspec; Phase C Reactive Power: Acurev 1300 | int16 | R | 1 | 0~9999 var
| 0xC3B5 | 0xC3B5 | 50101 | 50101 | Reactive Power scale factor: Sunspec | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10)
| 0xC3B6 | 0xC3B6 | 50102 | 50102 | Power Factor | int16 | R | 1 | -1000 ~ 1000
| 0xC3B7 | 0xC3B7 | 50103 | 50103 | PF phase A | int16 | R | 1 | -1000 ~ 1000
| 0xC3B8 | 0xC3B8 | 50104 | 50104 | PF phase B | int16 | R | 1 | -1000 ~ 1000
| 0xC3B9 | 0xC3B9 | 50105 | 50105 | PF phase C | int16 | R | 1 | -1000 ~ 1000
| 0xC3BA | 0xC3BA | 50106 | 50106 | Power Factor scale factor: Sunspec | sunssf | R | 1 | -3(used as exponent of a power of 10)
| 0xC3BB | 0xC3BC | 50107 | 50108 | Total Real Energy Exported: Sunspec Total Active Energy Exported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3BD | 0xC3BE | 50109 | 50110 | Total Watt-hours Exported in phase A: Sunspec; Total Active Energy Exported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3BF | 0xC3C0 | 50111 | 50112 | Total Watt-hours Exported in phase B: Sunspec; Total Active Energy Exported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3C1 | 0xC3C2 | 50113 | 50114 | Total Watt-hours Exported in phase C: Sunspec; Total Active Energy Exported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3C3 | 0xC3C4 | 50115 | 50116 | Total Real Energy Imported: Sunspec; Total Active Energy Imported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3C5 | 0xC3C6 | 50117 | 50118 | Total Watt-hours Imported phase A: Sunspec; Total Active Energy Imported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3C7 | 0xC3C8 | 50119 | 50120 | Total Watt-hours Imported phase B: Sunspec; Total Active Energy Imported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3C9 | 0xC3CA | 50121 | 50122 | Total Watt-hours Imported phase C: Sunspec; Total Active Energy Imported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Wh
| 0xC3CB | 0xC3CB | 50123 | 50123 | TotWh_SF: Sunspec | sunssf | R | 1 | 0 ~ 3(used as exponent of a power of 10)
| 0xC3CC | 0xC3CD | 50124 | 50125 | Total VA-hours Exported: Sunspec; Total Apparent Power Exported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3CE | 0xC3CF | 50126 | 50127 | Total VA-hours Exported phase A: Sunspec; Total Apparent Power Exported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3D0 | 0xC3D1 | 50128 | 50129 | Total VA-hours Exported phase B: Sunspec; Total Apparent Power Exported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3D2 | 0xC3D3 | 50130 | 50131 | Total VA-hours Exported phase C: Sunspec; Total Apparent Power Exported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3D4 | 0xC3D5 | 50132 | 50133 | Total VA-hours Imported: Sunspec; Total Apparent Power Imported: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3D6 | 0xC3D7 | 50134 | 50135 | Total VA-hours Imported phase A: Sunspec; Total Apparent Power Imported in Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3D8 | 0xC3D9 | 50136 | 50137 | Total VA-hours Imported phase B: Sunspec; Total Apparent Power Imported in Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3DA | 0xC3DB | 50138 | 50139 | Total VA-hours Imported phase C: Sunspec; Total Apparent Power Imported in Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 Vah
| 0xC3DC | 0xC3DC | 50140 | 50140 | TotVAh_SF: Sunspec | sunssf | R | 1 | 0 ~3(used as exponent of a power of 10)
| 0xC3DD | 0xC3DE | 50141 | 50142 | Total VAR-hours Imported Q1: Sunspec; Total Reactive Imported Q1: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3DF | 0xC3E0 | 50143 | 50144 | Total VAR-hours Imported Q1 Phase A: Sunspec; Total Reactive Imported Q1 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3E1 | 0xC3E2 | 50145 | 50146 | Total VAR-hours Imported Q1 Phase B: Sunspec; Total Reactive Imported Q1 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3E3 | 0xC3E4 | 50147 | 50148 | Total VAR-hours Imported Q1 Phase C: Sunspec; Total Reactive Imported Q1 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3E5 | 0xC3E6 | 50149 | 50150 | Total VAR-hours Imported Q2: Sunspec; Total Reactive Imported Q2: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3E7 | 0xC3E8 | 50151 | 50152 | Total VAR-hours Imported Q2 Phase A: Sunspec; Total Reactive Imported Q2 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3E9 | 0xC3EA | 50153 | 50154 | Total VAR-hours Imported Q2 Phase B: Sunspec; Total Reactive Imported Q2 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3EB | 0xC3EC | 50155 | 50156 | Total VAR-hours Imported Q2 Phase C: Sunspec; Total Reactive Imported Q2 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3ED | 0xC3EE | 50157 | 50158 | Total VAR-hours Imported Q3: Sunspec; Total Reactive Imported Q3: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3EF | 0xC3F0 | 50159 | 50160 | Total VAR-hours Imported Q3 Phase A: Sunspec; Total Reactive Imported Q3 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3F1 | 0xC3F2 | 50161 | 50162 | Total VAR-hours Imported Q3 Phase B: Sunspec; Total Reactive Imported Q3 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3F3 | 0xC3F4 | 50163 | 50164 | Total VAR-hours Imported Q3 Phase C: Sunspec; Total Reactive Imported Q3 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3F5 | 0xC3F6 | 50165 | 50166 | Total VAR-hours Imported Q4: Sunspec; Total Reactive Imported Q4: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3F7 | 0xC3F8 | 50167 | 50168 | Total VAR-hours Imported Q4 Phase A: Sunspec; Total Reactive Imported Q4 Phase A: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3F9 | 0xC3FA | 50169 | 50170 | Total VAR-hours Imported Q4 Phase B: Sunspec; Total Reactive Imported Q4 Phase B: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3FB | 0xC3FC | 50171 | 50172 | Total VAR-hours Imported Q4 Phase C: Sunspec; Total Reactive Imported Q4 Phase C: Acurev 1300 | acc32 | R/W | 2 | 0-999999999 varh
| 0xC3FD | 0xC3FD | 50173 | 50173 | TotVArh_SF: Sunspec; | sunssf | R | 1 | All the energy use the same SF
| 0xC3FE | 0xC3FF | 50174 | 50175 | Meter Event Flags | bitfield32 | R | 2 | 0
| 0xC400 | 0xC400 | 50176 | 50176 | SunSpec_end_ID: Sunspec | Uint16 |  | 1 | 0xFFFF
| 0xC401 | 0xC401 | 50177 | 50177 | SunSpec_end_lenth: Sunspec | Uint16 |  | 1 | 0x0000