## Revision History
AcuRev 1310 ¦ Revision History
Modbus Register Map
Revision | Date | Description
1.1 | 2026-10-27 | • Corrected eight Q3/Q4 reactive-energy parameter names from “Imported” to “Exported” (2076H–2085H). • Corrected eight apparent-energy parameter names from “Apparent Power” to “Apparent Energy” (2056H–2065H). • Corrected unit labels for 42 peak-demand entries (kW → W: 20; kvar → var: 20; kVA → VA: 2). • Added engineering units to energy parameters. • Corrected peak-demand timestamp data type from DWORD to 6 bytes (3 registers). • Reformatted and reorganized the document, including parameter and block names, worksheet layout, address presentation, and reference information. • Consolidated Self-defined Measured Parameter into Real-time Parameters, and combined the energy blocks into Energy Reading (formerly Self-defined Energy Data).

## Modbus Map Overview
AcuRev 1310 ¦ Modbus Map Overview
Block ranges are inclusive, 0-based hexadecimal addresses. Select a worksheet link to open the detailed block.
Block | Start Address (Hex) | End Address (Hex) | Description | Worksheet
Meter Status | 0100H | 010FH | Wiring check result and seal status; includes reserved addresses. | Meter Status
SunSpec System Information | 1000H | 1044H | SunSpec identifier, manufacturer, model, firmware and device address. | SunSpec
SunSpec Measured Data | 1045H | 10B1H | Scaled measurements, energy counters and event flags; includes end markers. | SunSpec
Real-Time Parameters 2 | 1200H | 1221H | Additional measurements, power and current demand, and demand predictions. | Real-time Parameters
Energy by Tariff | 1300H | 136BH | Total, net and tariff energy counters. | Energy Reading
Prior Month Accumulated Energy Data | 1400H | 14ABH | Accumulated energy for the previous month. | Monthly Energy History
Prior Two-month Accumulated Energy Data | 1500H | 15ABH | Accumulated energy for two months ago. | Monthly Energy History
Current Demand Peak and Happening Time (Current Month) | 1600H | 1677H | Current-month peak demand values and occurrence timestamps. | Peak Demand & Timestamps
Current Demand Peak and Happening Time (Previous Month) | 1800H | 1877H | Previous-month peak demand values and occurrence timestamps. | Peak Demand & Timestamps
Demand Reset Event | 1B00H | 1B0AH | Demand reset count and timestamps. | Reset Event & Unseal Record
Meter Unseal Record | 1C00H | 1C13H | Unseal count and unseal/reseal timestamps. | Reset Event & Unseal Record
Event Reset | 1D00H | 1D0DH | Event reset count, timestamps and reset codes. | Reset Event & Unseal Record
Meter Reset | 1E00H | 1E0AH | Meter reset count and timestamps. | Reset Event & Unseal Record
Real-Time Parameters 1 | 2000H | 2045H | Current, voltage, frequency, power, power factor and phase angles. | Real-time Parameters
Energy by Phase | 2046H | 2085H | Imported/exported active, apparent and quadrant reactive energy by phase and total. | Energy Reading
Dual Source Energy Parameter | 3000H | 3001H | Dual-source enable and source selection. | Dual Source Energy
Dual Source Energy Command | 3100H | 3101H | Commands to clear dual-source energy or source-change logs. | Dual Source Energy
Dual Source Energy Data | 3200H | 320BH | Grid and alternate-source energy counters. | Dual Source Energy
Dual Source Change Log | 3300H | 332FH | Source-change timestamps, direction and energy snapshots. | Dual Source Energy
Max | 4000H | 407CH | Maximum measurement values and timestamps. | Max Min
Min | 4100H | 417CH | Minimum measurement values and timestamps. | Max Min
SunSpec System Information | C350H | C394H | SunSpec identifier, manufacturer, model, firmware and device address. | New SunSpec
SunSpec Measured Data | C395H | C401H | Scaled measurements, energy counters and event flags; includes end markers. | New SunSpec

## Data Types
AcuRev 1310 ¦ Data Types
One Modbus register = 16 bits (2 bytes).
Data Type | Registers | Description
Int16 | 1 | Signed 16-bit integer
UInt16 | 1 | Unsigned 16-bit integer
Int32 | 2 | Signed 32-bit integer
UInt32 | 2 | Unsigned 32-bit integer
Float32 (Float) | 2 | IEEE 754 single-precision floating-point number
Bitfield32 | 2 | 32-bit status flags; Meter Event Flags are defined below
String | As specified | Text string; length is specified in the register map
Timestamp — 6 bytes / 3 registers
Register | High Byte | Low Byte
1 | Year (YY) | Month (MM)
2 | Day (DD) | Hour (hh)
3 | Minute (mm) | Second (ss)
Record — Composite Data
Data Type | Registers | Field Layout (in register order)
Record (8 bytes) | 4 | Timestamp (6 bytes) + Reset Code (2 bytes)
Record (12 bytes) | 6 | Unseal Timestamp (6 bytes) + Reseal Timestamp (6 bytes)
Record (32 bytes) | 16 | Timestamp (6 bytes) + Direction (2 bytes) + six Energy values (4 bytes each)
Decode each field separately using the order and data types specified in the corresponding register block.
Common interpretation rules
Byte order: high byte first within each register.
32-bit numeric values: high-order register first, then low-order register.
Addresses are 0-based Modbus PDU addresses. Hex and Dec show the same starting address; Registers specifies the number of 16-bit registers.
SunSpec-specific information
The information below applies only to the SunSpec and New SunSpec sheets in this workbook.
Scale Factor (SF)
Engineering value = decoded raw value × 10^SF. SF is a signed Int16 exponent.
Apply SF only where specified. Read the SF register address shown in the parameter’s Range column; the listed unit applies after scaling.
Meter Event Flags — Bit Definitions
Bit | Description
0–1 | Reserved
2 | Power Failure
3 | Under Voltage
4 | Low Power Factor
5 | Over Current
6 | Over Voltage
7 | Missing Sensor
8–31 | Reserved

## Real-time Parameters
AcuRev 1310 ¦ Real-time Parameters
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Real-Time Parameters 1 (0x03 Read) | 2000H | 8192 | 2 | Total Current | A | Float32 | R
| 2002H | 8194 | 2 | Phase A Current | A | Float32 | R
| 2004H | 8196 | 2 | Phase B Current | A | Float32 | R
| 2006H | 8198 | 2 | Phase C Current | A | Float32 | R
| 2008H | 8200 | 2 | Phase Average Voltage | V | Float32 | R
| 200AH | 8202 | 2 | Phase A Voltage | V | Float32 | R
| 200CH | 8204 | 2 | Phase B Voltage | V | Float32 | R
| 200EH | 8206 | 2 | Phase C Voltage | V | Float32 | R
| 2010H | 8208 | 2 | Line Average Voltage | V | Float32 | R
| 2012H | 8210 | 2 | Line AB Voltage | V | Float32 | R
| 2014H | 8212 | 2 | Line BC Voltage | V | Float32 | R
| 2016H | 8214 | 2 | Line CA Voltage | V | Float32 | R
| 2018H | 8216 | 2 | Frequency | Hz | Float32 | R
| 201AH | 8218 | 2 | Total Active Power | W | Float32 | R
| 201CH | 8220 | 2 | Phase A Active Power | W | Float32 | R
| 201EH | 8222 | 2 | Phase B Active Power | W | Float32 | R
| 2020H | 8224 | 2 | Phase C Active Power | W | Float32 | R
| 2022H | 8226 | 2 | Total Apparent Power | VA | Float32 | R
| 2024H | 8228 | 2 | Phase A Apparent Power | VA | Float32 | R
| 2026H | 8230 | 2 | Phase B Apparent Power | VA | Float32 | R
| 2028H | 8232 | 2 | Phase C Apparent Power | VA | Float32 | R
| 202AH | 8234 | 2 | Total Reactive Power | var | Float32 | R
| 202CH | 8236 | 2 | Phase A Reactive Power | var | Float32 | R
| 202EH | 8238 | 2 | Phase B Reactive Power | var | Float32 | R
| 2030H | 8240 | 2 | Phase C Reactive Power | var | Float32 | R
| 2032H | 8242 | 2 | Power Factor | No unit | Float32 | R
| 2034H | 8244 | 2 | PF phase A | No unit | Float32 | R
| 2036H | 8246 | 2 | PF phase B | No unit | Float32 | R
| 2038H | 8248 | 2 | PF phase C | No unit | Float32 | R
| 203AH | 8250 | 2 | Phase Angle of V1 to V1 | ° | Float32 | R
| 203CH | 8252 | 2 | Phase Angle of V2 to V1 | ° | Float32 | R
| 203EH | 8254 | 2 | Phase Angle of V3 to V1 | ° | Float32 | R
| 2040H | 8256 | 2 | Phase Angle of I1 to V1 | ° | Float32 | R
| 2042H | 8258 | 2 | Phase Angle of I2 to V1 | ° | Float32 | R
| 2044H | 8260 | 2 | Phase Angle of I3 to V1 | ° | Float32 | R
Real-Time Parameters 2 (0x03 Read) | 1200H | 4608 | 2 | Neutral Current | A | Float32 | R | 0~9999A
| 1202H | 4610 | 2 | Residual Voltage | V | Float32 | R | 0~9999V
| 1204H | 4612 | 2 | Temperature of chips | °C | Float32 | R | -40°C ~ 80°C
| 1206H | 4614 | 2 | Load type | No unit | Float32 | R | 67(‘C’); 76(‘L’); 82(‘R’)
| 1208H | 4616 | 2 | system active power demand | W | Float32 | R
| 120AH | 4618 | 2 | system Reactive power demand | var | Float32 | R
| 120CH | 4620 | 2 | system apparent power demand | VA | Float32 | R
| 120EH | 4622 | 2 | Phase A current demand | A | Float32 | R
| 1210H | 4624 | 2 | Phase B current demand | A | Float32 | R
| 1212H | 4626 | 2 | Phase C current demand | A | Float32 | R
| 1214H | 4628 | 2 | System Active Power Demand Prediction | W | Float32 | R
| 1216H | 4630 | 2 | System Reactive Power Demand Prediction | var | Float32 | R
| 1218H | 4632 | 2 | System Apparent Power Demand Prediction | VA | Float32 | R
| 121AH | 4634 | 2 | Phase A Current Demand Prediction | A | Float32 | R
| 121CH | 4636 | 2 | Phase B Current Demand Prediction | A | Float32 | R
| 121EH | 4638 | 2 | Phase C Current Demand Prediction | A | Float32 | R
| 1220H | 4640 | 2 | Residual Current | A | Float32 | R

## Energy Reading
AcuRev 1310 ¦ Energy Reading
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Energy by Phase (0x03 Read, 0x10 Write) | 2046H | 8262 | 2 | Total Active Energy Exported | Wh | Int32 | R/W
| 2048H | 8264 | 2 | Active Energy Exported in Phase A | Wh | Int32 | R/W
| 204AH | 8266 | 2 | Active Energy Exported in Phase B | Wh | Int32 | R/W
| 204CH | 8268 | 2 | Active Energy Exported in Phase C | Wh | Int32 | R/W
| 204EH | 8270 | 2 | Total Active Energy Imported | Wh | Int32 | R/W
| 2050H | 8272 | 2 | Active Energy Imported in Phase A | Wh | Int32 | R/W
| 2052H | 8274 | 2 | Active Energy Imported in Phase B | Wh | Int32 | R/W
| 2054H | 8276 | 2 | Active Energy Imported in Phase C | Wh | Int32 | R/W
| 2056H | 8278 | 2 | Total Apparent Energy Exported | VAh | Int32 | R/W
| 2058H | 8280 | 2 | Apparent Energy Exported in Phase A | VAh | Int32 | R/W
| 205AH | 8282 | 2 | Apparent Energy Exported in Phase B | VAh | Int32 | R/W
| 205CH | 8284 | 2 | Apparent Energy Exported in Phase C | VAh | Int32 | R/W
| 205EH | 8286 | 2 | Total Apparent Energy Imported | VAh | Int32 | R/W
| 2060H | 8288 | 2 | Apparent Energy Imported in Phase A | VAh | Int32 | R/W
| 2062H | 8290 | 2 | Apparent Energy Imported in Phase B | VAh | Int32 | R/W
| 2064H | 8292 | 2 | Apparent Energy Imported in Phase C | VAh | Int32 | R/W
| 2066H | 8294 | 2 | Total Reactive Imported Q1 | varh | Int32 | R/W
| 2068H | 8296 | 2 | Reactive Imported Q1 Phase A | varh | Int32 | R/W
| 206AH | 8298 | 2 | Reactive Imported Q1 Phase B | varh | Int32 | R/W
| 206CH | 8300 | 2 | Reactive Imported Q1 Phase C | varh | Int32 | R/W
| 206EH | 8302 | 2 | Total Reactive Imported Q2 | varh | Int32 | R/W
| 2070H | 8304 | 2 | Reactive Imported Q2 Phase A | varh | Int32 | R/W
| 2072H | 8306 | 2 | Reactive Imported Q2 Phase B | varh | Int32 | R/W
| 2074H | 8308 | 2 | Reactive Imported Q2 Phase C | varh | Int32 | R/W
| 2076H | 8310 | 2 | Total Reactive Energy Exported Q3 | varh | Int32 | R/W
| 2078H | 8312 | 2 | Reactive Energy Exported Q3 Phase A | varh | Int32 | R/W
| 207AH | 8314 | 2 | Reactive Energy Exported Q3 Phase B | varh | Int32 | R/W
| 207CH | 8316 | 2 | Reactive Energy Exported Q3 Phase C | varh | Int32 | R/W
| 207EH | 8318 | 2 | Total Reactive Energy Exported Q4 | varh | Int32 | R/W
| 2080H | 8320 | 2 | Reactive Energy Exported Q4 Phase A | varh | Int32 | R/W
| 2082H | 8322 | 2 | Reactive Energy Exported Q4 Phase B | varh | Int32 | R/W
| 2084H | 8324 | 2 | Reactive Energy Exported Q4 Phase C | varh | Int32 | R/W
Energy by Tariff (0x03 Read, 0x10 Write) | 1300H | 4864 | 2 | Total Active Energy | Wh | Int32 | R/W | 0~+999999999
| 1302H | 4866 | 2 | Total Active Energy tariff 1 | Wh | Int32 | R/W | 0~+999999999
| 1304H | 4868 | 2 | Total Active Energy tariff 2 | Wh | Int32 | R/W | 0~+999999999
| 1306H | 4870 | 2 | Total Active Energy tariff 3 | Wh | Int32 | R/W | 0~+999999999
| 1308H | 4872 | 2 | Total Active Energy tariff 4 | Wh | Int32 | R/W | 0~+999999999
| 130AH | 4874 | 2 | Net Active Energy | Wh | Int32 | R/W | -999999999~+999999999
| 130CH | 4876 | 2 | Net Active Energy tariff 1 | Wh | Int32 | R/W | -999999999~+999999999
| 130EH | 4878 | 2 | Net Active Energy tariff 2 | Wh | Int32 | R/W | -999999999~+999999999
| 1310H | 4880 | 2 | Net Active Energy tariff 3 | Wh | Int32 | R/W | -999999999~+999999999
| 1312H | 4882 | 2 | Net Active Energy tariff 4 | Wh | Int32 | R/W | -999999999~+999999999
| 1314H | 4884 | 2 | Imported Active Energy tariff 1 | Wh | Int32 | R/W | 0~+999999999
| 1316H | 4886 | 2 | Imported Active Energy tariff 2 | Wh | Int32 | R/W | 0~+999999999
| 1318H | 4888 | 2 | Imported Active Energy tariff 3 | Wh | Int32 | R/W | 0~+999999999
| 131AH | 4890 | 2 | Imported Active Energy tariff 4 | Wh | Int32 | R/W | 0~+999999999
| 131CH | 4892 | 2 | Exported Active Energy tariff 1 | Wh | Int32 | R/W | 0~+999999999
| 131EH | 4894 | 2 | Exported Active Energy tariff 2 | Wh | Int32 | R/W | 0~+999999999
| 1320H | 4896 | 2 | Exported Active Energy tariff 3 | Wh | Int32 | R/W | 0~+999999999
| 1322H | 4898 | 2 | Exported Active Energy tariff 4 | Wh | Int32 | R/W | 0~+999999999
| 1324H | 4900 | 2 | Total Reactive Energy Imported | varh | Int32 | R/W | 0~+999999999
| 1326H | 4902 | 2 | Total Reactive Energy Imported tariff 1 | varh | Int32 | R/W | 0~+999999999
| 1328H | 4904 | 2 | Total Reactive Energy Imported tariff 2 | varh | Int32 | R/W | 0~+999999999
| 132AH | 4906 | 2 | Total Reactive Energy Imported tariff 3 | varh | Int32 | R/W | 0~+999999999
| 132CH | 4908 | 2 | Total Reactive Energy Imported tariff 4 | varh | Int32 | R/W | 0~+999999999
| 132EH | 4910 | 2 | Total Reactive Energy Exported | varh | Int32 | R/W | 0~+999999999
| 1330H | 4912 | 2 | Exported Reactive Energy tariff 1 | varh | Int32 | R/W | 0~+999999999
| 1332H | 4914 | 2 | Exported Reactive Energy tariff 2 | varh | Int32 | R/W | 0~+999999999
| 1334H | 4916 | 2 | Exported Reactive Energy tariff 3 | varh | Int32 | R/W | 0~+999999999
| 1336H | 4918 | 2 | Exported Reactive Energy tariff 4 | varh | Int32 | R/W | 0~+999999999
| 1338H | 4920 | 2 | Total Reactive Energy | varh | Int32 | R/W | 0~+999999999
| 133AH | 4922 | 2 | Total Reactive Energy tariff 1 | varh | Int32 | R/W | 0~+999999999
| 133CH | 4924 | 2 | Total Reactive Energy tariff 2 | varh | Int32 | R/W | 0~+999999999
| 133EH | 4926 | 2 | Total Reactive Energy tariff 3 | varh | Int32 | R/W | 0~+999999999
| 1340H | 4928 | 2 | Total Reactive Energy tariff 4 | varh | Int32 | R/W | 0~+999999999
| 1342H | 4930 | 2 | Net Reactive Energy | varh | Int32 | R/W | -999999999~+999999999
| 1344H | 4932 | 2 | Net Reactive Energy tariff 1 | varh | Int32 | R/W | -999999999~+999999999
| 1346H | 4934 | 2 | Net Reactive Energy tariff 2 | varh | Int32 | R/W | -999999999~+999999999
| 1348H | 4936 | 2 | Net Reactive Energy tariff 3 | varh | Int32 | R/W | -999999999~+999999999
| 134AH | 4938 | 2 | Net Reactive Energy tariff 4 | varh | Int32 | R/W | -999999999~+999999999
| 134CH | 4940 | 2 | Total Reactive Energy Imported Q1 tariff 1 | varh | Int32 | R/W | 0~+999999999
| 134EH | 4942 | 2 | Total Reactive Energy Imported Q1 tariff 2 | varh | Int32 | R/W | 0~+999999999
| 1350H | 4944 | 2 | Total Reactive Energy Imported Q1 tariff 3 | varh | Int32 | R/W | 0~+999999999
| 1352H | 4946 | 2 | Total Reactive Energy Imported Q1 tariff 4 | varh | Int32 | R/W | 0~+999999999
| 1354H | 4948 | 2 | Total Reactive Energy Imported Q2 tariff 1 | varh | Int32 | R/W | 0~+999999999
| 1356H | 4950 | 2 | Total Reactive Energy Imported Q2 tariff 2 | varh | Int32 | R/W | 0~+999999999
| 1358H | 4952 | 2 | Total Reactive Energy Imported Q2 tariff 3 | varh | Int32 | R/W | 0~+999999999
| 135AH | 4954 | 2 | Total Reactive Energy Imported Q2 tariff 4 | varh | Int32 | R/W | 0~+999999999
| 135CH | 4956 | 2 | Total Reactive Energy Exported Q3 tariff 1 | varh | Int32 | R/W | 0~+999999999
| 135EH | 4958 | 2 | Total Reactive Energy Exported Q3 tariff 2 | varh | Int32 | R/W | 0~+999999999
| 1360H | 4960 | 2 | Total Reactive Energy Exported Q3 tariff 3 | varh | Int32 | R/W | 0~+999999999
| 1362H | 4962 | 2 | Total Reactive Energy Exported Q3 tariff 4 | varh | Int32 | R/W | 0~+999999999
| 1364H | 4964 | 2 | Total Reactive Energy Exported Q4 tariff 1 | varh | Int32 | R/W | 0~+999999999
| 1366H | 4966 | 2 | Total Reactive Energy Exported Q4 tariff 2 | varh | Int32 | R/W | 0~+999999999
| 1368H | 4968 | 2 | Total Reactive Energy Exported Q4 tariff 3 | varh | Int32 | R/W | 0~+999999999
| 136AH | 4970 | 2 | Total Reactive Energy Exported Q4 tariff 4 | varh | Int32 | R/W | 0~+999999999

## Monthly Energy History
AcuRev 1310 ¦ Monthly Energy History
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Prior Month Accumulated Energy Data (0x03 Read) | 1400H | 5120 | 2 | Total Active Energy Imported | Wh | Int32 | R | 0~+999999999
| 1402H | 5122 | 2 | Active Energy Imported in phase A | Wh | Int32 | R | 0~+999999999
| 1404H | 5124 | 2 | Active Energy Imported in phase B | Wh | Int32 | R | 0~+999999999
| 1406H | 5126 | 2 | Active Energy Imported in phase C | Wh | Int32 | R | 0~+999999999
| 1408H | 5128 | 2 | Total Active Energy Imported tariff 1 | Wh | Int32 | R | 0~+999999999
| 140AH | 5130 | 2 | Total Active Energy Imported tariff 2 | Wh | Int32 | R | 0~+999999999
| 140CH | 5132 | 2 | Total Active Energy Imported tariff 3 | Wh | Int32 | R | 0~+999999999
| 140EH | 5134 | 2 | Total Active Energy Imported tariff 4 | Wh | Int32 | R | 0~+999999999
| 1410H | 5136 | 2 | Total Active Energy Exported | Wh | Int32 | R | 0~+999999999
| 1412H | 5138 | 2 | Active Energy Exported in phase A | Wh | Int32 | R | 0~+999999999
| 1414H | 5140 | 2 | Active Energy Exported in phase B | Wh | Int32 | R | 0~+999999999
| 1416H | 5142 | 2 | Active Energy Exported in phase C | Wh | Int32 | R | 0~+999999999
| 1418H | 5144 | 2 | Total Active Energy Exported tariff 1 | Wh | Int32 | R | 0~+999999999
| 141AH | 5146 | 2 | Total Active Energy Exported tariff 2 | Wh | Int32 | R | 0~+999999999
| 141CH | 5148 | 2 | Total Active Energy Exported tariff 3 | Wh | Int32 | R | 0~+999999999
| 141EH | 5150 | 2 | Total Active Energy Exported tariff 4 | Wh | Int32 | R | 0~+999999999
| 1420H | 5152 | 2 | Total Active Energy | Wh | Int32 | R | 0~+999999999
| 1422H | 5154 | 2 | Total Active Energy tariff 1 | Wh | Int32 | R | 0~+999999999
| 1424H | 5156 | 2 | Total Active Energy tariff 2 | Wh | Int32 | R | 0~+999999999
| 1426H | 5158 | 2 | Total Active Energy tariff 3 | Wh | Int32 | R | 0~+999999999
| 1428H | 5160 | 2 | Total Active Energy tariff 4 | Wh | Int32 | R | 0~+999999999
| 142AH | 5162 | 2 | Net Active Energy | Wh | Int32 | R | -999999999~+999999999
| 142CH | 5164 | 2 | Net Active Energy tariff 1 | Wh | Int32 | R | -999999999~+999999999
| 142EH | 5166 | 2 | Net Active Energy tariff 2 | Wh | Int32 | R | -999999999~+999999999
| 1430H | 5168 | 2 | Net Active Energy tariff 3 | Wh | Int32 | R | -999999999~+999999999
| 1432H | 5170 | 2 | Net Active Energy tariff 4 | Wh | Int32 | R | -999999999~+999999999
| 1434H | 5172 | 2 | Total Reactive energy Imported Q1 | varh | Int32 | R | 0~+999999999
| 1436H | 5174 | 2 | Reactive energy Imported Q1 in phase A | varh | Int32 | R | 0~+999999999
| 1438H | 5176 | 2 | Reactive energy Imported Q1 in phase B | varh | Int32 | R | 0~+999999999
| 143AH | 5178 | 2 | Reactive energy Imported Q1 in phase C | varh | Int32 | R | 0~+999999999
| 143CH | 5180 | 2 | Total Reactive energy Imported Q1 tariff 1 | varh | Int32 | R | 0~+999999999
| 143EH | 5182 | 2 | Total Reactive energy Imported Q1 tariff 2 | varh | Int32 | R | 0~+999999999
| 1440H | 5184 | 2 | Total Reactive energy Imported Q1 tariff 3 | varh | Int32 | R | 0~+999999999
| 1442H | 5186 | 2 | Total Reactive energy Imported Q1 tariff 4 | varh | Int32 | R | 0~+999999999
| 1444H | 5188 | 2 | Total Reactive energy Imported Q2 | varh | Int32 | R | 0~+999999999
| 1446H | 5190 | 2 | Reactive energy Imported Q2 phase A | varh | Int32 | R | 0~+999999999
| 1448H | 5192 | 2 | Reactive energy Imported Q2 phase B | varh | Int32 | R | 0~+999999999
| 144AH | 5194 | 2 | Reactive energy Imported Q2 phase C | varh | Int32 | R | 0~+999999999
| 144CH | 5196 | 2 | Total Reactive energy Imported Q2 tariff 1 | varh | Int32 | R | 0~+999999999
| 144EH | 5198 | 2 | Total Reactive energy Imported Q2 tariff 2 | varh | Int32 | R | 0~+999999999
| 1450H | 5200 | 2 | Total Reactive energy Imported Q2 tariff 3 | varh | Int32 | R | 0~+999999999
| 1452H | 5202 | 2 | Total Reactive energy Imported Q2 tariff 4 | varh | Int32 | R | 0~+999999999
| 1454H | 5204 | 2 | Total Reactive energy Exported Q3 | varh | Int32 | R | 0~+999999999
| 1456H | 5206 | 2 | Reactive energy Exported Q3 phase A | varh | Int32 | R | 0~+999999999
| 1458H | 5208 | 2 | Reactive energy Exported Q3 phase B | varh | Int32 | R | 0~+999999999
| 145AH | 5210 | 2 | Reactive energy Exported Q3 phase C | varh | Int32 | R | 0~+999999999
| 145CH | 5212 | 2 | Total Reactive energy Exported Q3 tariff 1 | varh | Int32 | R | 0~+999999999
| 145EH | 5214 | 2 | Total Reactive energy Exported Q3 tariff 2 | varh | Int32 | R | 0~+999999999
| 1460H | 5216 | 2 | Total Reactive energy Exported Q3 tariff 3 | varh | Int32 | R | 0~+999999999
| 1462H | 5218 | 2 | Total Reactive energy Exported Q3 tariff 4 | varh | Int32 | R | 0~+999999999
| 1464H | 5220 | 2 | Total VAR-hours Exported energy d Q4 | Wh | Int32 | R | 0~+999999999
| 1466H | 5222 | 2 | Reactive energy Exported Q4 phase A | varh | Int32 | R | 0~+999999999
| 1468H | 5224 | 2 | Reactive energy Exported Q4 phase B | varh | Int32 | R | 0~+999999999
| 146AH | 5226 | 2 | Reactive energy Exported Q4 phase C | varh | Int32 | R | 0~+999999999
| 146CH | 5228 | 2 | Total Reactive energy Exported Q4 tariff 1 | varh | Int32 | R | 0~+999999999
| 146EH | 5230 | 2 | Total Reactive energy Exported Q4 tariff 2 | varh | Int32 | R | 0~+999999999
| 1470H | 5232 | 2 | Total Reactive energy Exported Q4 tariff 3 | varh | Int32 | R | 0~+999999999
| 1472H | 5234 | 2 | Total Reactive energy Exported Q4 tariff 4 | varh | Int32 | R | 0~+999999999
| 1474H | 5236 | 2 | Total Reactive energy Imported | varh | Int32 | R | 0~+999999999
| 1476H | 5238 | 2 | Total Reactive energy Imported tariff 1 | varh | Int32 | R | 0~+999999999
| 1478H | 5240 | 2 | Total Reactive energy Imported tariff 2 | varh | Int32 | R | 0~+999999999
| 147AH | 5242 | 2 | Total Reactive energy Imported tariff 3 | varh | Int32 | R | 0~+999999999
| 147CH | 5244 | 2 | Total Reactive energy Imported tariff 4 | varh | Int32 | R | 0~+999999999
| 147EH | 5246 | 2 | Total Reactive energy Exported | varh | Int32 | R | 0~+999999999
| 1480H | 5248 | 2 | Total Reactive energy Exported tariff 1 | varh | Int32 | R | 0~+999999999
| 1482H | 5250 | 2 | Total Reactive energy Exported tariff 2 | varh | Int32 | R | 0~+999999999
| 1484H | 5252 | 2 | Total Reactive energy Exported tariff 3 | varh | Int32 | R | 0~+999999999
| 1486H | 5254 | 2 | Total Reactive energy Exported tariff 4 | varh | Int32 | R | 0~+999999999
| 1488H | 5256 | 2 | Total Reactive Energy | varh | Int32 | R | 0~+999999999
| 148AH | 5258 | 2 | Total Reactive Energy tariff 1 | varh | Int32 | R | 0~+999999999
| 148CH | 5260 | 2 | Total Reactive Energy tariff 2 | varh | Int32 | R | 0~+999999999
| 148EH | 5262 | 2 | Total Reactive Energy tariff 3 | varh | Int32 | R | 0~+999999999
| 1490H | 5264 | 2 | Total Reactive Energy tariff 4 | varh | Int32 | R | 0~+999999999
| 1492H | 5266 | 2 | Net Reactive Energy | varh | Int32 | R | -999999999~+999999999
| 1494H | 5268 | 2 | Net Reactive Energy tariff 1 | varh | Int32 | R | -999999999~+999999999
| 1496H | 5270 | 2 | Net Reactive Energy tariff 2 | varh | Int32 | R | -999999999~+999999999
| 1498H | 5272 | 2 | Net Reactive Energy tariff 3 | varh | Int32 | R | -999999999~+999999999
| 149AH | 5274 | 2 | Net Reactive Energy tariff 4 | varh | Int32 | R | -999999999~+999999999
| 149CH | 5276 | 2 | Total Apparent Energy Imported | VAh | Int32 | R | 0~+999999999
| 149EH | 5278 | 2 | Apparent Energy Imported phase A | VAh | Int32 | R | 0~+999999999
| 14A0H | 5280 | 2 | Apparent Energy Imported phase B | VAh | Int32 | R | 0~+999999999
| 14A2H | 5282 | 2 | Apparent Energy Imported phase C | VAh | Int32 | R | 0~+999999999
| 14A4H | 5284 | 2 | Total Apparent Energy Exported | VAh | Int32 | R | 0~+999999999
| 14A6H | 5286 | 2 | Apparent Energy Exported phase A | VAh | Int32 | R | 0~+999999999
| 14A8H | 5288 | 2 | Apparent Energy Exported phase B | VAh | Int32 | R | 0~+999999999
| 14AAH | 5290 | 2 | Apparent Energy Exported phase C | VAh | Int32 | R | 0~+999999999
Prior Two-month Accumulated Energy Data (0x03 Read) | 1500H | 5376 | 2 | Total Active Energy Imported | Wh | Int32 | R | 0~+999999999
| 1502H | 5378 | 2 | Active Energy Imported in phase A | Wh | Int32 | R | 0~+999999999
| 1504H | 5380 | 2 | Active Energy Imported in phase B | Wh | Int32 | R | 0~+999999999
| 1506H | 5382 | 2 | Active Energy Imported in phase C | Wh | Int32 | R | 0~+999999999
| 1508H | 5384 | 2 | Total Active Energy Imported tariff 1 | Wh | Int32 | R | 0~+999999999
| 150AH | 5386 | 2 | Total Active Energy Imported tariff 2 | Wh | Int32 | R | 0~+999999999
| 150CH | 5388 | 2 | Total Active Energy Imported tariff 3 | Wh | Int32 | R | 0~+999999999
| 150EH | 5390 | 2 | Total Active Energy Imported tariff 4 | Wh | Int32 | R | 0~+999999999
| 1510H | 5392 | 2 | Total Active Energy Exported | Wh | Int32 | R | 0~+999999999
| 1512H | 5394 | 2 | Active Energy Exported in phase A | Wh | Int32 | R | 0~+999999999
| 1514H | 5396 | 2 | Active Energy Exported in phase B | Wh | Int32 | R | 0~+999999999
| 1516H | 5398 | 2 | Active Energy Exported in phase C | Wh | Int32 | R | 0~+999999999
| 1518H | 5400 | 2 | Total Active Energy Exported tariff 1 | Wh | Int32 | R | 0~+999999999
| 151AH | 5402 | 2 | Total Active Energy Exported tariff 2 | Wh | Int32 | R | 0~+999999999
| 151CH | 5404 | 2 | Total Active Energy Exported tariff 3 | Wh | Int32 | R | 0~+999999999
| 151EH | 5406 | 2 | Total Active Energy Exported tariff 4 | Wh | Int32 | R | 0~+999999999
| 1520H | 5408 | 2 | Total Active Energy | Wh | Int32 | R | 0~+999999999
| 1522H | 5410 | 2 | Total Active Energy tariff 1 | Wh | Int32 | R | 0~+999999999
| 1524H | 5412 | 2 | Total Active Energy tariff 2 | Wh | Int32 | R | 0~+999999999
| 1526H | 5414 | 2 | Total Active Energy tariff 3 | Wh | Int32 | R | 0~+999999999
| 1528H | 5416 | 2 | Total Active Energy tariff 4 | Wh | Int32 | R | 0~+999999999
| 152AH | 5418 | 2 | Net Active Energy | Wh | Int32 | R | -999999999~+999999999
| 152CH | 5420 | 2 | Net Active Energy tariff 1 | Wh | Int32 | R | -999999999~+999999999
| 152EH | 5422 | 2 | Net Active Energy tariff 2 | Wh | Int32 | R | -999999999~+999999999
| 1530H | 5424 | 2 | Net Active Energy tariff 3 | Wh | Int32 | R | -999999999~+999999999
| 1532H | 5426 | 2 | Net Active Energy tariff 4 | Wh | Int32 | R | -999999999~+999999999
| 1534H | 5428 | 2 | Total Reactive energy Imported Q1 | varh | Int32 | R | 0~+999999999
| 1536H | 5430 | 2 | Reactive energy Imported Q1 in phase A | varh | Int32 | R | 0~+999999999
| 1538H | 5432 | 2 | Reactive energy Imported Q1 in phase B | varh | Int32 | R | 0~+999999999
| 153AH | 5434 | 2 | Reactive energy Imported Q1 in phase C | varh | Int32 | R | 0~+999999999
| 153CH | 5436 | 2 | Total Reactive energy Imported Q1 tariff 1 | varh | Int32 | R | 0~+999999999
| 153EH | 5438 | 2 | Total Reactive energy Imported Q1 tariff 2 | varh | Int32 | R | 0~+999999999
| 1540H | 5440 | 2 | Total Reactive energy Imported Q1 tariff 3 | varh | Int32 | R | 0~+999999999
| 1542H | 5442 | 2 | Total Reactive energy Imported Q1 tariff 4 | varh | Int32 | R | 0~+999999999
| 1544H | 5444 | 2 | Total Reactive energy Imported Q2 | varh | Int32 | R | 0~+999999999
| 1546H | 5446 | 2 | Reactive energy Imported Q2 phase A | varh | Int32 | R | 0~+999999999
| 1548H | 5448 | 2 | Reactive energy Imported Q2 phase B | varh | Int32 | R | 0~+999999999
| 154AH | 5450 | 2 | Reactive energy Imported Q2 phase C | varh | Int32 | R | 0~+999999999
| 154CH | 5452 | 2 | Total Reactive energy Imported Q2 tariff 1 | varh | Int32 | R | 0~+999999999
| 154EH | 5454 | 2 | Total Reactive energy Imported Q2 tariff 2 | varh | Int32 | R | 0~+999999999
| 1550H | 5456 | 2 | Total Reactive energy Imported Q2 tariff 3 | varh | Int32 | R | 0~+999999999
| 1552H | 5458 | 2 | Total Reactive energy Imported Q2 tariff 4 | varh | Int32 | R | 0~+999999999
| 1554H | 5460 | 2 | Total Reactive energy Exported Q3 | varh | Int32 | R | 0~+999999999
| 1556H | 5462 | 2 | Reactive energy Exported Q3 phase A | varh | Int32 | R | 0~+999999999
| 1558H | 5464 | 2 | Reactive energy Exported Q3 phase B | varh | Int32 | R | 0~+999999999
| 155AH | 5466 | 2 | Reactive energy Exported Q3 phase C | varh | Int32 | R | 0~+999999999
| 155CH | 5468 | 2 | Total Reactive energy Exported Q3 tariff 1 | varh | Int32 | R | 0~+999999999
| 155EH | 5470 | 2 | Total Reactive energy Exported Q3 tariff 2 | varh | Int32 | R | 0~+999999999
| 1560H | 5472 | 2 | Total Reactive energy Exported Q3 tariff 3 | varh | Int32 | R | 0~+999999999
| 1562H | 5474 | 2 | Total Reactive energy Exported Q3 tariff 4 | varh | Int32 | R | 0~+999999999
| 1564H | 5476 | 2 | Total VAR-hours Exported energy d Q4 | Wh | Int32 | R | 0~+999999999
| 1566H | 5478 | 2 | Reactive energy Exported Q4 phase A | varh | Int32 | R | 0~+999999999
| 1568H | 5480 | 2 | Reactive energy Exported Q4 phase B | varh | Int32 | R | 0~+999999999
| 156AH | 5482 | 2 | Reactive energy Exported Q4 phase C | varh | Int32 | R | 0~+999999999
| 156CH | 5484 | 2 | Total Reactive energy Exported Q4 tariff 1 | varh | Int32 | R | 0~+999999999
| 156EH | 5486 | 2 | Total Reactive energy Exported Q4 tariff 2 | varh | Int32 | R | 0~+999999999
| 1570H | 5488 | 2 | Total Reactive energy Exported Q4 tariff 3 | varh | Int32 | R | 0~+999999999
| 1572H | 5490 | 2 | Total Reactive energy Exported Q4 tariff 4 | varh | Int32 | R | 0~+999999999
| 1574H | 5492 | 2 | Total Reactive energy Imported | varh | Int32 | R | 0~+999999999
| 1576H | 5494 | 2 | Total Reactive energy Imported tariff 1 | varh | Int32 | R | 0~+999999999
| 1578H | 5496 | 2 | Total Reactive energy Imported tariff 2 | varh | Int32 | R | 0~+999999999
| 157AH | 5498 | 2 | Total Reactive energy Imported tariff 3 | varh | Int32 | R | 0~+999999999
| 157CH | 5500 | 2 | Total Reactive energy Imported tariff 4 | varh | Int32 | R | 0~+999999999
| 157EH | 5502 | 2 | Total Reactive energy Exported | varh | Int32 | R | 0~+999999999
| 1580H | 5504 | 2 | Total Reactive energy Exported tariff 1 | varh | Int32 | R | 0~+999999999
| 1582H | 5506 | 2 | Total Reactive energy Exported tariff 2 | varh | Int32 | R | 0~+999999999
| 1584H | 5508 | 2 | Total Reactive energy Exported tariff 3 | varh | Int32 | R | 0~+999999999
| 1586H | 5510 | 2 | Total Reactive energy Exported tariff 4 | varh | Int32 | R | 0~+999999999
| 1588H | 5512 | 2 | Total Reactive Energy | varh | Int32 | R | 0~+999999999
| 158AH | 5514 | 2 | Total Reactive Energy tariff 1 | varh | Int32 | R | 0~+999999999
| 158CH | 5516 | 2 | Total Reactive Energy tariff 2 | varh | Int32 | R | 0~+999999999
| 158EH | 5518 | 2 | Total Reactive Energy tariff 3 | varh | Int32 | R | 0~+999999999
| 1590H | 5520 | 2 | Total Reactive Energy tariff 4 | varh | Int32 | R | 0~+999999999
| 1592H | 5522 | 2 | Net Reactive Energy | varh | Int32 | R | -999999999~+999999999
| 1594H | 5524 | 2 | Net Reactive Energy tariff 1 | varh | Int32 | R | -999999999~+999999999
| 1596H | 5526 | 2 | Net Reactive Energy tariff 2 | varh | Int32 | R | -999999999~+999999999
| 1598H | 5528 | 2 | Net Reactive Energy tariff 3 | varh | Int32 | R | -999999999~+999999999
| 159AH | 5530 | 2 | Net Reactive Energy tariff 4 | varh | Int32 | R | -999999999~+999999999
| 159CH | 5532 | 2 | Total Apparent Energy Imported | VAh | Int32 | R | 0~+999999999
| 159EH | 5534 | 2 | Apparent Energy Imported phase A | VAh | Int32 | R | 0~+999999999
| 15A0H | 5536 | 2 | Apparent Energy Imported phase B | VAh | Int32 | R | 0~+999999999
| 15A2H | 5538 | 2 | Apparent Energy Imported phase C | VAh | Int32 | R | 0~+999999999
| 15A4H | 5540 | 2 | Total Apparent Energy Exported | VAh | Int32 | R | 0~+999999999
| 15A6H | 5542 | 2 | Apparent Energy Exported phase A | VAh | Int32 | R | 0~+999999999
| 15A8H | 5544 | 2 | Apparent Energy Exported phase B | VAh | Int32 | R | 0~+999999999
| 15AAH | 5546 | 2 | Apparent Energy Exported phase C | VAh | Int32 | R | 0~+999999999

## Peak Demand & Timestamps
AcuRev 1310 ¦ Peak Demand & Timestamps
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Current Demand Peak and Happening Time (Current Month) (0x03 Read) | 1600H | 5632 | 2 | Total Imported Active Power Demand Peak | W | Float32 | R | Float32 value (W)
| 1602H | 5634 | 3 | Total Imported Active Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1605H | 5637 | 2 | Imported Active Power Demand 1 Peak | W | Float32 | R | Float32 value (W)
| 1607H | 5639 | 3 | Imported Active Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 160AH | 5642 | 2 | Imported Active Power Demand 2 Peak | W | Float32 | R | Float32 value (W)
| 160CH | 5644 | 3 | Imported Active Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 160FH | 5647 | 2 | Imported Active Power Demand 3 Peak | W | Float32 | R | Float32 value (W)
| 1611H | 5649 | 3 | Imported Active Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1614H | 5652 | 2 | Imported Active Power Demand 4 Peak | W | Float32 | R | Float32 value (W)
| 1616H | 5654 | 3 | Imported Active Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1619H | 5657 | 2 | Total Exported Active Power Demand Peak | W | Float32 | R | Float32 value (W)
| 161BH | 5659 | 3 | Total Exported Active Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 161EH | 5662 | 2 | Exported Active Power Demand 1 Peak | W | Float32 | R | Float32 value (W)
| 1620H | 5664 | 3 | Exported Active Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1623H | 5667 | 2 | Exported Active Power Demand 2 Peak | W | Float32 | R | Float32 value (W)
| 1625H | 5669 | 3 | Exported Active Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1628H | 5672 | 2 | Exported Active Power Demand 3 Peak | W | Float32 | R | Float32 value (W)
| 162AH | 5674 | 3 | Exported Active Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 162DH | 5677 | 2 | Exported Active Power Demand 4 Peak | W | Float32 | R | Float32 value (W)
| 162FH | 5679 | 3 | Exported Active Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1632H | 5682 | 2 | Total Imported Reactive Power Demand Peak | var | Float32 | R | Float32 value (var)
| 1634H | 5684 | 3 | Total Imported Reactive Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1637H | 5687 | 2 | Imported Reactive Power Demand 1 Peak | var | Float32 | R | Float32 value (var)
| 1639H | 5689 | 3 | Imported Reactive Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 163CH | 5692 | 2 | Imported Reactive Power Demand 2 Peak | var | Float32 | R | Float32 value (var)
| 163EH | 5694 | 3 | Imported Reactive Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1641H | 5697 | 2 | Imported Reactive Power Demand 3 Peak | var | Float32 | R | Float32 value (var)
| 1643H | 5699 | 3 | Imported Reactive Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1646H | 5702 | 2 | Imported Reactive Power Demand 4 Peak | var | Float32 | R | Float32 value (var)
| 1648H | 5704 | 3 | Imported Reactive Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 164BH | 5707 | 2 | Total Exported Reactive Power Demand Peak | var | Float32 | R | Float32 value (var)
| 164DH | 5709 | 3 | Total Exported Reactive Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1650H | 5712 | 2 | Exported Reactive Power Demand 1 Peak | var | Float32 | R | Float32 value (var)
| 1652H | 5714 | 3 | Exported Reactive Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1655H | 5717 | 2 | Exported Reactive Power Demand 2 Peak | var | Float32 | R | Float32 value (var)
| 1657H | 5719 | 3 | Exported Reactive Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 165AH | 5722 | 2 | Exported Reactive Power Demand 3 Peak | var | Float32 | R | Float32 value (var)
| 165CH | 5724 | 3 | Exported Reactive Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 165FH | 5727 | 2 | Exported Reactive Power Demand 4 Peak | var | Float32 | R | Float32 value (var)
| 1661H | 5729 | 3 | Exported Reactive Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1664H | 5732 | 2 | Total Apparent Power Demand Peak | VA | Float32 | R | Float32 value (VA)
| 1666H | 5734 | 3 | Total Apparent Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1669H | 5737 | 2 | Phase A Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 166BH | 5739 | 3 | Phase A Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 166EH | 5742 | 2 | Phase B Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 1670H | 5744 | 3 | Phase B Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1673H | 5747 | 2 | Phase C Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 1675H | 5749 | 3 | Phase C Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
Current Demand Peak and Happening Time (Previous Month) (0x03 Read) | 1800H | 6144 | 2 | Total Imported Active Power Demand Peak | W | Float32 | R | Float32 value (W)
| 1802H | 6146 | 3 | Total Imported Active Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1805H | 6149 | 2 | Imported Active Power Demand 1 Peak | W | Float32 | R | Float32 value (W)
| 1807H | 6151 | 3 | Imported Active Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 180AH | 6154 | 2 | Imported Active Power Demand 2 Peak | W | Float32 | R | Float32 value (W)
| 180CH | 6156 | 3 | Imported Active Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 180FH | 6159 | 2 | Imported Active Power Demand 3 Peak | W | Float32 | R | Float32 value (W)
| 1811H | 6161 | 3 | Imported Active Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1814H | 6164 | 2 | Imported Active Power Demand 4 Peak | W | Float32 | R | Float32 value (W)
| 1816H | 6166 | 3 | Imported Active Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1819H | 6169 | 2 | Total Exported Active Power Demand Peak | W | Float32 | R | Float32 value (W)
| 181BH | 6171 | 3 | Total Exported Active Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 181EH | 6174 | 2 | Exported Active Power Demand 1 Peak | W | Float32 | R | Float32 value (W)
| 1820H | 6176 | 3 | Exported Active Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1823H | 6179 | 2 | Exported Active Power Demand 2 Peak | W | Float32 | R | Float32 value (W)
| 1825H | 6181 | 3 | Exported Active Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1828H | 6184 | 2 | Exported Active Power Demand 3 Peak | W | Float32 | R | Float32 value (W)
| 182AH | 6186 | 3 | Exported Active Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 182DH | 6189 | 2 | Exported Active Power Demand 4 Peak | W | Float32 | R | Float32 value (W)
| 182FH | 6191 | 3 | Exported Active Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1832H | 6194 | 2 | Total Imported Reactive Power Demand Peak | var | Float32 | R | Float32 value (var)
| 1834H | 6196 | 3 | Total Imported Reactive Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1837H | 6199 | 2 | Imported Reactive Power Demand 1 Peak | var | Float32 | R | Float32 value (var)
| 1839H | 6201 | 3 | Imported Reactive Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 183CH | 6204 | 2 | Imported Reactive Power Demand 2 Peak | var | Float32 | R | Float32 value (var)
| 183EH | 6206 | 3 | Imported Reactive Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1841H | 6209 | 2 | Imported Reactive Power Demand 3 Peak | var | Float32 | R | Float32 value (var)
| 1843H | 6211 | 3 | Imported Reactive Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1846H | 6214 | 2 | Imported Reactive Power Demand 4 Peak | var | Float32 | R | Float32 value (var)
| 1848H | 6216 | 3 | Imported Reactive Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 184BH | 6219 | 2 | Total Exported Reactive Power Demand Peak | var | Float32 | R | Float32 value (var)
| 184DH | 6221 | 3 | Total Exported Reactive Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1850H | 6224 | 2 | Exported Reactive Power Demand 1 Peak | var | Float32 | R | Float32 value (var)
| 1852H | 6226 | 3 | Exported Reactive Power Demand 1 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1855H | 6229 | 2 | Exported Reactive Power Demand 2 Peak | var | Float32 | R | Float32 value (var)
| 1857H | 6231 | 3 | Exported Reactive Power Demand 2 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 185AH | 6234 | 2 | Exported Reactive Power Demand 3 Peak | var | Float32 | R | Float32 value (var)
| 185CH | 6236 | 3 | Exported Reactive Power Demand 3 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 185FH | 6239 | 2 | Exported Reactive Power Demand 4 Peak | var | Float32 | R | Float32 value (var)
| 1861H | 6241 | 3 | Exported Reactive Power Demand 4 Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1864H | 6244 | 2 | Total Apparent Power Demand Peak | VA | Float32 | R | Float32 value (VA)
| 1866H | 6246 | 3 | Total Apparent Power Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1869H | 6249 | 2 | Phase A Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 186BH | 6251 | 3 | Phase A Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 186EH | 6254 | 2 | Phase B Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 1870H | 6256 | 3 | Phase B Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes
| 1873H | 6259 | 2 | Phase C Current Demand Peak | A | Float32 | R | Xx.xxxx A
| 1875H | 6261 | 3 | Phase C Current Demand Peak Happening Time | Date/time | 6 bytes | R | YY/MM/DD/hh/mm + byte 6 6 binary bytes

## Dual Source Energy
AcuRev 1310 ¦ Dual Source Energy
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Dual Source Energy Data (0x03 Read, 0x10 Write) | 3200H | 12800 | 2 | Grid Active Energy | Wh | Dword | R/W | 0~999999999
| 3202H | 12802 | 2 | Alternate Active Energy | Wh | Dword | R/W | 0~999999999
| 3204H | 12804 | 2 | Grid Reactive Energy | varh | Dword | R/W | 0~999999999
| 3206H | 12806 | 2 | Alternate Reactive Energy | varh | Dword | R/W | 0~999999999
| 3208H | 12808 | 2 | Grid Apparent Energy | VAh | Dword | R/W | 0~999999999
| 320AH | 12810 | 2 | Alternate Apparent Energy | VAh | Dword | R/W | 0~999999999
Dual Source Energy Parameter (0x03 Read, 0x10 Write) | 3000H | 12288 | 1 | Enable | No unit | Word | R/W | 0: Disable 1: Enable
| 3001H | 12289 | 1 | Energy source | No unit | Word | R/W | 0: From Grid 1: From alternative source
Dual Source Energy Command (0x10 Write) | 3100H | 12544 | 1 | Clear dual-source energy | No unit | Word | W | 0x0A: Valid
| 3101H | 12545 | 1 | Clear Dual-source change log | No unit | Word | W | 0x0A: Valid
Dual Source Change Log (0x03 Read) | 3300H | 13056 | 3 | Source Change Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss Binary bytes; meter clock
| 3303H | 13059 | 1 | Source Change Direction | No unit | Word | R | 0: To Grid 1: To Alternative source
| 3304H | 13060 | 2 | Grid Active Energy at Source Change | Wh | Dword | R
| 3306H | 13062 | 2 | Alternate Active Energy at Source Change | Wh | Dword | R
| 3308H | 13064 | 2 | Grid Reactive Energy at Source Change | varh | Dword | R
| 330AH | 13066 | 2 | Alternate Reactive Energy at Source Change | varh | Dword | R
| 330CH | 13068 | 2 | Grid Apparent Energy at Source Change | VAh | Dword | R
| 330EH | 13070 | 2 | Alternate Apparent Energy at Source Change | VAh | Dword | R
| 3310H | 13072 | 16 | Last 2nd change log (same as above) | Mixed | Record (32 bytes) | R
| 3320H | 13088 | 16 | Last 3rd change log (same as above) | Mixed | Record (32 bytes) | R

## Max Min
AcuRev 1310 ¦ Max Min
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Max (0x03 Read) | 4000H | 16384 | 2 | Total Current | A | Float32 | R
| 4002H | 16386 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4005H | 16389 | 2 | Phase A Current | A | Float32 | R
| 4007H | 16391 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 400AH | 16394 | 2 | Phase B Current | A | Float32 | R
| 400CH | 16396 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 400FH | 16399 | 2 | Phase C Current | A | Float32 | R
| 4011H | 16401 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4014H | 16404 | 2 | Average Phase Voltage | V | Float32 | R
| 4016H | 16406 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4019H | 16409 | 2 | Phase A Voltage | V | Float32 | R
| 401BH | 16411 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 401EH | 16414 | 2 | Phase B Voltage | V | Float32 | R
| 4020H | 16416 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4023H | 16419 | 2 | Phase C Voltage | V | Float32 | R
| 4025H | 16421 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4028H | 16424 | 2 | Average Line Voltage | V | Float32 | R
| 402AH | 16426 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 402DH | 16429 | 2 | Line AB Voltage | V | Float32 | R
| 402FH | 16431 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4032H | 16434 | 2 | Line BC Voltage | V | Float32 | R
| 4034H | 16436 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4037H | 16439 | 2 | Line CA Voltage | V | Float32 | R
| 4039H | 16441 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 403CH | 16444 | 2 | Frequency | Hz | Float32 | R
| 403EH | 16446 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4041H | 16449 | 2 | Total Active Power | W | Float32 | R
| 4043H | 16451 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4046H | 16454 | 2 | Phase A Active Power | W | Float32 | R
| 4048H | 16456 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 404BH | 16459 | 2 | Phase B Active Power | W | Float32 | R
| 404DH | 16461 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4050H | 16464 | 2 | Phase C Active Power | W | Float32 | R
| 4052H | 16466 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4055H | 16469 | 2 | Total Apparent Power | VA | Float32 | R
| 4057H | 16471 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 405AH | 16474 | 2 | Phase A Apparent Power | VA | Float32 | R
| 405CH | 16476 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 405FH | 16479 | 2 | Phase B Apparent Power | VA | Float32 | R
| 4061H | 16481 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4064H | 16484 | 2 | Phase C Apparent Power | VA | Float32 | R
| 4066H | 16486 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4069H | 16489 | 2 | Total Reactive Power | var | Float32 | R
| 406BH | 16491 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 406EH | 16494 | 2 | Phase A Reactive Power | var | Float32 | R
| 4070H | 16496 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4073H | 16499 | 2 | Phase B Reactive Power | var | Float32 | R
| 4075H | 16501 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4078H | 16504 | 2 | Phase C Reactive Power | var | Float32 | R
| 407AH | 16506 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
Min (0x03 Read) | 4100H | 16640 | 2 | Total Current | A | Float32 | R
| 4102H | 16642 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4105H | 16645 | 2 | Phase A Current | A | Float32 | R
| 4107H | 16647 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 410AH | 16650 | 2 | Phase B Current | A | Float32 | R
| 410CH | 16652 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 410FH | 16655 | 2 | Phase C Current | A | Float32 | R
| 4111H | 16657 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4114H | 16660 | 2 | Average Phase Voltage | V | Float32 | R
| 4116H | 16662 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4119H | 16665 | 2 | Phase A Voltage | V | Float32 | R
| 411BH | 16667 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 411EH | 16670 | 2 | Phase B Voltage | V | Float32 | R
| 4120H | 16672 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4123H | 16675 | 2 | Phase C Voltage | V | Float32 | R
| 4125H | 16677 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4128H | 16680 | 2 | Average Line Voltage | V | Float32 | R
| 412AH | 16682 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 412DH | 16685 | 2 | Line AB Voltage | V | Float32 | R
| 412FH | 16687 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4132H | 16690 | 2 | Line BC Voltage | V | Float32 | R
| 4134H | 16692 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4137H | 16695 | 2 | Line CA Voltage | V | Float32 | R
| 4139H | 16697 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 413CH | 16700 | 2 | Frequency | Hz | Float32 | R
| 413EH | 16702 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4141H | 16705 | 2 | Total Active Power | W | Float32 | R
| 4143H | 16707 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4146H | 16710 | 2 | Phase A Active Power | W | Float32 | R
| 4148H | 16712 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 414BH | 16715 | 2 | Phase B Active Power | W | Float32 | R
| 414DH | 16717 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4150H | 16720 | 2 | Phase C Active Power | W | Float32 | R
| 4152H | 16722 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4155H | 16725 | 2 | Total Apparent Power | VA | Float32 | R
| 4157H | 16727 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 415AH | 16730 | 2 | Phase A Apparent Power | VA | Float32 | R
| 415CH | 16732 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 415FH | 16735 | 2 | Phase B Apparent Power | VA | Float32 | R
| 4161H | 16737 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4164H | 16740 | 2 | Phase C Apparent Power | VA | Float32 | R
| 4166H | 16742 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4169H | 16745 | 2 | Total Reactive Power | var | Float32 | R
| 416BH | 16747 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 416EH | 16750 | 2 | Phase A Reactive Power | var | Float32 | R
| 4170H | 16752 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4173H | 16755 | 2 | Phase B Reactive Power | var | Float32 | R
| 4175H | 16757 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 4178H | 16760 | 2 | Phase C Reactive Power | var | Float32 | R
| 417AH | 16762 | 3 | Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes

## Reset Event & Unseal Record
AcuRev 1310 ¦ Reset Event & Unseal Record
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Demand Reset Event (0x03 Read) | 1B00H | 6912 | 2 | Demand Reset Count | Count | UInt32 | R | 0~0xFFFFFFFF
| 1B02H | 6914 | 3 | Latest Demand Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1B05H | 6917 | 3 | Previous Demand Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1B08H | 6920 | 3 | Third Most Recent Demand Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
Meter Unseal Record (0x03 Read) | 1C00H | 7168 | 2 | Meter Unseal Count | Count | UInt32 | R | 0~0xFFFFFFFF
| 1C02H | 7170 | 3 | Latest Meter Unseal Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1C05H | 7173 | 3 | Latest Meter Reseal Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1C08H | 7176 | 6 | Previous Unseal / Reseal Record | Mixed | Record (12 bytes) | R | Unseal time (6 bytes) Reseal time (6 bytes)
| 1C0EH | 7182 | 6 | Third Most Recent Unseal / Reseal Record | Mixed | Record (12 bytes) | R | Unseal time (6 bytes) Reseal time (6 bytes)
Event Reset (0x03 Read) | 1D00H | 7424 | 2 | Event Reset Count | Count | UInt32 | R | 0~0xFFFFFFFF
| 1D02H | 7426 | 3 | Latest Event Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1D05H | 7429 | 1 | Latest Event Reset Code | No unit | UInt16 | R | 1: Reset Event Record; 2: Reset Demand Record; 3: Reset Meter Opening Record; 4: Reset Alarm; 5: Reset Meter Operation Time; 6: Reset Time of Meter Operation with Load;
| 1D06H | 7430 | 4 | Previous Event Reset Record | Mixed | Record (8 bytes) | R | Time (6 bytes) Reset code (UInt16)
| 1D0AH | 7434 | 4 | Third Most Recent Event Reset Record | Mixed | Record (8 bytes) | R | Time (6 bytes) Reset code (UInt16)
Meter Reset (0x03 Read) | 1E00H | 7680 | 2 | Meter Reset Count | Count | UInt32 | R | 0~0xFFFFFFFF
| 1E02H | 7682 | 3 | Latest Meter Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1E05H | 7685 | 3 | Previous Meter Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes
| 1E08H | 7688 | 3 | Third Most Recent Meter Reset Timestamp | Date/time | 6 bytes | R | YY/MM/DD/hh/mm/ss 6 binary bytes

## Meter Status
AcuRev 1310 ¦ Meter Status
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
Meter Status (0x03 Read) | 0100H | 256 | 1 | The Result of Wiring Check | No unit | Word | R | Refer to “The Result of Wiring Check”
| 0101H | 257 | 1 | Seals status | No unit | Word | R | 0x0A: Seal sealed Others: Seal opened
| 0102H | 258 | 14 | Reserved | — | Word | R

## SunSpec
AcuRev 1310 ¦ SunSpec
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
SunSpec System Information (0x03 Read, 0x10 Write) | 1000H | 4096 | 2 | SunSpec Identifier | No unit | UInt32 | R | 0x53756E53 (ASCII: SunS)
| 1002H | 4098 | 1 | Common Model ID | No unit | UInt16 | R | 1
| 1003H | 4099 | 1 | Common Model Length | No unit | UInt16 | R | 65
| 1004H | 4100 | 16 | Manufacturer | No unit | String | R | Well known value registered with SunSpec for compliance
| 1014H | 4116 | 16 | Model | No unit | String | R | Manufacturer specific value (32 chars)
| 1024H | 4132 | 8 | Options | No unit | String | R | Manufacturer specific value (16 chars)
| 102CH | 4140 | 8 | Version | No unit | String | R | Manufacturer specific value (16 chars)
| 1034H | 4148 | 16 | Serial Number | No unit | String | R | Manufacturer specific value (32 chars)
| 1044H | 4164 | 1 | Modbus Device Address | No unit | UInt16 | R/W | Modbus device address
SunSpec Measured Data (0x03 Read, 0x10 Write) | 1045H | 4165 | 1 | Meter Model ID | No unit | UInt16 | R | 201: Single phase; 202: Split phase 203: Three-phase wye; 204: Delta
| 1046H | 4166 | 1 | Meter Model Length | No unit | UInt16 | R | 105
| 1047H | 4167 | 1 | Total Current | A | Int16 | R | 0~9999 A SF: 104BH
| 1048H | 4168 | 1 | Phase A Current | A | Int16 | R | 0~9999 A SF: 104BH
| 1049H | 4169 | 1 | Phase B Current | A | Int16 | R | 0~9999 A SF: 104BH
| 104AH | 4170 | 1 | Phase C Current | A | Int16 | R | 0~9999 A SF: 104BH
| 104BH | 4171 | 1 | Current Scale Factor | No unit | Int16 | R | −3 to +5 (signed exponent) Applies to 1047H–104AH
| 104CH | 4172 | 1 | Average Phase Voltage (L-N) | V | Int16 | R | 0~9999 V SF: 1054H
| 104DH | 4173 | 1 | Phase A Voltage (A-N) | V | Int16 | R | 0~9999 V SF: 1054H
| 104EH | 4174 | 1 | Phase B Voltage (B-N) | V | Int16 | R | 0~9999 V SF: 1054H
| 104FH | 4175 | 1 | Phase C Voltage (C-N) | V | Int16 | R | 0~9999 V SF: 1054H
| 1050H | 4176 | 1 | Average Line Voltage (L-L) | V | Int16 | R | 0~9999 V SF: 1054H
| 1051H | 4177 | 1 | Line Voltage AB | V | Int16 | R | 0~9999 V SF: 1054H
| 1052H | 4178 | 1 | Line Voltage BC | V | Int16 | R | 0~9999 V SF: 1054H
| 1053H | 4179 | 1 | Line Voltage CA | V | Int16 | R | 0~9999 V SF: 1054H
| 1054H | 4180 | 1 | Voltage Scale Factor | No unit | Int16 | R | -2~2 Applies to 104CH–1053H
| 1055H | 4181 | 1 | Frequency | Hz | Int16 | R | 45–65 Hz SF: 1056H
| 1056H | 4182 | 1 | Frequency Scale Factor | No unit | Int16 | R | -2 Applies to 1055H–1055H
| 1057H | 4183 | 1 | Total Active Power | W | Int16 | R | Signed value (import/export) SF: 105BH
| 1058H | 4184 | 1 | Phase A Active Power | W | Int16 | R | Signed value (import/export) SF: 105BH
| 1059H | 4185 | 1 | Phase B Active Power | W | Int16 | R | Signed value (import/export) SF: 105BH
| 105AH | 4186 | 1 | Phase C Active Power | W | Int16 | R | Signed value (import/export) SF: 105BH
| 105BH | 4187 | 1 | Active Power Scale Factor | No unit | Int16 | R | -1~ 4 Applies to 1057H–105AH
| 105CH | 4188 | 1 | Total Apparent Power | VA | Int16 | R | 0~9999 VA SF: 1060H
| 105DH | 4189 | 1 | Phase A Apparent Power | VA | Int16 | R | 0~9999 VA SF: 1060H
| 105EH | 4190 | 1 | Phase B Apparent Power | VA | Int16 | R | 0~9999 VA SF: 1060H
| 105FH | 4191 | 1 | Phase C Apparent Power | VA | Int16 | R | 0~9999 VA SF: 1060H
| 1060H | 4192 | 1 | Apparent Power Scale Factor | No unit | Int16 | R | -1 ~ 4 Applies to 105CH–105FH
| 1061H | 4193 | 1 | Total Reactive Power | var | Int16 | R | Signed value (import/export) SF: 1065H
| 1062H | 4194 | 1 | Phase A Reactive Power | var | Int16 | R | Signed value (import/export) SF: 1065H
| 1063H | 4195 | 1 | Phase B Reactive Power | var | Int16 | R | Signed value (import/export) SF: 1065H
| 1064H | 4196 | 1 | Phase C Reactive Power | var | Int16 | R | Signed value (import/export) SF: 1065H
| 1065H | 4197 | 1 | Reactive Power Scale Factor | No unit | Int16 | R | -1 ~ 4 Applies to 1061H–1064H
| 1066H | 4198 | 1 | Total Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: 106AH
| 1067H | 4199 | 1 | Phase A Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: 106AH
| 1068H | 4200 | 1 | Phase B Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: 106AH
| 1069H | 4201 | 1 | Phase C Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: 106AH
| 106AH | 4202 | 1 | Power Factor Scale Factor | No unit | Int16 | R | -3 Applies to 1066H–1069H
| 106BH | 4203 | 2 | Total Active Energy Exported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 106DH | 4205 | 2 | Phase A Active Energy Exported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 106FH | 4207 | 2 | Phase B Active Energy Exported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 1071H | 4209 | 2 | Phase C Active Energy Exported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 1073H | 4211 | 2 | Total Active Energy Imported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 1075H | 4213 | 2 | Phase A Active Energy Imported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 1077H | 4215 | 2 | Phase B Active Energy Imported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 1079H | 4217 | 2 | Phase C Active Energy Imported | kWh | UInt32 | R/W | 0-999999999 kWh SF: 107BH
| 107BH | 4219 | 1 | Active Energy Scale Factor | No unit | Int16 | R | -3 ~ 0 Applies to 106BH–107AH
| 107CH | 4220 | 2 | Total Apparent Energy Exported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 107EH | 4222 | 2 | Phase A Apparent Energy Exported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 1080H | 4224 | 2 | Phase B Apparent Energy Exported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 1082H | 4226 | 2 | Phase C Apparent Energy Exported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 1084H | 4228 | 2 | Total Apparent Energy Imported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 1086H | 4230 | 2 | Phase A Apparent Energy Imported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 1088H | 4232 | 2 | Phase B Apparent Energy Imported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 108AH | 4234 | 2 | Phase C Apparent Energy Imported | kVAh | UInt32 | R/W | 0-999999999 kVah SF: 108CH
| 108CH | 4236 | 1 | Apparent Energy Scale Factor | No unit | Int16 | R | -3 ~ 0 Applies to 107CH–108BH
| 108DH | 4237 | 2 | Total Reactive Energy Imported Q1 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 108FH | 4239 | 2 | Phase A Reactive Energy Imported Q1 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 1091H | 4241 | 2 | Phase B Reactive Energy Imported Q1 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 1093H | 4243 | 2 | Phase C Reactive Energy Imported Q1 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 1095H | 4245 | 2 | Total Reactive Energy Imported Q2 | kvarh | UInt32 | R/W | 0-999999999k varh SF: 10ADH
| 1097H | 4247 | 2 | Phase A Reactive Energy Imported Q2 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 1099H | 4249 | 2 | Phase B Reactive Energy Imported Q2 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 109BH | 4251 | 2 | Phase C Reactive Energy Imported Q2 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 109DH | 4253 | 2 | Total Reactive Energy Exported Q3 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 109FH | 4255 | 2 | Phase A Reactive Energy Exported Q3 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10A1H | 4257 | 2 | Phase B Reactive Energy Exported Q3 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10A3H | 4259 | 2 | Phase C Reactive Energy Exported Q3 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10A5H | 4261 | 2 | Total Reactive Energy Exported Q4 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10A7H | 4263 | 2 | Phase A Reactive Energy Exported Q4 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10A9H | 4265 | 2 | Phase B Reactive Energy Exported Q4 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10ABH | 4267 | 2 | Phase C Reactive Energy Exported Q4 | kvarh | UInt32 | R/W | 0-999999999 kvarh SF: 10ADH
| 10ADH | 4269 | 1 | Reactive Energy Scale Factor | No unit | Int16 | R | Use this SF for reactive energy 108DH–10ACH
| 10AEH | 4270 | 2 | Meter Event Flags | No unit | bitfield32 | R | See Data Types — Meter Event Flags
| 10B0H | 4272 | 1 | End Model ID | No unit | UInt16 | R | 0xFFFF
| 10B1H | 4273 | 1 | End Model Length | No unit | UInt16 | R | 0x0000

## New SunSpec
AcuRev 1310 ¦ New SunSpec
Block / Function | Start Address (Hex) | Start Address (Dec) | Registers | Parameter | Units | Data Type | Permissions | Range
SunSpec System Information (0x03 Read, 0x10 Write) | C350H | 50000 | 2 | SunSpec Identifier | No unit | UInt32 | R | 0x53756E53 (ASCII: SunS)
| C352H | 50002 | 1 | Common Model ID | No unit | UInt16 | R | 1
| C353H | 50003 | 1 | Common Model Length | No unit | UInt16 | R | 65
| C354H | 50004 | 16 | Manufacturer | No unit | String | R | Well known value registered with SunSpec for compliance
| C364H | 50020 | 16 | Model | No unit | String | R | Manufacturer specific value (32 chars)
| C374H | 50036 | 8 | Options | No unit | String | R | Manufacturer specific value (16 chars)
| C37CH | 50044 | 8 | Version | No unit | String | R | Manufacturer specific value (16 chars)
| C384H | 50052 | 16 | Serial Number | No unit | String | R | Manufacturer specific value (32 chars)
| C394H | 50068 | 1 | Modbus Device Address | No unit | UInt16 | R/W | Modbus device address
SunSpec Measured Data (0x03 Read, 0x10 Write) | C395H | 50069 | 1 | Meter Model ID | No unit | UInt16 | R | 201: Single phase; 202: Split phase 203: Three-phase wye; 204: Delta
| C396H | 50070 | 1 | Meter Model Length | No unit | UInt16 | R | 105
| C397H | 50071 | 1 | Total Current | A | Int16 | R | 0~9999 A SF: C39BH
| C398H | 50072 | 1 | Phase A Current | A | Int16 | R | 0~9999 A SF: C39BH
| C399H | 50073 | 1 | Phase B Current | A | Int16 | R | 0~9999 A SF: C39BH
| C39AH | 50074 | 1 | Phase C Current | A | Int16 | R | 0~9999 A SF: C39BH
| C39BH | 50075 | 1 | Current Scale Factor | No unit | Int16 | R | −3 to +5 (signed exponent) Applies to C397H–C39AH
| C39CH | 50076 | 1 | Average Phase Voltage (L-N) | V | Int16 | R | 0~9999 V SF: C3A4H
| C39DH | 50077 | 1 | Phase A Voltage (A-N) | V | Int16 | R | 0~9999 V SF: C3A4H
| C39EH | 50078 | 1 | Phase B Voltage (B-N) | V | Int16 | R | 0~9999 V SF: C3A4H
| C39FH | 50079 | 1 | Phase C Voltage (C-N) | V | Int16 | R | 0~9999 V SF: C3A4H
| C3A0H | 50080 | 1 | Average Line Voltage (L-L) | V | Int16 | R | 0~9999 V SF: C3A4H
| C3A1H | 50081 | 1 | Line Voltage AB | V | Int16 | R | 0~9999 V SF: C3A4H
| C3A2H | 50082 | 1 | Line Voltage BC | V | Int16 | R | 0~9999 V SF: C3A4H
| C3A3H | 50083 | 1 | Line Voltage CA | V | Int16 | R | 0~9999 V SF: C3A4H
| C3A4H | 50084 | 1 | Voltage Scale Factor | No unit | Int16 | R | -2~2 Applies to C39CH–C3A3H
| C3A5H | 50085 | 1 | Frequency | Hz | Int16 | R | 45–65 Hz SF: C3A6H
| C3A6H | 50086 | 1 | Frequency Scale Factor | No unit | Int16 | R | -2 Applies to C3A5H–C3A5H
| C3A7H | 50087 | 1 | Total Active Power | W | Int16 | R | Signed value (import/export) SF: C3ABH
| C3A8H | 50088 | 1 | Phase A Active Power | W | Int16 | R | Signed value (import/export) SF: C3ABH
| C3A9H | 50089 | 1 | Phase B Active Power | W | Int16 | R | Signed value (import/export) SF: C3ABH
| C3AAH | 50090 | 1 | Phase C Active Power | W | Int16 | R | Signed value (import/export) SF: C3ABH
| C3ABH | 50091 | 1 | Active Power Scale Factor | No unit | Int16 | R | -1~ 4 Applies to C3A7H–C3AAH
| C3ACH | 50092 | 1 | Total Apparent Power | VA | Int16 | R | 0~9999 VA SF: C3B0H
| C3ADH | 50093 | 1 | Phase A Apparent Power | VA | Int16 | R | 0~9999 VA SF: C3B0H
| C3AEH | 50094 | 1 | Phase B Apparent Power | VA | Int16 | R | 0~9999 VA SF: C3B0H
| C3AFH | 50095 | 1 | Phase C Apparent Power | VA | Int16 | R | 0~9999 VA SF: C3B0H
| C3B0H | 50096 | 1 | Apparent Power Scale Factor | No unit | Int16 | R | -1 ~ 4 Applies to C3ACH–C3AFH
| C3B1H | 50097 | 1 | Total Reactive Power | var | Int16 | R | Signed value (import/export) SF: C3B5H
| C3B2H | 50098 | 1 | Phase A Reactive Power | var | Int16 | R | Signed value (import/export) SF: C3B5H
| C3B3H | 50099 | 1 | Phase B Reactive Power | var | Int16 | R | Signed value (import/export) SF: C3B5H
| C3B4H | 50100 | 1 | Phase C Reactive Power | var | Int16 | R | Signed value (import/export) SF: C3B5H
| C3B5H | 50101 | 1 | Reactive Power Scale Factor | No unit | Int16 | R | -1 ~ 4 Applies to C3B1H–C3B4H
| C3B6H | 50102 | 1 | Total Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: C3BAH
| C3B7H | 50103 | 1 | Phase A Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: C3BAH
| C3B8H | 50104 | 1 | Phase B Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: C3BAH
| C3B9H | 50105 | 1 | Phase C Power Factor | No unit | Int16 | R | −1 to +1 after scaling (ratio) SF: C3BAH
| C3BAH | 50106 | 1 | Power Factor Scale Factor | No unit | Int16 | R | -3 Applies to C3B6H–C3B9H
| C3BBH | 50107 | 2 | Total Active Energy Exported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3BDH | 50109 | 2 | Phase A Active Energy Exported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3BFH | 50111 | 2 | Phase B Active Energy Exported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3C1H | 50113 | 2 | Phase C Active Energy Exported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3C3H | 50115 | 2 | Total Active Energy Imported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3C5H | 50117 | 2 | Phase A Active Energy Imported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3C7H | 50119 | 2 | Phase B Active Energy Imported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3C9H | 50121 | 2 | Phase C Active Energy Imported | Wh | UInt32 | R/W | 0-999999999 Wh SF: C3CBH
| C3CBH | 50123 | 1 | Active Energy Scale Factor | No unit | Int16 | R | 0 ~ 3 Applies to C3BBH–C3CAH
| C3CCH | 50124 | 2 | Total Apparent Energy Exported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3CEH | 50126 | 2 | Phase A Apparent Energy Exported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3D0H | 50128 | 2 | Phase B Apparent Energy Exported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3D2H | 50130 | 2 | Phase C Apparent Energy Exported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3D4H | 50132 | 2 | Total Apparent Energy Imported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3D6H | 50134 | 2 | Phase A Apparent Energy Imported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3D8H | 50136 | 2 | Phase B Apparent Energy Imported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3DAH | 50138 | 2 | Phase C Apparent Energy Imported | VAh | UInt32 | R/W | 0-999999999 Vah SF: C3DCH
| C3DCH | 50140 | 1 | Apparent Energy Scale Factor | No unit | Int16 | R | 0 ~3 Applies to C3CCH–C3DBH
| C3DDH | 50141 | 2 | Total Reactive Energy Imported Q1 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3DFH | 50143 | 2 | Phase A Reactive Energy Imported Q1 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3E1H | 50145 | 2 | Phase B Reactive Energy Imported Q1 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3E3H | 50147 | 2 | Phase C Reactive Energy Imported Q1 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3E5H | 50149 | 2 | Total Reactive Energy Imported Q2 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3E7H | 50151 | 2 | Phase A Reactive Energy Imported Q2 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3E9H | 50153 | 2 | Phase B Reactive Energy Imported Q2 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3EBH | 50155 | 2 | Phase C Reactive Energy Imported Q2 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3EDH | 50157 | 2 | Total Reactive Energy Exported Q3 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3EFH | 50159 | 2 | Phase A Reactive Energy Exported Q3 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3F1H | 50161 | 2 | Phase B Reactive Energy Exported Q3 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3F3H | 50163 | 2 | Phase C Reactive Energy Exported Q3 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3F5H | 50165 | 2 | Total Reactive Energy Exported Q4 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3F7H | 50167 | 2 | Phase A Reactive Energy Exported Q4 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3F9H | 50169 | 2 | Phase B Reactive Energy Exported Q4 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3FBH | 50171 | 2 | Phase C Reactive Energy Exported Q4 | varh | UInt32 | R/W | 0-999999999 varh SF: C3FDH
| C3FDH | 50173 | 1 | Reactive Energy Scale Factor | No unit | Int16 | R | Use this SF for reactive energy C3DDH–C3FCH
| C3FEH | 50174 | 2 | Meter Event Flags | No unit | bitfield32 | R | See Data Types — Meter Event Flags
| C400H | 50176 | 1 | End Model ID | No unit | UInt16 | R | 0xFFFF
| C401H | 50177 | 1 | End Model Length | No unit | UInt16 | R | 0x0000