## AcuRev1320
BACnet Points List AcuRev1320
Firmware v1.01p21. List generated 2026-10-10 from firmware source. BACnet/IP and BACnet MS/TP expose the same objects.
ID | Name | Description | Object Type | Data type | RW | Unit
RealTime
1 | Freq_rms | System Frequency | Object Analog Input | float | R | Hertz
2 | Ua_rms | Phase A Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
3 | Ub_rms | Phase B Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
4 | Uc_rms | Phase C Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
5 | Uavg_rms | Average Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
6 | Uab_rms | Phase AB Line-to-Line Voltage | Object Analog Input | float | R | Volts
7 | Ubc_rms | Phase BC Line-to-Line Voltage | Object Analog Input | float | R | Volts
8 | Uca_rms | Phase CA Line-to-Line Voltage | Object Analog Input | float | R | Volts
9 | Ulavg_rms | Average Line-to-Line Voltage | Object Analog Input | float | R | Volts
10 | Ia_rms | Phase A Current | Object Analog Input | float | R | Amperes
11 | Ib_rms | Phase B Current | Object Analog Input | float | R | Amperes
12 | Ic_rms | Phase C Current | Object Analog Input | float | R | Amperes
13 | Iavg_rms | Average Current | Object Analog Input | float | R | Amperes
14 | In_rms | Phase N Current | Object Analog Input | float | R | Amperes
15 | Pa_rms | Phase A Active Power | Object Analog Input | float | R | Kilowatts
16 | Pb_rms | Phase B Active Power | Object Analog Input | float | R | Kilowatts
17 | Pc_rms | Phase C Active Power | Object Analog Input | float | R | Kilowatts
18 | P_rms | System Active Power | Object Analog Input | float | R | Kilowatts
19 | Qa_rms | Phase A Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
20 | Qb_rms | Phase B Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
21 | Qc_rms | Phase C Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
22 | Q_rms | System Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
23 | Sa_rms | Phase A Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
24 | Sb_rms | Phase B Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
25 | Sc_rms | Phase C Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
26 | S_rms | System Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
Power Quality
27 | PFa_rms | Phase A Power Factor | Object Analog Input | float | R | Power Factor
28 | PFb_rms | Phase B Power Factor | Object Analog Input | float | R | Power Factor
29 | PFc_rms | Phase C Power Factor | Object Analog Input | float | R | Power Factor
30 | PF_rms | System Power Factor | Object Analog Input | float | R | Power Factor
31 | U_unbl | Voltage Unbalance Negative | Object Analog Input | float | R | Percent
32 | I_unbl | Current Unbalance Negative | Object Analog Input | float | R | Percent
33 | Rlc_val | System Load Nature(82:Resistive load 76:Inductive load 67:Capacitive load) | Object Analog Input | float | R | No Units
34 | V1_thd | Phase A Voltage THD | Object Analog Input | float | R | Percent
35 | V2_thd | Phase B Voltage THD | Object Analog Input | float | R | Percent
36 | V3_thd | Phase C Voltage THD | Object Analog Input | float | R | Percent
37 | I1_thd | Phase A Current THD | Object Analog Input | float | R | Percent
38 | I2_thd | Phase B Current THD | Object Analog Input | float | R | Percent
39 | I3_thd | Phase C Current THD | Object Analog Input | float | R | Percent
Demand
40 | p_dema | System Active Power Demand | Object Analog Input | float | R | Kilowatts
41 | q_dema | System Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
42 | s_dema | System Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
43 | Ia_dema | Phase A Current Demand | Object Analog Input | float | R | Amperes
44 | Ib_dema | Phase B Current Demand | Object Analog Input | float | R | Amperes
45 | Ic_dema | Phase C Current Demand | Object Analog Input | float | R | Amperes
Independent Input Channel
46 | I4_rms | Channel 4 Current | Object Analog Input | float | R | Amperes
47 | P4_rms | Channel 4 Active Power | Object Analog Input | float | R | Kilowatts
48 | Q4_rms | Channel 4 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
49 | S4_rms | Channel 4 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
50 | PF4_rms | Channel 4 Power Factor | Object Analog Input | float | R | Power Factor
51 | I4_thd | Channel 4 Current THD | Object Analog Input | float | R | Percent
52 | I4_dema | Channel 4 Current Demand | Object Analog Input | float | R | Amperes
53 | Isum2_avg_rms | Summation 2 Average Current | Object Analog Input | float | R | Amperes
54 | Psum2_rms | Summation 2 Active Power | Object Analog Input | float | R | Kilowatts
55 | Qsum2_rms | Summation 2 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
56 | Ssum2_rms | Summation 2 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
57 | PFsum2_rms | Summation 2 Power Factor | Object Analog Input | float | R | Power Factor
58 | Rlc_sum2_val | Summation 2 Load Nature(82:Resistive load 76:Inductive load 67:Capacitive load) | Object Analog Input | float | R | No Units
59 | Psum2_dema | Summation 2 Active Power Demand | Object Analog Input | float | R | Kilowatts
60 | Qsum2_dema | Summation 2 Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
61 | Ssum2_dema | Summation 2 Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
Energy
1 | Active_Energy_Imp | System active energy import | Object Large Analog Value | double | R | Kilowatt Hours
2 | Active_Energy_Exp | System active energy export | Object Large Analog Value | double | R | Kilowatt Hours
3 | Reactive_Energy_Imp | System reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
4 | Reactive_Energy_Exp | System reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
5 | Active_Energy_Total | System active energy total | Object Large Analog Value | double | R | Kilowatt Hours
6 | Active_Energy_Net | System active energy net | Object Large Analog Value | double | R | Kilowatt Hours
7 | Reactive_Energy_Total | System reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
8 | Reactive_Energy_Net | System reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
9 | Apparent_Energy | System apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
10 | Active_Energy_Imp_A | Phase A active energy import | Object Large Analog Value | double | R | Kilowatt Hours
11 | Active_Energy_Exp_A | Phase A active energy export | Object Large Analog Value | double | R | Kilowatt Hours
12 | Active_Energy_Imp_B | Phase B active energy import | Object Large Analog Value | double | R | Kilowatt Hours
13 | Active_Energy_Exp_B | Phase B active energy export | Object Large Analog Value | double | R | Kilowatt Hours
14 | Active_Energy_Imp_C | Phase C active energy import | Object Large Analog Value | double | R | Kilowatt Hours
15 | Active_Energy_Exp_C | Phase C active energy export | Object Large Analog Value | double | R | Kilowatt Hours
16 | Reactive_Energy_Imp_A | Phase A reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
17 | Reactive_Energy_Exp_A | Phase A reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
18 | Reactive_Energy_Imp_B | Phase B reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
19 | Reactive_Energy_Exp_B | Phase B reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
20 | Reactive_Energy_Imp_C | Phase C reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
21 | Reactive_Energy_Exp_C | Phase C reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
22 | Apparent_Energy_A | Phase A apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
23 | Apparent_Energy_B | Phase B apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
24 | Apparent_Energy_C | Phase C apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
25 | CH4_Active_Energy_Imp | Channel 4 active energy import | Object Large Analog Value | double | R | Kilowatt Hours
26 | CH4_Active_Energy_Exp | Channel 4 active energy export | Object Large Analog Value | double | R | Kilowatt Hours
27 | CH4_Reactive_Energy_Imp | Channel 4 reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
28 | CH4_Reactive_Energy_Exp | Channel 4 reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
29 | CH4_Apparent_Energy_Total | Channel 4 apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
30 | Sum2_Active_Energy_Imp | Summation 2 active energy import | Object Large Analog Value | double | R | Kilowatt Hours
31 | Sum2_Active_Energy_Exp | Summation 2 active energy export | Object Large Analog Value | double | R | Kilowatt Hours
32 | Sum2_Reactive_Energy_Imp | Summation 2 reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
33 | Sum2_Reactive_Energy_Exp | Summation 2 reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
34 | Sum2_Active_Energy_Total | Summation 2 active energy total | Object Large Analog Value | double | R | Kilowatt Hours
35 | Sum2_Active_Energy_Net | Summation 2 active energy net | Object Large Analog Value | double | R | Kilowatt Hours
36 | Sum2_Reactive_Energy_Total | Summation 2 reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
37 | Sum2_Reactive_Energy_Net | Summation 2 reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
38 | Sum2_Apparent_Energy_Total | Summation 2 apparent energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours
IO-DI Pulse
1 | DI1_pc | DI1 pulse counter | Object Pulse Converter | uint32_t | R | No Units
2 | DI2_pc | DI2 pulse counter | Object Pulse Converter | uint32_t | R | No Units
3 | DI3_pc | DI3 pulse counter | Object Pulse Converter | uint32_t | R | No Units
IO-DI Status
1 | DI1_s | Digital Input 1 Status | Object Binary_Input | bool | R | No Units
2 | DI2_s | Digital Input 2 Status | Object Binary_Input | bool | R | No Units
3 | DI3_s | Digital Input 3 Status | Object Binary_Input | bool | R | No Units

## Note
Notes
Source:
AcuRev1320 firmware v1.01p21 Date :October 10, 2026 BACnet Protocol Version: 1 BACnet Protocol Revision: 26 Objects are defined by the parameter mapping and BACnet mapper tables in the firmware database (createParamDefault).
Object counts:
Analog Input: 61 objects (instances 1-61)
Large Analog Value: 38 objects (instances 1-38)
Object Pulse Converter : 3 objects (instances 1-3)
Object Binary_Input: 3 objects (instances 1-3)
Availability:
RealTime Objects( Start 1 -End 26 ),
Power Quality Objects (Start 27;End 39),
Demand Objects (Start 40;End 45),
Energy Objects( Start 1 -End 38),
Independent Input Channel Objects ( Start 46 -End 61 ),
IO-DI Pulse ( Start 1 -End 3 ),
IO-DI Status( Start 1 -End 3 )