## Demand Max Reset & Wire Check
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Demand Max Reset | 0x900 | 0x900 | 2304 | 2304 | Mode of demand max reset | Word | R/W | 1 | 0: Disable; 1: Auto; 2: Manual | 2
(0x03 Read, 0x10 Write) | 0x901 | 0x901 | 2305 | 2305 | Demand max reset counter | Word | R | 1 |  | 0
| 0x902 | 0x907 | 2306 | 2311 | Last demand max reset timestamp | Word | R | 6 | YY MM DD hh mm ss | 00 01 01 00 00 00
Wire Check | 0x910 | 0x910 | 2320 | 2320 | Wire check enable/disable | Word | R/W | 1 | 0: Disable; 1: Enable | 0
(0x03 Read, 0x10 Write) | 0x911 | 0x911 | 2321 | 2321 | Wire check update | Word | R/W | 1 | 0: No; 1: Yes | 0
| 0x912 | 0x912 | 2322 | 2322 | Voltage input A, B, C result | Word | R | 1 | Bit0 - Bit3: Va (missing, incorrect, reversal) Bit4 - Bit6: Vb (missing, incorrect, reversal) Bit8 - Bit10: Vc (missing, incorrect, reversal)
| 0x913 | 0x913 | 2323 | 2323 | Current input 1, 2, 3 result | Word | R | 1 | Bit0 - Bit3: I1 (missing, incorrect, reversal) Bit4 - Bit6: I2 (missing, incorrect, reversal) Bit8 - Bit10: I3 (missing, incorrect, reversal)
| 0x914 | 0x914 | 2324 | 2324 | Current input 4, 5, 6 result | Word | R | 1 | Bit0 - Bit3: I4 (missing, incorrect, reversal) Bit4 - Bit6: I5 (missing, incorrect, reversal) Bit8 - Bit10: I6 (missing, incorrect, reversal)
| 0x915 | 0x915 | 2325 | 2325 | Current input 7, 8, 9 result | Word | R | 1 | Bit0 - Bit3: I7 (missing, incorrect, reversal) Bit4 - Bit6: I8 (missing, incorrect, reversal) Bit8 - Bit10: I9 (missing, incorrect, reversal)
| 0x916 | 0x916 | 2326 | 2326 | Current input 10, 11, 12 result | Word | R | 1 | Bit0 - Bit3: I10 (missing, incorrect, reversal) Bit4 - Bit6: I11 (missing, incorrect, reversal) Bit8 - Bit10: I12 (missing, incorrect, reversal)
| 0x917 | 0x917 | 2327 | 2327 | Current input 13, 14, 15 result | Word | R | 1 | Bit0 - Bit3: I13 (missing, incorrect, reversal) Bit4 - Bit6: I14 (missing, incorrect, reversal) Bit8 - Bit10: I15 (missing, incorrect, reversal)
| 0x918 | 0x918 | 2328 | 2328 | Current input 16, 17, 18 result | Word | R | 1 | Bit0 - Bit3: I16 (missing, incorrect, reversal) Bit4 - Bit6: I17 (missing, incorrect, reversal) Bit8 - Bit10: I18 (missing, incorrect, reversal)

## Meter Run Time & Clock
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Device Run Time | 0x1050 | 0x1051 | 4176 | 4177 | Device Run Time | Dword | R | 2
(0x03 Read)
System Clock | 0x1054 | 0x1054 | 4180 | 4180 | Year | Word | R/W | 1 | 0~99
(0x03 Read, 0x10 Write) | 0x1055 | 0x1055 | 4181 | 4181 | Month | Word | R/W | 1 | 1~12
| 0x1056 | 0x1056 | 4182 | 4182 | Day | Word | R/W | 1 | 1~31
| 0x1057 | 0x1057 | 4183 | 4183 | Hour | Word | R/W | 1 | 0~23
| 0x1058 | 0x1058 | 4184 | 4184 | Minute | Word | R/W | 1 | 0~59
| 0x1059 | 0x1059 | 4185 | 4185 | Second | Word | R/W | 1 | 0~59
| 0x105A | 0x105A | 4186 | 4186 | Week | Word | R/W | 1 | 0~6, 0: Sunday

## Real-time Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Inline | 0x2000 | 0x2001 | 8192 | 8193 | Freq | Float | R | 2 | x.xx
(0x03 Read) | 0x2002 | 0x2003 | 8194 | 8195 | U1 | Float | R | 2 | x.x
| 0x2004 | 0x2005 | 8196 | 8197 | U2 | Float | R | 2 | x.x
| 0x2006 | 0x2007 | 8198 | 8199 | U3 | Float | R | 2 | x.x
| 0x2008 | 0x2009 | 8200 | 8201 | Uavg | Float | R | 2 | x.x
| 0x200A | 0x200B | 8202 | 8203 | U12 | Float | R | 2 | x.x
| 0x200C | 0x200D | 8204 | 8205 | U23 | Float | R | 2 | x.x
| 0x200E | 0x200F | 8206 | 8207 | U31 | Float | R | 2 | x.x
| 0x2010 | 0x2011 | 8208 | 8209 | Ulavg | Float | R | 2 | x.x
| 0x2012 | 0x2013 | 8210 | 8211 | IL1 | Float | R | 2 | x.xxx
| 0x2014 | 0x2015 | 8212 | 8213 | IL2 | Float | R | 2 | x.xxx
| 0x2016 | 0x2017 | 8214 | 8215 | IL3 | Float | R | 2 | x.xxx
| 0x2018 | 0x2019 | 8216 | 8217 | Iavg | Float | R | 2 | x.xxx
| 0x201A | 0x201B | 8218 | 8219 | Pin-s | Float | R | 2 | x.xxxx
| 0x201C | 0x201D | 8220 | 8221 | Qin-s | Float | R | 2 | x.xxxx
| 0x201E | 0x201F | 8222 | 8223 | Sin-s | Float | R | 2 | x.xxxx
| 0x2020 | 0x2021 | 8224 | 8225 | PFin-s | Float | R | 2 | x.xxx
| 0x2022 | 0x2023 | 8226 | 8227 | Load Nature S | Float | R | 2 | 1: R; 2: L; 3: C
| 0x2024 | 0x2025 | 8228 | 8229 | Pin-A | Float | R | 2 | x.xxxx
| 0x2026 | 0x2027 | 8230 | 8231 | Pin-B | Float | R | 2 | x.xxxx
| 0x2028 | 0x2029 | 8232 | 8233 | Pin-C | Float | R | 2 | x.xxxx
| 0x202A | 0x202B | 8234 | 8235 | Qin-A | Float | R | 2 | x.xxxx
| 0x202C | 0x202D | 8236 | 8237 | Qin-B | Float | R | 2 | x.xxxx
| 0x202E | 0x202F | 8238 | 8239 | Qin-C | Float | R | 2 | x.xxxx
| 0x2030 | 0x2031 | 8240 | 8241 | Sin-A | Float | R | 2 | x.xxxx
| 0x2032 | 0x2033 | 8242 | 8243 | Sin-B | Float | R | 2 | x.xxxx
| 0x2034 | 0x2035 | 8244 | 8245 | Sin-C | Float | R | 2 | x.xxxx
| 0x2036 | 0x2037 | 8246 | 8247 | PFin-A | Float | R | 2 | x.xxx
| 0x2038 | 0x2039 | 8248 | 8249 | PFin-B | Float | R | 2 | x.xxx
| 0x203A | 0x203B | 8250 | 8251 | PFin-C | Float | R | 2 | x.xxx
| 0x203C | 0x203D | 8252 | 8253 | Load Nature A | Float | R | 2 | 1: R; 2: L; 3: C
| 0x203E | 0x203F | 8254 | 8255 | Load Nature B | Float | R | 2 | 1: R; 2: L; 3: C
| 0x2040 | 0x2041 | 8256 | 8257 | Load Nature C | Float | R | 2 | 1: R; 2: L; 3: C
Individual/User Channel | 0x2100 | 0x2101 | 8448 | 8449 | I1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
(0x03 Read) | 0x2102 | 0x2103 | 8450 | 8451 | P1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2104 | 0x2105 | 8452 | 8453 | Q1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2106 | 0x2107 | 8454 | 8455 | S1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2108 | 0x2109 | 8456 | 8457 | PF1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x210A | 0x210B | 8458 | 8459 | Load Nature 1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x210C | 0x2117 | 8460 | 8471 | Individual channel 2 | Float | R | 12 | Same as in "Inline"
| 0x2118 | 0x2123 | 8472 | 8483 | Individual channel 3 | Float | R | 12 | Same as in "Inline"
| 0x2124 | 0x212F | 8484 | 8495 | Individual channel 4 | Float | R | 12 | Same as in "Inline"
| 0x2130 | 0x213B | 8496 | 8507 | Individual channel 5 | Float | R | 12 | Same as in "Inline"
| 0x213C | 0x2147 | 8508 | 8519 | Individual channel 6 | Float | R | 12 | Same as in "Inline"
| 0x2148 | 0x2153 | 8520 | 8531 | Individual channel 7 | Float | R | 12 | Same as in "Inline"
| 0x2154 | 0x215F | 8532 | 8543 | Individual channel 8 | Float | R | 12 | Same as in "Inline"
| 0x2160 | 0x216B | 8544 | 8555 | Individual channel 9 | Float | R | 12 | Same as in "Inline"
| 0x216C | 0x2177 | 8556 | 8567 | Individual channel 10 | Float | R | 12 | Same as in "Inline"
| 0x2178 | 0x2183 | 8568 | 8579 | Individual channel 11 | Float | R | 12 | Same as in "Inline"
| 0x2184 | 0x218F | 8580 | 8591 | Individual channel 12 | Float | R | 12 | Same as in "Inline"
| 0x2190 | 0x219B | 8592 | 8603 | Individual channel 13 | Float | R | 12 | Same as in "Inline"
| 0x219C | 0x21A7 | 8604 | 8615 | Individual channel 14 | Float | R | 12 | Same as in "Inline"
| 0x21A8 | 0x21B3 | 8616 | 8627 | Individual channel 15 | Float | R | 12 | Same as in "Inline"
| 0x21B4 | 0x21BF | 8628 | 8639 | Individual channel 16 | Float | R | 12 | Same as in "Inline"
| 0x21C0 | 0x21CB | 8640 | 8651 | Individual channel 17 | Float | R | 12 | Same as in "Inline"
| 0x21CC | 0x21D7 | 8652 | 8663 | Individual channel 18 | Float | R | 12 | Same as in "Inline"
| 0x21D8 | 0x21D9 | 8664 | 8665 | Ps1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DA | 0x21DB | 8666 | 8667 | Qs1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DC | 0x21DD | 8668 | 8669 | Ss1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DE | 0x21DF | 8670 | 8671 | PFs1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21E0 | 0x21E1 | 8672 | 8673 | Load Nature s1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21E2 | 0x21EB | 8674 | 8683 | User channel 2 | Float | R | 10 | Same as in "Inline"
| 0x21EC | 0x21F5 | 8684 | 8693 | User channel 3 | Float | R | 10 | Same as in "Inline"
| 0x21F6 | 0x21FF | 8694 | 8703 | User channel 4 | Float | R | 10 | Same as in "Inline"
| 0x2200 | 0x2209 | 8704 | 8713 | User channel 5 | Float | R | 10 | Same as in "Inline"
| 0x220A | 0x2213 | 8714 | 8723 | User channel 6 | Float | R | 10 | Same as in "Inline"
| 0x2214 | 0x221D | 8724 | 8733 | User channel 7 | Float | R | 10 | Same as in "Inline"
| 0x221E | 0x2227 | 8734 | 8743 | User channel 8 | Float | R | 10 | Same as in "Inline"
| 0x2228 | 0x2231 | 8744 | 8753 | User channel 9 | Float | R | 10 | Same as in "Inline"

## Active Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Import Active Energy | 0x2500 | 0x2501 | 9472 | 9473 | Epin-A import | Dword | R/W | 2 | Max 999999999 (99999999.9)
(0x03 Read, 0x10 Write) | 0x2502 | 0x2503 | 9474 | 9475 | Epin-B import | Dword | R/W | 2 | All same as above
| 0x2504 | 0x2505 | 9476 | 9477 | Epin-C import | Dword | R/W | 2
| 0x2506 | 0x2507 | 9478 | 9479 | Epin-S import | Dword | R/W | 2
| 0x2508 | 0x2509 | 9480 | 9481 | Ep import - Individual channel 1 | Dword | R/W | 2
| 0x250A | 0x250B | 9482 | 9483 | Ep import - Individual channel 2 | Dword | R/W | 2
| 0x250C | 0x250D | 9484 | 9485 | Ep import - Individual channel 3 | Dword | R/W | 2
| 0x250E | 0x250F | 9486 | 9487 | Ep import - Individual channel 4 | Dword | R/W | 2
| 0x2510 | 0x2511 | 9488 | 9489 | Ep import - Individual channel 5 | Dword | R/W | 2
| 0x2512 | 0x2513 | 9490 | 9491 | Ep import - Individual channel 6 | Dword | R/W | 2
| 0x2514 | 0x2515 | 9492 | 9493 | Ep import - Individual channel 7 | Dword | R/W | 2
| 0x2516 | 0x2517 | 9494 | 9495 | Ep import - Individual channel 8 | Dword | R/W | 2
| 0x2518 | 0x2519 | 9496 | 9497 | Ep import - Individual channel 9 | Dword | R/W | 2
| 0x251A | 0x251B | 9498 | 9499 | Ep import - Individual channel 10 | Dword | R/W | 2
| 0x251C | 0x251D | 9500 | 9501 | Ep import - Individual channel 11 | Dword | R/W | 2
| 0x251E | 0x251F | 9502 | 9503 | Ep import - Individual channel 12 | Dword | R/W | 2
| 0x2520 | 0x2521 | 9504 | 9505 | Ep import - Individual channel 13 | Dword | R/W | 2
| 0x2522 | 0x2523 | 9506 | 9507 | Ep import - Individual channel 14 | Dword | R/W | 2
| 0x2524 | 0x2525 | 9508 | 9509 | Ep import - Individual channel 15 | Dword | R/W | 2
| 0x2526 | 0x2527 | 9510 | 9511 | Ep import - Individual channel 16 | Dword | R/W | 2
| 0x2528 | 0x2529 | 9512 | 9513 | Ep import - Individual channel 17 | Dword | R/W | 2
| 0x252A | 0x252B | 9514 | 9515 | Ep import - Individual channel 18 | Dword | R/W | 2
| 0x252C | 0x252D | 9516 | 9517 | Ep import - User channel 1 | Dword | R/W | 2
| 0x252E | 0x252F | 9518 | 9519 | Ep import - User channel 2 | Dword | R/W | 2
| 0x2530 | 0x2531 | 9520 | 9521 | Ep import - User channel 3 | Dword | R/W | 2
| 0x2532 | 0x2533 | 9522 | 9523 | Ep import - User channel 4 | Dword | R/W | 2
| 0x2534 | 0x2535 | 9524 | 9525 | Ep import - User channel 5 | Dword | R/W | 2
| 0x2536 | 0x2537 | 9526 | 9527 | Ep import - User channel 6 | Dword | R/W | 2
| 0x2538 | 0x2539 | 9528 | 9529 | Ep import - User channel 7 | Dword | R/W | 2
| 0x253A | 0x253B | 9530 | 9531 | Ep import - User channel 8 | Dword | R/W | 2
| 0x253C | 0x253D | 9532 | 9533 | Ep import - User channel 9 | Dword | R/W | 2
Previous 1~7 days Energy | 0x4C00 | 0x4C37 | 19456 | 19511 | Previous 1-day energy | Dword | R | 56
(0x03 Read) | 0x4D00 | 0x4D37 | 19712 | 19767 | Previous 2-day energy | Dword | R | 56
| 0x4E00 | 0x4E37 | 19968 | 20023 | Previous 3-day energy | Dword | R | 56
| 0x4F00 | 0x4F37 | 20224 | 20279 | Previous 4-day energy | Dword | R | 56
| 0x5000 | 0x5037 | 20480 | 20535 | Previous 5-day energy | Dword | R | 56
| 0x5100 | 0x5137 | 20736 | 20791 | Previous 6-day energy | Dword | R | 56
| 0x5200 | 0x5237 | 20992 | 21047 | Previous 7-day energy | Dword | R | 56
TOU Ep import (curren month) | 0x2600 | 0x2601 | 9728 | 9729 | Epin-S import - current month - total | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2602 | 0x2603 | 9730 | 9731 | Epin-S import - current month - tariff 1 | Dword | R/W | 2
| 0x2604 | 0x2605 | 9732 | 9733 | Epin-S import - current month - tariff 2 | Dword | R/W | 2
| 0x2606 | 0x2607 | 9734 | 9735 | Epin-S import - current month - tariff 3 | Dword | R/W | 2
| 0x2608 | 0x2609 | 9736 | 9737 | Epin-S import - current month - tariff 4 | Dword | R/W | 2
| 0x260A | 0x260B | 9738 | 9739 | Epin-A import - current month - total | Dword | R/W | 2
| 0x260C | 0x260D | 9740 | 9741 | Epin-A import - current month - tariff 1 | Dword | R/W | 2
| 0x260E | 0x260F | 9742 | 9743 | Epin-A import - current month - tariff 2 | Dword | R/W | 2
| 0x2610 | 0x2611 | 9744 | 9745 | Epin-A import - current month - tariff 3 | Dword | R/W | 2
| 0x2612 | 0x2613 | 9746 | 9747 | Epin-A import - current month - tariff 4 | Dword | R/W | 2
| 0x2614 | 0x2615 | 9748 | 9749 | Epin-B import - current month - total | Dword | R/W | 2
| 0x2616 | 0x2617 | 9750 | 9751 | Epin-B import - current month - tariff 1 | Dword | R/W | 2
| 0x2618 | 0x2619 | 9752 | 9753 | Epin-B import - current month - tariff 2 | Dword | R/W | 2
| 0x261A | 0x261B | 9754 | 9755 | Epin-B import - current month - tariff 3 | Dword | R/W | 2
| 0x261C | 0x261D | 9756 | 9757 | Epin-B import - current month - tariff 4 | Dword | R/W | 2
| 0x261E | 0x261F | 9758 | 9759 | Epin-C import - current month - total | Dword | R/W | 2
| 0x2620 | 0x2621 | 9760 | 9761 | Epin-C import - current month - tariff 1 | Dword | R/W | 2
| 0x2622 | 0x2623 | 9762 | 9763 | Epin-C import - current month - tariff 2 | Dword | R/W | 2
| 0x2624 | 0x2625 | 9764 | 9765 | Epin-C import - current month - tariff 3 | Dword | R/W | 2
| 0x2626 | 0x2627 | 9766 | 9767 | Epin-C import - current month - tariff 4 | Dword | R/W | 2
| 0x2628 | 0x2629 | 9768 | 9769 | Ep1 import - current month - total | Dword | R/W | 2
| 0x262A | 0x262B | 9770 | 9771 | Ep1 import - current month - tariff 1 | Dword | R/W | 2
| 0x262C | 0x262D | 9772 | 9773 | Ep1 import - current month - tariff 2 | Dword | R/W | 2
| 0x262E | 0x262F | 9774 | 9775 | Ep1 import - current month - tariff 3 | Dword | R/W | 2
| 0x2630 | 0x2631 | 9776 | 9777 | Ep1 import - current month - tariff 4 | Dword | R/W | 2
| 0x2632 | 0x263B | 9778 | 9787 | Ep2 import - current month (same as Ep1) | Dword | R/W | 10
| 0x263C | 0x2645 | 9788 | 9797 | Ep3 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2646 | 0x264F | 9798 | 9807 | Ep4 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2650 | 0x2659 | 9808 | 9817 | Ep5 import - current month (same as Ep1) | Dword | R/W | 10
| 0x265A | 0x2663 | 9818 | 9827 | Ep6 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2664 | 0x266D | 9828 | 9837 | Ep7 import - current month (same as Ep1) | Dword | R/W | 10
| 0x266E | 0x2677 | 9838 | 9847 | Ep8 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2678 | 0x2681 | 9848 | 9857 | Ep9 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2682 | 0x268B | 9858 | 9867 | Ep10 import - current month (same as Ep1) | Dword | R/W | 10
| 0x268C | 0x2695 | 9868 | 9877 | Ep11 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2696 | 0x269F | 9878 | 9887 | Ep12 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26A0 | 0x26A9 | 9888 | 9897 | Ep13 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26AA | 0x26B3 | 9898 | 9907 | Ep14 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26B4 | 0x26BD | 9908 | 9917 | Ep15 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26BE | 0x26C7 | 9918 | 9927 | Ep16 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26C8 | 0x26D1 | 9928 | 9937 | Ep17 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26D2 | 0x26DB | 9938 | 9947 | Ep18 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26DC | 0x26DD | 9948 | 9949 | Eps1 import - current month - total | Dword | R/W | 2
| 0x26DE | 0x26DF | 9950 | 9951 | Eps1 import - current month - tariff 1 | Dword | R/W | 2
| 0x26E0 | 0x26E1 | 9952 | 9953 | Eps1 import - current month - tariff 2 | Dword | R/W | 2
| 0x26E2 | 0x26E3 | 9954 | 9955 | Eps1 import - current month - tariff 3 | Dword | R/W | 2
| 0x26E4 | 0x26E5 | 9956 | 9957 | Eps1 import - current month - tariff 4 | Dword | R/W | 2
| 0x26E6 | 0x26EF | 9958 | 9967 | Eps2 import - current month (same as Eps1) | Dword | R/W | 10
| 0x26F0 | 0x26F9 | 9968 | 9977 | Eps3 import - current month (same as Eps1) | Dword | R/W | 10
| 0x26FA | 0x2703 | 9978 | 9987 | Eps4 import - current month (same as Eps1) | Dword | R/W | 10
| 0x2704 | 0x270D | 9988 | 9997 | Eps5 import - current month (same as Eps1) | Dword | R/W | 10
| 0x270E | 0x2717 | 9998 | 10007 | Eps6 import - current month (same as Eps1) | Dword | R/W | 10
TOU Ep import (previous month) | 0x2900 | 0x2901 | 10496 | 10497 | Epin-S import - previous month - total | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2902 | 0x2903 | 10498 | 10499 | Epin-S import - previous month - tariff 1 | Dword | R/W | 2
| 0x2904 | 0x2905 | 10500 | 10501 | Epin-S import - previous month - tariff 2 | Dword | R/W | 2
| 0x2906 | 0x2907 | 10502 | 10503 | Epin-S import - previous month - tariff 3 | Dword | R/W | 2
| 0x2908 | 0x2909 | 10504 | 10505 | Epin-S import - previous month - tariff 4 | Dword | R/W | 2
| 0x290A | 0x290B | 10506 | 10507 | Epin-A import - previous month - total | Dword | R/W | 2
| 0x290C | 0x290D | 10508 | 10509 | Epin-A import - previous month - tariff 1 | Dword | R/W | 2
| 0x290E | 0x290F | 10510 | 10511 | Epin-A import - previous month - tariff 2 | Dword | R/W | 2
| 0x2910 | 0x2911 | 10512 | 10513 | Epin-A import - previous month - tariff 3 | Dword | R/W | 2
| 0x2912 | 0x2913 | 10514 | 10515 | Epin-A import - previous month - tariff 4 | Dword | R/W | 2
| 0x2914 | 0x2915 | 10516 | 10517 | Epin-B import - previous month - total | Dword | R/W | 2
| 0x2916 | 0x2917 | 10518 | 10519 | Epin-B import - previous month - tariff 1 | Dword | R/W | 2
| 0x2918 | 0x2919 | 10520 | 10521 | Epin-B import - previous month - tariff 2 | Dword | R/W | 2
| 0x291A | 0x291B | 10522 | 10523 | Epin-B import - previous month - tariff 3 | Dword | R/W | 2
| 0x291C | 0x291D | 10524 | 10525 | Epin-B import - previous month - tariff 4 | Dword | R/W | 2
| 0x291E | 0x291F | 10526 | 10527 | Epin-C import - previous month - total | Dword | R/W | 2
| 0x2920 | 0x2921 | 10528 | 10529 | Epin-C import - previous month - tariff 1 | Dword | R/W | 2
| 0x2922 | 0x2923 | 10530 | 10531 | Epin-C import - previous month - tariff 2 | Dword | R/W | 2
| 0x2924 | 0x2925 | 10532 | 10533 | Epin-C import - previous month - tariff 3 | Dword | R/W | 2
| 0x2926 | 0x2927 | 10534 | 10535 | Epin-C import - previous month - tariff 4 | Dword | R/W | 2
| 0x2928 | 0x2929 | 10536 | 10537 | Ep1 import - previous month - total | Dword | R/W | 2
| 0x292A | 0x292B | 10538 | 10539 | Ep1 import - previous month - tariff 1 | Dword | R/W | 2
| 0x292C | 0x292D | 10540 | 10541 | Ep1 import - previous month - tariff 2 | Dword | R/W | 2
| 0x292E | 0x292F | 10542 | 10543 | Ep1 import - previous month - tariff 3 | Dword | R/W | 2
| 0x2930 | 0x2931 | 10544 | 10545 | Ep1 import - previous month - tariff 4 | Dword | R/W | 2
| 0x2932 | 0x293B | 10546 | 10555 | Ep2 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x293C | 0x2945 | 10556 | 10565 | Ep3 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2946 | 0x294F | 10566 | 10575 | Ep4 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2950 | 0x2959 | 10576 | 10585 | Ep5 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x295A | 0x2963 | 10586 | 10595 | Ep6 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2964 | 0x296D | 10596 | 10605 | Ep7 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x296E | 0x2977 | 10606 | 10615 | Ep8 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2978 | 0x2981 | 10616 | 10625 | Ep9 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2982 | 0x298B | 10626 | 10635 | Ep10 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x298C | 0x2995 | 10636 | 10645 | Ep11 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2996 | 0x299F | 10646 | 10655 | Ep12 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29A0 | 0x29A9 | 10656 | 10665 | Ep13 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29AA | 0x29B3 | 10666 | 10675 | Ep14 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29B4 | 0x29BD | 10676 | 10685 | Ep15 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29BE | 0x29C7 | 10686 | 10695 | Ep16 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29C8 | 0x29D1 | 10696 | 10705 | Ep17 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29D2 | 0x29DB | 10706 | 10715 | Ep18 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29DC | 0x29DD | 10716 | 10717 | Eps1 import - previous month - total | Dword | R/W | 2
| 0x29DE | 0x29DF | 10718 | 10719 | Eps1 import - previous month - tariff 1 | Dword | R/W | 2
| 0x29E0 | 0x29E1 | 10720 | 10721 | Eps1 import - previous month - tariff 2 | Dword | R/W | 2
| 0x29E2 | 0x29E3 | 10722 | 10723 | Eps1 import - previous month - tariff 3 | Dword | R/W | 2
| 0x29E4 | 0x29E5 | 10724 | 10725 | Eps1 import - previous month - tariff 4 | Dword | R/W | 2
| 0x29E6 | 0x29EF | 10726 | 10735 | Eps2 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x29F0 | 0x29F9 | 10736 | 10745 | Eps3 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x29FA | 0x2A03 | 10746 | 10755 | Eps4 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x2A04 | 0x2A0D | 10756 | 10765 | Eps5 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x2A0E | 0x2A17 | 10766 | 10775 | Eps6 import - previous month (same as Eps1) | Dword | R/W | 10

## Reactive & Apparent Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Import Reactive Energy | 0x2B00 | 0x2B01 | 11008 | 11009 | Eqin-A import | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2B02 | 0x2B03 | 11010 | 11011 | Eqin-B import | Dword | R/W | 2
| 0x2B04 | 0x2B05 | 11012 | 11013 | Eqin-C import | Dword | R/W | 2
| 0x2B06 | 0x2B07 | 11014 | 11015 | Eqin-S import | Dword | R/W | 2
| 0x2B08 | 0x2B09 | 11016 | 11017 | Eq import - Individual channel 1 | Dword | R/W | 2
| 0x2B0A | 0x2B0B | 11018 | 11019 | Eq import - Individual channel 2 | Dword | R/W | 2
| 0x2B0C | 0x2B0D | 11020 | 11021 | Eq import - Individual channel 3 | Dword | R/W | 2
| 0x2B0E | 0x2B0F | 11022 | 11023 | Eq import - Individual channel 4 | Dword | R/W | 2
| 0x2B10 | 0x2B11 | 11024 | 11025 | Eq import - Individual channel 5 | Dword | R/W | 2
| 0x2B12 | 0x2B13 | 11026 | 11027 | Eq import - Individual channel 6 | Dword | R/W | 2
| 0x2B14 | 0x2B15 | 11028 | 11029 | Eq import - Individual channel 7 | Dword | R/W | 2
| 0x2B16 | 0x2B17 | 11030 | 11031 | Eq import - Individual channel 8 | Dword | R/W | 2
| 0x2B18 | 0x2B19 | 11032 | 11033 | Eq import - Individual channel 9 | Dword | R/W | 2
| 0x2B1A | 0x2B1B | 11034 | 11035 | Eq import - Individual channel 10 | Dword | R/W | 2
| 0x2B1C | 0x2B1D | 11036 | 11037 | Eq import - Individual channel 11 | Dword | R/W | 2
| 0x2B1E | 0x2B1F | 11038 | 11039 | Eq import - Individual channel 12 | Dword | R/W | 2
| 0x2B20 | 0x2B21 | 11040 | 11041 | Eq import - Individual channel 13 | Dword | R/W | 2
| 0x2B22 | 0x2B23 | 11042 | 11043 | Eq import - Individual channel 14 | Dword | R/W | 2
| 0x2B24 | 0x2B25 | 11044 | 11045 | Eq import - Individual channel 15 | Dword | R/W | 2
| 0x2B26 | 0x2B27 | 11046 | 11047 | Eq import - Individual channel 16 | Dword | R/W | 2
| 0x2B28 | 0x2B29 | 11048 | 11049 | Eq import - Individual channel 17 | Dword | R/W | 2
| 0x2B2A | 0x2B2B | 11050 | 11051 | Eq import - Individual channel 18 | Dword | R/W | 2
| 0x2B2C | 0x2B2D | 11052 | 11053 | Eq import - User channel 1 | Dword | R/W | 2
| 0x2B2E | 0x2B2F | 11054 | 11055 | Eq import - User channel 2 | Dword | R/W | 2
| 0x2B30 | 0x2B31 | 11056 | 11057 | Eq import - User channel 3 | Dword | R/W | 2
| 0x2B32 | 0x2B33 | 11058 | 11059 | Eq import - User channel 4 | Dword | R/W | 2
| 0x2B34 | 0x2B35 | 11060 | 11061 | Eq import - User channel 5 | Dword | R/W | 2
| 0x2B36 | 0x2B37 | 11062 | 11063 | Eq import - User channel 6 | Dword | R/W | 2
| 0x2B70 | 0x2B71 | 11120 | 11121 | Eq import - User channel 7 | Dword | R/W | 2
| 0x2B72 | 0x2B73 | 11122 | 11123 | Eq import - User channel 8 | Dword | R/W | 2
| 0x2B74 | 0x2B75 | 11124 | 11125 | Eq import - User channel 9 | Dword | R/W | 2
Import Apparent Energy | 0x2B38 | 0x2B39 | 11064 | 11065 | Esin-A import | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2B3A | 0x2B3B | 11066 | 11067 | Esin-B import | Dword | R/W | 2
| 0x2B3C | 0x2B3D | 11068 | 11069 | Esin-C import | Dword | R/W | 2
| 0x2B3E | 0x2B3F | 11070 | 11071 | Esin-S import | Dword | R/W | 2
| 0x2B40 | 0x2B41 | 11072 | 11073 | Es import - Individual channel 1 | Dword | R/W | 2
| 0x2B42 | 0x2B43 | 11074 | 11075 | Es import - Individual channel 2 | Dword | R/W | 2
| 0x2B44 | 0x2B45 | 11076 | 11077 | Es import - Individual channel 3 | Dword | R/W | 2
| 0x2B46 | 0x2B47 | 11078 | 11079 | Es import - Individual channel 4 | Dword | R/W | 2
| 0x2B48 | 0x2B49 | 11080 | 11081 | Es import - Individual channel 5 | Dword | R/W | 2
| 0x2B4A | 0x2B4B | 11082 | 11083 | Es import - Individual channel 6 | Dword | R/W | 2
| 0x2B4C | 0x2B4D | 11084 | 11085 | Es import - Individual channel 7 | Dword | R/W | 2
| 0x2B4E | 0x2B4F | 11086 | 11087 | Es import - Individual channel 8 | Dword | R/W | 2
| 0x2B50 | 0x2B51 | 11088 | 11089 | Es import - Individual channel 9 | Dword | R/W | 2
| 0x2B52 | 0x2B53 | 11090 | 11091 | Es import - Individual channel 10 | Dword | R/W | 2
| 0x2B54 | 0x2B55 | 11092 | 11093 | Es import - Individual channel 11 | Dword | R/W | 2
| 0x2B56 | 0x2B57 | 11094 | 11095 | Es import - Individual channel 12 | Dword | R/W | 2
| 0x2B58 | 0x2B59 | 11096 | 11097 | Es import - Individual channel 13 | Dword | R/W | 2
| 0x2B5A | 0x2B5B | 11098 | 11099 | Es import - Individual channel 14 | Dword | R/W | 2
| 0x2B5C | 0x2B5D | 11100 | 11101 | Es import - Individual channel 15 | Dword | R/W | 2
| 0x2B5E | 0x2B5F | 11102 | 11103 | Es import - Individual channel 16 | Dword | R/W | 2
| 0x2B60 | 0x2B61 | 11104 | 11105 | Es import - Individual channel 17 | Dword | R/W | 2
| 0x2B62 | 0x2B63 | 11106 | 11107 | Es import - Individual channel 18 | Dword | R/W | 2
| 0x2B64 | 0x2B65 | 11108 | 11109 | Es import - User channel 1 | Dword | R/W | 2
| 0x2B66 | 0x2B67 | 11110 | 11111 | Es import - User channel 2 | Dword | R/W | 2
| 0x2B68 | 0x2B69 | 11112 | 11113 | Es import - User channel 3 | Dword | R/W | 2
| 0x2B6A | 0x2B6B | 11114 | 11115 | Es import - User channel 4 | Dword | R/W | 2
| 0x2B6C | 0x2B6D | 11116 | 11117 | Es import - User channel 5 | Dword | R/W | 2
| 0x2B6E | 0x2B6F | 11118 | 11119 | Es import - User channel 6 | Dword | R/W | 2
| 0x2B76 | 0x2B77 | 11126 | 11127 | Es import - User channel 7 | Dword | R/W | 2
| 0x2B78 | 0x2B79 | 11128 | 11129 | Es import - User channel 8 | Dword | R/W | 2
| 0x2B7A | 0x2B7B | 11130 | 11131 | Es import - User channel 9 | Dword | R/W | 2

## Demand
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Demand | 0x2D00 | 0x2D01 | 11520 | 11521 | Pin-s-demand | Float | R | 2
(0x03 Read) | 0x2D02 | 0x2D03 | 11522 | 11523 | Pin-s-demand Prediction | Float | R | 2
| 0x2D04 | 0x2D05 | 11524 | 11525 | Pin-s-demand-max | Float | R | 2
| 0x2D06 | 0x2D08 | 11526 | 11528 | Pin-s-demand-max Time | Word | R | 3
| 0x2D09 | 0x2D0A | 11529 | 11530 | Qin-s-demand | Float | R | 2
| 0x2D0B | 0x2D0C | 11531 | 11532 | Qin-s-demand Prediction | Float | R | 2
| 0x2D0D | 0x2D0E | 11533 | 11534 | Qin-s-demand-max | Float | R | 2
| 0x2D0F | 0x2D11 | 11535 | 11537 | Qin-s-demand-max Time | Word | R | 3
| 0x2D12 | 0x2D13 | 11538 | 11539 | Sin-s-demand | Float | R | 2
| 0x2D14 | 0x2D15 | 11540 | 11541 | Sin-s-demand Prediction | Float | R | 2
| 0x2D16 | 0x2D17 | 11542 | 11543 | Sin-s-demand-max | Float | R | 2
| 0x2D18 | 0x2D1A | 11544 | 11546 | Sin-s-demand-max Time | Word | R | 3
| 0x2D1B | 0x2D1C | 11547 | 11548 | Ia-demand | Float | R | 2
| 0x2D1D | 0x2D1E | 11549 | 11550 | Ia-demand Prediction | Float | R | 2
| 0x2D1F | 0x2D20 | 11551 | 11552 | Ia-demand-max | Float | R | 2
| 0x2D21 | 0x2D23 | 11553 | 11555 | Ia-demand-max Time | Word | R | 3
| 0x2D24 | 0x2D25 | 11556 | 11557 | Pin-A-demand | Float | R | 2
| 0x2D26 | 0x2D27 | 11558 | 11559 | Pin-A-demand Prediction | Float | R | 2
| 0x2D28 | 0x2D29 | 11560 | 11561 | Pin-A-demand-max | Float | R | 2
| 0x2D2A | 0x2D2C | 11562 | 11564 | Pin-A-demand-max Time | Word | R | 3
| 0x2D2D | 0x2D2E | 11565 | 11566 | Qin-A-demand | Float | R | 2
| 0x2D2F | 0x2D30 | 11567 | 11568 | Qin-A-demand Prediction | Float | R | 2
| 0x2D31 | 0x2D32 | 11569 | 11570 | Qin-A-demand-max | Float | R | 2
| 0x2D33 | 0x2D35 | 11571 | 11573 | Qin-A-demand-max Time | Word | R | 3
| 0x2D36 | 0x2D37 | 11574 | 11575 | Sin-A-demand | Float | R | 2
| 0x2D38 | 0x2D39 | 11576 | 11577 | Sin-A-demand Prediction | Float | R | 2
| 0x2D3A | 0x2D3B | 11578 | 11579 | Sin-A-demand-max | Float | R | 2
| 0x2D3C | 0x2D3E | 11580 | 11582 | Sin-A-demand-max Time | Word | R | 3
| 0x2D3F | 0x2D62 | 11583 | 11618 | Inline B demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2D63 | 0x2D86 | 11619 | 11654 | Inline C demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2D87 | 0x2DAA | 11655 | 11690 | Individual channel 1 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DAB | 0x2DCE | 11691 | 11726 | Individual channel 2 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DCF | 0x2DF2 | 11727 | 11762 | Individual channel 3 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DF3 | 0x2E16 | 11763 | 11798 | Individual channel 4 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E17 | 0x2E3A | 11799 | 11834 | Individual channel 5 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E3B | 0x2E5E | 11835 | 11870 | Individual channel 6 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E5F | 0x2E82 | 11871 | 11906 | Individual channel 7 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E83 | 0x2EA6 | 11907 | 11942 | Individual channel 8 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2EA7 | 0x2ECA | 11943 | 11978 | Individual channel 9 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2ECB | 0x2EEE | 11979 | 12014 | Individual channel 10 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2EEF | 0x2F12 | 12015 | 12050 | Individual channel 11 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F13 | 0x2F36 | 12051 | 12086 | Individual channel 12 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F37 | 0x2F5A | 12087 | 12122 | Individual channel 13 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F5B | 0x2F7E | 12123 | 12158 | Individual channel 14 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F7F | 0x2FA2 | 12159 | 12194 | Individual channel 15 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FA3 | 0x2FC6 | 12195 | 12230 | Individual channel 16 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FC7 | 0x2FEA | 12231 | 12266 | Individual channel 17 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FEB | 0x300E | 12267 | 12302 | Individual channel 18 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x300F | 0x3010 | 12303 | 12304 | User channel 1 Pin-A-demand | Float | R | 2
| 0x3011 | 0x3012 | 12305 | 12306 | User channel 1 Pin-A-demand Prediction | Float | R | 2
| 0x3013 | 0x3014 | 12307 | 12308 | User channel 1 Pin-A-demand-max | Float | R | 2
| 0x3015 | 0x3017 | 12309 | 12311 | User channel 1 Pin-A-demand-max Time | Word | R | 3
| 0x3018 | 0x3019 | 12312 | 12313 | User channel 1 Qin-A-demand | Float | R | 2
| 0x301A | 0x301B | 12314 | 12315 | User channel 1 Qin-A-demand Prediction | Float | R | 2
| 0x301C | 0x301D | 12316 | 12317 | User channel 1 Qin-A-demand-max | Float | R | 2
| 0x301E | 0x3020 | 12318 | 12320 | User channel 1 Qin-A-demand-max Time | Word | R | 3
| 0x3021 | 0x3022 | 12321 | 12322 | User channel 1 Sin-A-demand | Float | R | 2
| 0x3023 | 0x3024 | 12323 | 12324 | User channel 1 Sin-A-demand Prediction | Float | R | 2
| 0x3025 | 0x3026 | 12325 | 12326 | User channel 1 Sin-A-demand-max | Float | R | 2
| 0x3027 | 0x3029 | 12327 | 12329 | User channel 1 Sin-A-demand-max Time | Word | R | 3
| 0x302A | 0x3044 | 12330 | 12356 | User channel 2 demand | Float + Word | R | 27 | Same as "User channel 1"
| 0x3045 | 0x305F | 12357 | 12383 | User channel 3 demand | Float + Word | R | 27
| 0x3060 | 0x307A | 12384 | 12410 | User channel 4 demand | Float + Word | R | 27
| 0x307B | 0x3095 | 12411 | 12437 | User channel 5 demand | Float + Word | R | 27
| 0x3096 | 0x30B0 | 12438 | 12464 | User channel 6 demand | Float + Word | R | 27
| 0x30B1 | 0x30CB | 12465 | 12491 | User channel 7 demand | Float + Word | R | 27
| 0x30CC | 0x30E6 | 12492 | 12518 | User channel 8 demand | Float + Word | R | 27
| 0x30E7 | 0x3101 | 12519 | 12545 | User channel 9 demand | Float + Word | R | 27

## Power Quality
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Power Quality | 0x3200 | 0x3200 | 12800 | 12800 | Unbalance U | Word | R | 1
(0x03 Read) | 0x3201 | 0x3201 | 12801 | 12801 | THD-U1 or U12 | Word | R | 1
| 0x3202 | 0x3202 | 12802 | 12802 | THD-U2 or U23 | Word | R | 1
| 0x3203 | 0x3203 | 12803 | 12803 | THD-U3 or U31 | Word | R | 1
| 0x3204 | 0x3204 | 12804 | 12804 | THD-Uavg | Word | R | 1
| 0x3205 | 0x3205 | 12805 | 12805 | 2nd harmonics U1 or U12 | Word | R | 1
| 0x3206 | 0x3222 | 12806 | 12834 | 3rd~31st harmonics U1 or U12 | Word | R | 29
| 0x3223 | 0x3223 | 12835 | 12835 | 2nd harmonics U2 or U23 | Word | R | 1
| 0x3224 | 0x3240 | 12836 | 12864 | 3rd~31st harmonics U2 or U23 | Word | R | 29
| 0x3241 | 0x3241 | 12865 | 12865 | 2nd harmonics U3 or U31 | Word | R | 1
| 0x3242 | 0x325E | 12866 | 12894 | 3rd~31st harmonics U3 or U31 | Word | R | 29
| 0x325F | 0x325F | 12895 | 12895 | Unbalance I | Word | R | 1
| 0x3260 | 0x3260 | 12896 | 12896 | Odd THD U1 | Word | R | 1
| 0x3261 | 0x3261 | 12897 | 12897 | Even THD U1 | Word | R | 1
| 0x3262 | 0x3262 | 12898 | 12898 | Crest Factor U1 | Word | R | 1
| 0x3263 | 0x3263 | 12899 | 12899 | THF U1 | Word | R | 1
| 0x3264 | 0x3264 | 12900 | 12900 | Odd THD U2 | Word | R | 1
| 0x3265 | 0x3265 | 12901 | 12901 | Even THD U2 | Word | R | 1
| 0x3266 | 0x3266 | 12902 | 12902 | Crest Factor U2 | Word | R | 1
| 0x3267 | 0x3267 | 12903 | 12903 | THF U2 | Word | R | 1
| 0x3268 | 0x3268 | 12904 | 12904 | Odd THD U3 | Word | R | 1
| 0x3269 | 0x3269 | 12905 | 12905 | Even THD U3 | Word | R | 1
| 0x326A | 0x326A | 12906 | 12906 | Crest Factor U3 | Word | R | 1
| 0x326B | 0x326B | 12907 | 12907 | THF U3 | Word | R | 1
| 0x32A0 | 0x32A0 | 12960 | 12960 | Odd THD I1 | Word | R | 1
| 0x32A1 | 0x32A1 | 12961 | 12961 | Even THD I1 | Word | R | 1
| 0x32A2 | 0x32A2 | 12962 | 12962 | K Factor I1 | Word | R | 1
| 0x32A3 | 0x32A3 | 12963 | 12963 | Odd THD I2 | Word | R | 1
| 0x32A4 | 0x32A4 | 12964 | 12964 | Even THD I2 | Word | R | 1
| 0x32A5 | 0x32A5 | 12965 | 12965 | K Factor I2 | Word | R | 1
| 0x32A6 | 0x32A6 | 12966 | 12966 | Odd THD I3 | Word | R | 1
| 0x32A7 | 0x32A7 | 12967 | 12967 | Even THD I3 | Word | R | 1
| 0x32A8 | 0x32A8 | 12968 | 12968 | K Factor I3 | Word | R | 1
| 0x32A9 | 0x32A9 | 12969 | 12969 | Odd THD I4 | Word | R | 1
| 0x32AA | 0x32AA | 12970 | 12970 | Even THD I4 | Word | R | 1
| 0x32AB | 0x32AB | 12971 | 12971 | K Factor I4 | Word | R | 1
| 0x32AC | 0x32AC | 12972 | 12972 | Odd THD I5 | Word | R | 1
| 0x32AD | 0x32AD | 12973 | 12973 | Even THD I5 | Word | R | 1
| 0x32AE | 0x32AE | 12974 | 12974 | K Factor I5 | Word | R | 1
| 0x32AF | 0x32AF | 12975 | 12975 | Odd THD I6 | Word | R | 1
| 0x32B0 | 0x32B0 | 12976 | 12976 | Even THD I6 | Word | R | 1
| 0x32B1 | 0x32B1 | 12977 | 12977 | K Factor I6 | Word | R | 1
| 0x32B2 | 0x32B2 | 12978 | 12978 | Odd THD I7 | Word | R | 1
| 0x32B3 | 0x32B3 | 12979 | 12979 | Even THD I7 | Word | R | 1
| 0x32B4 | 0x32B4 | 12980 | 12980 | K Factor I7 | Word | R | 1
| 0x32B5 | 0x32B5 | 12981 | 12981 | Odd THD I8 | Word | R | 1
| 0x32B6 | 0x32B6 | 12982 | 12982 | Even THD I8 | Word | R | 1
| 0x32B7 | 0x32B7 | 12983 | 12983 | K Factor I8 | Word | R | 1
| 0x32B8 | 0x32B8 | 12984 | 12984 | Odd THD I9 | Word | R | 1
| 0x32B9 | 0x32B9 | 12985 | 12985 | Even THD I9 | Word | R | 1
| 0x32BA | 0x32BA | 12986 | 12986 | K Factor I9 | Word | R | 1
| 0x32BB | 0x32BB | 12987 | 12987 | Odd THD I10 | Word | R | 1
| 0x32BC | 0x32BC | 12988 | 12988 | Even THD I10 | Word | R | 1
| 0x32BD | 0x32BD | 12989 | 12989 | K Factor I10 | Word | R | 1
| 0x32BE | 0x32BE | 12990 | 12990 | Odd THD I11 | Word | R | 1
| 0x32BF | 0x32BF | 12991 | 12991 | Even THD I11 | Word | R | 1
| 0x32C0 | 0x32C0 | 12992 | 12992 | K Factor I11 | Word | R | 1
| 0x32C1 | 0x32C1 | 12993 | 12993 | Odd THD I12 | Word | R | 1
| 0x32C2 | 0x32C2 | 12994 | 12994 | Even THD I12 | Word | R | 1
| 0x32C3 | 0x32C3 | 12995 | 12995 | K Factor I12 | Word | R | 1
| 0x32C4 | 0x32C4 | 12996 | 12996 | Odd THD I13 | Word | R | 1
| 0x32C5 | 0x32C5 | 12997 | 12997 | Even THD I13 | Word | R | 1
| 0x32C6 | 0x32C6 | 12998 | 12998 | K Factor I13 | Word | R | 1
| 0x32C7 | 0x32C7 | 12999 | 12999 | Odd THD I14 | Word | R | 1
| 0x32C8 | 0x32C8 | 13000 | 13000 | Even THD I14 | Word | R | 1
| 0x32C9 | 0x32C9 | 13001 | 13001 | K Factor I14 | Word | R | 1
| 0x32CA | 0x32CA | 13002 | 13002 | Odd THD I15 | Word | R | 1
| 0x32CB | 0x32CB | 13003 | 13003 | Even THD I15 | Word | R | 1
| 0x32CC | 0x32CC | 13004 | 13004 | K Factor I15 | Word | R | 1
| 0x32CD | 0x32CD | 13005 | 13005 | Odd THD I16 | Word | R | 1
| 0x32CE | 0x32CE | 13006 | 13006 | Even THD I16 | Word | R | 1
| 0x32CF | 0x32CF | 13007 | 13007 | K Factor I16 | Word | R | 1
| 0x32D0 | 0x32D0 | 13008 | 13008 | Odd THD I17 | Word | R | 1
| 0x32D1 | 0x32D1 | 13009 | 13009 | Even THD I17 | Word | R | 1
| 0x32D2 | 0x32D2 | 13010 | 13010 | K Factor I17 | Word | R | 1
| 0x32D3 | 0x32D3 | 13011 | 13011 | Odd THD I18 | Word | R | 1
| 0x32D4 | 0x32D4 | 13012 | 13012 | Even THD I18 | Word | R | 1
| 0x32D5 | 0x32D5 | 13013 | 13013 | K Factor I18 | Word | R | 1
| 0x3300 | 0x3300 | 13056 | 13056 | THD I1 | Word | R | 1
| 0x3301 | 0x331E | 13057 | 13086 | 2nd~31st harmonics I1 | Word | R | 30
| 0x331F | 0x331F | 13087 | 13087 | THD I2 | Word | R | 1
| 0x3320 | 0x333D | 13088 | 13117 | 2nd~31st harmonics I2 | Word | R | 30
| 0x333E | 0x333E | 13118 | 13118 | THD I3 | Word | R | 1
| 0x333F | 0x335C | 13119 | 13148 | 2nd~31st harmonics I3 | Word | R | 30
| 0x335D | 0x335D | 13149 | 13149 | THD I4 | Word | R | 1
| 0x335E | 0x337B | 13150 | 13179 | 2nd~31st harmonics I4 | Word | R | 30
| 0x337C | 0x337C | 13180 | 13180 | THD I5 | Word | R | 1
| 0x337D | 0x339A | 13181 | 13210 | 2nd~31st harmonics I5 | Word | R | 30
| 0x339B | 0x339B | 13211 | 13211 | THD I6 | Word | R | 1
| 0x339C | 0x33B9 | 13212 | 13241 | 2nd~31st harmonics I6 | Word | R | 30
| 0x33BA | 0x33BA | 13242 | 13242 | THD I7 | Word | R | 1
| 0x33BB | 0x33D8 | 13243 | 13272 | 2nd~31st harmonics I7 | Word | R | 30
| 0x33D9 | 0x33D9 | 13273 | 13273 | THD I8 | Word | R | 1
| 0x33DA | 0x33F7 | 13274 | 13303 | 2nd~31st harmonics I8 | Word | R | 30
| 0x33F8 | 0x33F8 | 13304 | 13304 | THD I9 | Word | R | 1
| 0x33F9 | 0x3416 | 13305 | 13334 | 2nd~31st harmonics I9 | Word | R | 30
| 0x3417 | 0x3417 | 13335 | 13335 | THD I10 | Word | R | 1
| 0x3418 | 0x3435 | 13336 | 13365 | 2nd~31st harmonics I10 | Word | R | 30
| 0x3436 | 0x3436 | 13366 | 13366 | THD I11 | Word | R | 1
| 0x3437 | 0x3454 | 13367 | 13396 | 2nd~31st harmonics I11 | Word | R | 30
| 0x3455 | 0x3455 | 13397 | 13397 | THD I12 | Word | R | 1
| 0x3456 | 0x3473 | 13398 | 13427 | 2nd~31st harmonics I12 | Word | R | 30
| 0x3474 | 0x3474 | 13428 | 13428 | THD I13 | Word | R | 1
| 0x3475 | 0x3492 | 13429 | 13458 | 2nd~31st harmonics I13 | Word | R | 30
| 0x3493 | 0x3493 | 13459 | 13459 | THD I14 | Word | R | 1
| 0x3494 | 0x34B1 | 13460 | 13489 | 2nd~31st harmonics I14 | Word | R | 30
| 0x34B2 | 0x34B2 | 13490 | 13490 | THD I15 | Word | R | 1
| 0x34B3 | 0x34D0 | 13491 | 13520 | 2nd~31st harmonics I15 | Word | R | 30
| 0x34D1 | 0x34D1 | 13521 | 13521 | THD I16 | Word | R | 1
| 0x34D2 | 0x34EF | 13522 | 13551 | 2nd~31st harmonics I16 | Word | R | 30
| 0x34F0 | 0x34F0 | 13552 | 13552 | THD I17 | Word | R | 1
| 0x34F1 | 0x350E | 13553 | 13582 | 2nd~31st harmonics I17 | Word | R | 30
| 0x350F | 0x350F | 13583 | 13583 | THD I18 | Word | R | 1
| 0x3510 | 0x352D | 13584 | 13613 | 2nd~31st harmonics I18 | Word | R | 30
| 0x352E | 0x352E | 13614 | 13614 | Unbalance I - User channel 1 | Word | R | 1
| 0x352F | 0x352F | 13615 | 13615 | Unbalance I - User channel 2 | Word | R | 1
| 0x3530 | 0x3530 | 13616 | 13616 | Unbalance I - User channel 3 | Word | R | 1
| 0x3531 | 0x3531 | 13617 | 13617 | Unbalance I - User channel 4 | Word | R | 1
| 0x3532 | 0x3532 | 13618 | 13618 | Unbalance I - User channel 5 | Word | R | 1
| 0x3533 | 0x3533 | 13619 | 13619 | Unbalance I - User channel 6 | Word | R | 1
| 0x3534 | 0x3534 | 13620 | 13620 | Unbalance I - User channel 7 | Word | R | 1
| 0x3535 | 0x3535 | 13621 | 13621 | Unbalance I - User channel 8 | Word | R | 1
| 0x3536 | 0x3536 | 13622 | 13622 | Unbalance I - User channel 9 | Word | R | 1

## Phase Angle
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Phase Angle | 0x3600 | 0x3600 | 13824 | 13824 | Vb/Vbc phase angle | Word | R | 1 | 0~3600
(0x03 Read) | 0x3601 | 0x3601 | 13825 | 13825 | Vc/Vca phase angle | Word | R | 1 | 0~3600
| 0x3602 | 0x3602 | 13826 | 13826 | I1 phase angle | Word | R | 1 | 0~3600
| 0x3603 | 0x3603 | 13827 | 13827 | I2 phase angle | Word | R | 1 | 0~3600
| 0x3604 | 0x3604 | 13828 | 13828 | I3 phase angle | Word | R | 1 | 0~3600
| 0x3605 | 0x3605 | 13829 | 13829 | I4 phase angle | Word | R | 1 | 0~3600
| 0x3606 | 0x3606 | 13830 | 13830 | I5 phase angle | Word | R | 1 | 0~3600
| 0x3607 | 0x3607 | 13831 | 13831 | I6 phase angle | Word | R | 1 | 0~3600
| 0x3608 | 0x3608 | 13832 | 13832 | I7 phase angle | Word | R | 1 | 0~3600
| 0x3609 | 0x3609 | 13833 | 13833 | I8 phase angle | Word | R | 1 | 0~3600
| 0x360A | 0x360A | 13834 | 13834 | I9 phase angle | Word | R | 1 | 0~3600
| 0x360B | 0x360B | 13835 | 13835 | I10 phase angle | Word | R | 1 | 0~3600
| 0x360C | 0x360C | 13836 | 13836 | I11 phase angle | Word | R | 1 | 0~3600
| 0x360D | 0x360D | 13837 | 13837 | I12 phase angle | Word | R | 1 | 0~3600
| 0x360E | 0x360E | 13838 | 13838 | I13 phase angle | Word | R | 1 | 0~3600
| 0x360F | 0x360F | 13839 | 13839 | I14 phase angle | Word | R | 1 | 0~3600
| 0x3610 | 0x3610 | 13840 | 13840 | I15 phase angle | Word | R | 1 | 0~3600
| 0x3611 | 0x3611 | 13841 | 13841 | I16 phase angle | Word | R | 1 | 0~3600
| 0x3612 | 0x3612 | 13842 | 13842 | I17 phase angle | Word | R | 1 | 0~3600
| 0x3613 | 0x3613 | 13843 | 13843 | I18 phase angle | Word | R | 1 | 0~3600

## DI Pulse Counter & Value
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI Counter & Value | 0x3A00 | 0x3A01 | 14848 | 14849 | DI1 pulse counter number | Dword | R | 2
(0x03 Read) | 0x3A02 | 0x3A03 | 14850 | 14851 | DI2 pulse counter number | Dword | R | 2
| 0x3A04 | 0x3A05 | 14852 | 14853 | DI3 pulse counter number | Dword | R | 2
| 0x3A06 | 0x3A07 | 14854 | 14855 | DI4 pulse counter number | Dword | R | 2
| 0x3A08 | 0x3A09 | 14856 | 14857 | DI5 pulse counter number | Dword | R | 2
| 0x3A0A | 0x3A0B | 14858 | 14859 | DI6 pulse counter number | Dword | R | 2
| 0x3A0C | 0x3A0D | 14860 | 14861 | DI7 pulse counter number | Dword | R | 2
| 0x3A0E | 0x3A0F | 14862 | 14863 | DI8 pulse counter number | Dword | R | 2
| 0x3A10 | 0x3A11 | 14864 | 14865 | DI9 pulse counter number | Dword | R | 2
| 0x3A12 | 0x3A13 | 14866 | 14867 | DI10 pulse counter number | Dword | R | 2
| 0x3A14 | 0x3A15 | 14868 | 14869 | DI11 pulse counter number | Dword | R | 2
| 0x3A16 | 0x3A17 | 14870 | 14871 | DI12 pulse counter number | Dword | R | 2
| 0x3A18 | 0x3A19 | 14872 | 14873 | DI13 pulse counter number | Dword | R | 2
| 0x3A1A | 0x3A1B | 14874 | 14875 | DI14 pulse counter number | Dword | R | 2
| 0x3A1C | 0x3A1D | 14876 | 14877 | DI15 pulse counter number | Dword | R | 2
| 0x3A1E | 0x3A1F | 14878 | 14879 | DI16 pulse counter number | Dword | R | 2
| 0x3A20 | 0x3A21 | 14880 | 14881 | DI17 pulse counter number | Dword | R | 2
| 0x3A22 | 0x3A23 | 14882 | 14883 | DI18 pulse counter number | Dword | R | 2
| 0x3A24 | 0x3A25 | 14884 | 14885 | DI1 pulse counter value | Float | R | 2
| 0x3A26 | 0x3A27 | 14886 | 14887 | DI2 pulse counter value | Float | R | 2
| 0x3A28 | 0x3A29 | 14888 | 14889 | DI3 pulse counter value | Float | R | 2
| 0x3A2A | 0x3A2B | 14890 | 14891 | DI4 pulse counter value | Float | R | 2
| 0x3A2C | 0x3A2D | 14892 | 14893 | DI5 pulse counter value | Float | R | 2
| 0x3A2E | 0x3A2F | 14894 | 14895 | DI6 pulse counter value | Float | R | 2
| 0x3A30 | 0x3A31 | 14896 | 14897 | DI7 pulse counter value | Float | R | 2
| 0x3A32 | 0x3A33 | 14898 | 14899 | DI8 pulse counter value | Float | R | 2
| 0x3A34 | 0x3A35 | 14900 | 14901 | DI9 pulse counter value | Float | R | 2
| 0x3A36 | 0x3A37 | 14902 | 14903 | DI10 pulse counter value | Float | R | 2
| 0x3A38 | 0x3A39 | 14904 | 14905 | DI11 pulse counter value | Float | R | 2
| 0x3A3A | 0x3A3B | 14906 | 14907 | DI12 pulse counter value | Float | R | 2
| 0x3A3C | 0x3A3D | 14908 | 14909 | DI13 pulse counter value | Float | R | 2
| 0x3A3E | 0x3A3F | 14910 | 14911 | DI14 pulse counter value | Float | R | 2
| 0x3A40 | 0x3A41 | 14912 | 14913 | DI15 pulse counter value | Float | R | 2
| 0x3A42 | 0x3A43 | 14914 | 14915 | DI16 pulse counter value | Float | R | 2
| 0x3A44 | 0x3A45 | 14916 | 14917 | DI17 pulse counter value | Float | R | 2
| 0x3A46 | 0x3A47 | 14918 | 14919 | DI18 pulse counter value | Float | R | 2
Pulse counter value = pulse counter number * pulse counter ratio (unit)

## DI & RO State
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI State | 0x0 | 0x0 | 0 | 0 | DI1 state | Bit | R | 1 | 1: ON, 0: OFF
(0x02 Read) | 0x1 | 0x1 | 1 | 1 | DI2 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x2 | 0x2 | 2 | 2 | DI3 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x3 | 0x3 | 3 | 3 | DI4 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x4 | 0x4 | 4 | 4 | DI5 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x5 | 0x5 | 5 | 5 | DI6 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x6 | 0x6 | 6 | 6 | DI7 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x7 | 0x7 | 7 | 7 | DI8 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x8 | 0x8 | 8 | 8 | DI9 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x9 | 0x9 | 9 | 9 | DI10 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xA | 0xA | 10 | 10 | DI11 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xB | 0xB | 11 | 11 | DI12 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xC | 0xC | 12 | 12 | DI13 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xD | 0xD | 13 | 13 | DI14 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xE | 0xE | 14 | 14 | DI15 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xF | 0xF | 15 | 15 | DI16 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x10 | 0x10 | 16 | 16 | DI17 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x11 | 0x11 | 17 | 17 | DI18 state | Bit | R | 1 | 1: ON, 0: OFF
RO State | 0x0 | 0x0 | 0 | 0 | RO1 state | Bit | R/W | 1 | 1: ON, 0: OFF
(0x01 Read, 0x05 Write) | 0x1 | 0x1 | 1 | 1 | RO2 state | Bit | R/W | 1 | 1: ON, 0: OFF

## Datalog & User Defined
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Datalog Window | 0x3B00 | 0x3B00 | 15104 | 15104 | Datalog type, enable, status | Word | R/W | 1
(0x03 Read, 0x10 Write) | 0x3B01 | 0x3B01 | 15105 | 15105 | Number of each window | Word | R/W | 1
| 0x3B02 | 0x3B03 | 15106 | 15107 | Window status + offset | Word | R/W | 2
| 0x3B04 | 0x3B7E | 15108 | 15230 | Window | Word | R | 123
Datalog 1 Data | 0x3C00 | 0x3C01 | 15360 | 15361 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3C02 | 0x3C03 | 15362 | 15363 | Used Records | UINT32 | R | 2
| 0x3C04 | 0x3C04 | 15364 | 15364 | Record Size | UINT16 | R | 1
| 0x3C05 | 0x3C05 | 15365 | 15365 | Log Availability | word | R | 1
| 0x3C06 | 0x3C08 | 15366 | 15368 | First Record Timestamp | word | R | 3
| 0x3C09 | 0x3C0B | 15369 | 15371 | Last Record Timestamp, | word | R | 3
Datalog 2 Data | 0x3D00 | 0x3D01 | 15616 | 15617 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3D02 | 0x3D03 | 15618 | 15619 | Used Records | UINT32 | R | 2
| 0x3D04 | 0x3D04 | 15620 | 15620 | Record Size | UINT16 | R | 1
| 0x3D05 | 0x3D05 | 15621 | 15621 | Log Availability | word | R | 1
| 0x3D06 | 0x3D08 | 15622 | 15624 | First Record Timestamp | word | R | 3
| 0x3D09 | 0x3D0B | 15625 | 15627 | Last Record Timestamp | word | R | 3
Datalog 3 Data | 0x3E00 | 0x3E01 | 15872 | 15873 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3E02 | 0x3E03 | 15874 | 15875 | Used Records | UINT32 | R | 2
| 0x3E04 | 0x3E04 | 15876 | 15876 | Record Size | UINT16 | R | 1
| 0x3E05 | 0x3E05 | 15877 | 15877 | Log Availability | word | R | 1
| 0x3E06 | 0x3E08 | 15878 | 15880 | First Record Timestamp | word | R | 3
| 0x3E09 | 0x3E0B | 15881 | 15883 | Last Record Timestamp | word | R | 3
User Defined Parameter | 0x3F00 | 0x3FE9 | 16128 | 16361 | User defined parameter reading window | word | R | 234
(0x03 Read)

## Ten-year Special Day
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Tne-year Special Day Settings | 0x4100 | 0x4100 | 16640 | 16640 | Ten-year special day settings enable/disable | word | R/W | 1 | 1: enable; 0: disable | 0
(0x03 Read, 0x10 Write) | 0x4101 | 0x4101 | 16641 | 16641 | Special day start year | word | R/W | 1 | 2000~2099 (end - start < 10) | 0
| 0x4102 | 0x4102 | 16642 | 16642 | Special day end year | word | R/W | 1 | 2000~2099 (end - start < 10) | 0
| 0x4103 | 0x4105 | 16643 | 16645 | 1st year setting: 1st special day - date & schedule | word | R/W | 3 | Month, day, schedule ID | 00:00 0
| 0x4106 | 0x4108 | 16646 | 16648 | 1st year setting : 2nd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4109 | 0x410B | 16649 | 16651 | 1st year setting: 3rd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x410C | 0x410E | 16652 | 16654 | 1st year setting: 4th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x410F | 0x4111 | 16655 | 16657 | 1st year setting: 5th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4112 | 0x4114 | 16658 | 16660 | 1st year setting: 6th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4115 | 0x4117 | 16661 | 16663 | 1st year setting: 7th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4118 | 0x411A | 16664 | 16666 | 1st year setting: 8th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x411B | 0x411D | 16667 | 16669 | 1st year setting: 9th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x411E | 0x4120 | 16670 | 16672 | 1st year setting: 10th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4121 | 0x4123 | 16673 | 16675 | 1st year setting: 11th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4124 | 0x4126 | 16676 | 16678 | 1st year setting: 12th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4127 | 0x4129 | 16679 | 16681 | 1st year setting: 13th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x412A | 0x412C | 16682 | 16684 | 1st year setting: 14th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x412D | 0x412F | 16685 | 16687 | 1st year setting: 15th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4130 | 0x4132 | 16688 | 16690 | 1st year setting: 16th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4133 | 0x4135 | 16691 | 16693 | 1st year setting: 17th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4136 | 0x4138 | 16694 | 16696 | 1st year setting: 18th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4139 | 0x413B | 16697 | 16699 | 1st year setting: 19th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x413C | 0x413E | 16700 | 16702 | 1st year setting: 20th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x413F | 0x4141 | 16703 | 16705 | 1st year setting: 21st special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4142 | 0x4144 | 16706 | 16708 | 1st year setting: 22nd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4145 | 0x4147 | 16709 | 16711 | 1st year setting: 23rd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4148 | 0x414A | 16712 | 16714 | 1st year setting: 24th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x414B | 0x414D | 16715 | 16717 | 1st year setting: 25th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x414E | 0x4150 | 16718 | 16720 | 1st year setting: 26th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4151 | 0x4153 | 16721 | 16723 | 1st year setting: 27th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4154 | 0x4156 | 16724 | 16726 | 1st year setting: 28th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4157 | 0x4159 | 16727 | 16729 | 1st year setting: 29th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x415A | 0x415C | 16730 | 16732 | 1st year setting: 30th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x415D | 0x415D | 16733 | 16733 | 1st year setting: setting year | word | R/W | 1 |  | 0
| 0x415E | 0x415E | 16734 | 16734 | 1st year setting: special day number | word | R/W | 1 |  | 0
| 0x415F | 0x41BA | 16735 | 16826 | 2nd year setting |  |  | 92 | Same as "1st year setting"
| 0x41BB | 0x4216 | 16827 | 16918 | 3rd year setting |  |  | 92
| 0x4217 | 0x4272 | 16919 | 17010 | 4th year setting |  |  | 92
| 0x4273 | 0x42CE | 17011 | 17102 | 5th year setting |  |  | 92
| 0x42CF | 0x432A | 17103 | 17194 | 6th year setting |  |  | 92
| 0x432B | 0x4386 | 17195 | 17286 | 7th year setting |  |  | 92
| 0x4387 | 0x43E2 | 17287 | 17378 | 8th year setting |  |  | 92
| 0x43E3 | 0x443E | 17379 | 17470 | 9th year setting |  |  | 92
| 0x443F | 0x449A | 17471 | 17562 | 10th year setting |  |  | 92