## AcuRev 4100
No. | Parameter Category | Parameter Name | Parameter Key | Unit | Data Type | R/W | Modbus Address (Dec)
1 | Real-time | System Frequency | FREQ_Hz | Hz | float32 | R | 8192
2 | Real-time | Phase A Line-to-Neutral Voltage | VLN_a_V | V | float32 | R | 8194
3 | Real-time | Phase B Line-to-Neutral Voltage | VLN_b_V | V | float32 | R | 8196
4 | Real-time | Phase C Line-to-Neutral Voltage | VLN_c_V | V | float32 | R | 8198
5 | Real-time | Average Line-to-Neutral Voltage | VLN_avg_V | V | float32 | R | 8200
6 | Real-time | Phase A-B Line-to-Line Voltage | VLL_ab_V | V | float32 | R | 8202
7 | Real-time | Phase B-C Line-to-Line Voltage | VLL_bc_V | V | float32 | R | 8204
8 | Real-time | Phase C-A Line-to-Line Voltage | VLL_ca_V | V | float32 | R | 8206
9 | Real-time | Average Line-to-Line Voltage | VLL_avg_V | V | float32 | R | 8208
10 | Real-time | Phase A Line-to-Neutral Voltage Phase Angle | ANG_VLN_a | ° | float32 | R | 8210
11 | Real-time | Phase B Line-to-Neutral Voltage Phase Angle | ANG_VLN_b | ° | float32 | R | 8212
12 | Real-time | Phase C Line-to-Neutral Voltage Phase Angle | ANG_VLN_c | ° | float32 | R | 8214
13 | Real-time | Phase A Current | I_a_A | A | float32 | R | 8216
14 | Real-time | Phase A Active Power | P_a_kW | kW | float32 | R | 8218
15 | Real-time | Phase A Reactive Power | Q_a_kvar | kvar | float32 | R | 8220
16 | Real-time | Phase A Apparent Power | S_a_kVA | kVA | float32 | R | 8222
17 | Real-time | Phase A Power Factor | PF_a |  | float32 | R | 8226
18 | Real-time | Phase B Current | I_b_A | A | float32 | R | 8228
19 | Real-time | Phase B Active Power | P_b_kW | kW | float32 | R | 8230
20 | Real-time | Phase B Reactive Power | Q_b_kvar | kvar | float32 | R | 8232
21 | Real-time | Phase B Apparent Power | S_b_kVA | kVA | float32 | R | 8234
22 | Real-time | Phase B Power Factor | PF_b |  | float32 | R | 8238
23 | Real-time | Phase C Current | I_c_A | A | float32 | R | 8240
24 | Real-time | Phase C Active Power | P_c_kW | kW | float32 | R | 8242
25 | Real-time | Phase C Reactive Power | Q_c_kvar | kvar | float32 | R | 8244
26 | Real-time | Phase C Apparent Power | S_c_kVA | kVA | float32 | R | 8246
27 | Real-time | Phase C Power Factor | PF_c |  | float32 | R | 8250
28 | Real-time | System Average Current | I_avg_A | A | float32 | R | 8252
29 | Real-time | System Active Power | P_kW | kW | float32 | R | 8254
30 | Real-time | System Reactive Power | Q_kvar | kvar | float32 | R | 8256
31 | Real-time | System Apparent Power | S_kVA | kVA | float32 | R | 8258
32 | Real-time | System Power Factor | PF |  | float32 | R | 8262
33 | Real-time | Input Channel 1 Current | I_001_A | A | float32 | R | 8264
34 | Real-time | Input Channel 1 Active Power | P_001_kW | kW | float32 | R | 8266
35 | Real-time | Input Channel 1 Reactive Power | Q_001_kvar | kvar | float32 | R | 8268
36 | Real-time | Input Channel 1 Apparent Power | S_001_kVA | kVA | float32 | R | 8270
37 | Real-time | Input Channel 1 Power Factor | PF_001 |  | float32 | R | 8274
38 | Real-time | Input Channel 1 Current Phase Angle | ANG_I_001 | ° | float32 | R | 8276
39 | Real-time | Input Channel 2 Current | I_002_A | A | float32 | R | 8278
40 | Real-time | Input Channel 2 Active Power | P_002_kW | kW | float32 | R | 8280
41 | Real-time | Input Channel 2 Reactive Power | Q_002_kvar | kvar | float32 | R | 8282
42 | Real-time | Input Channel 2 Apparent Power | S_002_kVA | kVA | float32 | R | 8284
43 | Real-time | Input Channel 2 Power Factor | PF_002 |  | float32 | R | 8288
44 | Real-time | Input Channel 2 Current Phase Angle | ANG_I_002 | ° | float32 | R | 8290
45 | Real-time | Input Channel 3 Current | I_003_A | A | float32 | R | 8292
46 | Real-time | Input Channel 3 Active Power | P_003_kW | kW | float32 | R | 8294
47 | Real-time | Input Channel 3 Reactive Power | Q_003_kvar | kvar | float32 | R | 8296
48 | Real-time | Input Channel 3 Apparent Power | S_003_kVA | kVA | float32 | R | 8298
49 | Real-time | Input Channel 3 Power Factor | PF_003 |  | float32 | R | 8302
50 | Real-time | Input Channel 3 Current Phase Angle | ANG_I_003 | ° | float32 | R | 8304
51 | Real-time | Input Channel 4 Current | I_004_A | A | float32 | R | 8306
52 | Real-time | Input Channel 4 Active Power | P_004_kW | kW | float32 | R | 8308
53 | Real-time | Input Channel 4 Reactive Power | Q_004_kvar | kvar | float32 | R | 8310
54 | Real-time | Input Channel 4 Apparent Power | S_004_kVA | kVA | float32 | R | 8312
55 | Real-time | Input Channel 4 Power Factor | PF_004 |  | float32 | R | 8316
56 | Real-time | Input Channel 4 Current Phase Angle | ANG_I_004 | ° | float32 | R | 8318
57 | Real-time | Input Channel 5 Current | I_005_A | A | float32 | R | 8320
58 | Real-time | Input Channel 5 Active Power | P_005_kW | kW | float32 | R | 8322
59 | Real-time | Input Channel 5 Reactive Power | Q_005_kvar | kvar | float32 | R | 8324
60 | Real-time | Input Channel 5 Apparent Power | S_005_kVA | kVA | float32 | R | 8326
61 | Real-time | Input Channel 5 Power Factor | PF_005 |  | float32 | R | 8330
62 | Real-time | Input Channel 5 Current Phase Angle | ANG_I_005 | ° | float32 | R | 8332
63 | Real-time | Input Channel 6 Current | I_006_A | A | float32 | R | 8334
64 | Real-time | Input Channel 6 Active Power | P_006_kW | kW | float32 | R | 8336
65 | Real-time | Input Channel 6 Reactive Power | Q_006_kvar | kvar | float32 | R | 8338
66 | Real-time | Input Channel 6 Apparent Power | S_006_kVA | kVA | float32 | R | 8340
67 | Real-time | Input Channel 6 Power Factor | PF_006 |  | float32 | R | 8344
68 | Real-time | Input Channel 6 Current Phase Angle | ANG_I_006 | ° | float32 | R | 8346
69 | Real-time | Input Channel 7 Current | I_007_A | A | float32 | R | 8348
70 | Real-time | Input Channel 7 Active Power | P_007_kW | kW | float32 | R | 8350
71 | Real-time | Input Channel 7 Reactive Power | Q_007_kvar | kvar | float32 | R | 8352
72 | Real-time | Input Channel 7 Apparent Power | S_007_kVA | kVA | float32 | R | 8354
73 | Real-time | Input Channel 7 Power Factor | PF_007 |  | float32 | R | 8358
74 | Real-time | Input Channel 7 Current Phase Angle | ANG_I_007 | ° | float32 | R | 8360
75 | Real-time | Input Channel 8 Current | I_008_A | A | float32 | R | 8362
76 | Real-time | Input Channel 8 Active Power | P_008_kW | kW | float32 | R | 8364
77 | Real-time | Input Channel 8 Reactive Power | Q_008_kvar | kvar | float32 | R | 8366
78 | Real-time | Input Channel 8 Apparent Power | S_008_kVA | kVA | float32 | R | 8368
79 | Real-time | Input Channel 8 Power Factor | PF_008 |  | float32 | R | 8372
80 | Real-time | Input Channel 8 Current Phase Angle | ANG_I_008 | ° | float32 | R | 8374
81 | Real-time | Input Channel 9 Current | I_009_A | A | float32 | R | 8376
82 | Real-time | Input Channel 9 Active Power | P_009_kW | kW | float32 | R | 8378
83 | Real-time | Input Channel 9 Reactive Power | Q_009_kvar | kvar | float32 | R | 8380
84 | Real-time | Input Channel 9 Apparent Power | S_009_kVA | kVA | float32 | R | 8382
85 | Real-time | Input Channel 9 Power Factor | PF_009 |  | float32 | R | 8386
86 | Real-time | Input Channel 9 Current Phase Angle | ANG_I_009 | ° | float32 | R | 8388
87 | Real-time | Input Channel 10 Current | I_010_A | A | float32 | R | 8390
88 | Real-time | Input Channel 10 Active Power | P_010_kW | kW | float32 | R | 8392
89 | Real-time | Input Channel 10 Reactive Power | Q_010_kvar | kvar | float32 | R | 8394
90 | Real-time | Input Channel 10 Apparent Power | S_010_kVA | kVA | float32 | R | 8396
91 | Real-time | Input Channel 10 Power Factor | PF_010 |  | float32 | R | 8400
92 | Real-time | Input Channel 10 Current Phase Angle | ANG_I_010 | ° | float32 | R | 8402
93 | Real-time | Input Channel 11 Current | I_011_A | A | float32 | R | 8404
94 | Real-time | Input Channel 11 Active Power | P_011_kW | kW | float32 | R | 8406
95 | Real-time | Input Channel 11 Reactive Power | Q_011_kvar | kvar | float32 | R | 8408
96 | Real-time | Input Channel 11 Apparent Power | S_011_kVA | kVA | float32 | R | 8410
97 | Real-time | Input Channel 11 Power Factor | PF_011 |  | float32 | R | 8414
98 | Real-time | Input Channel 11 Current Phase Angle | ANG_I_011 | ° | float32 | R | 8416
99 | Real-time | Input Channel 12 Current | I_012_A | A | float32 | R | 8418
100 | Real-time | Input Channel 12 Active Power | P_012_kW | kW | float32 | R | 8420
101 | Real-time | Input Channel 12 Reactive Power | Q_012_kvar | kvar | float32 | R | 8422
102 | Real-time | Input Channel 12 Apparent Power | S_012_kVA | kVA | float32 | R | 8424
103 | Real-time | Input Channel 12 Power Factor | PF_012 |  | float32 | R | 8428
104 | Real-time | Input Channel 12 Current Phase Angle | ANG_I_012 | ° | float32 | R | 8430
105 | Real-time | Input Channel 13 Current | I_013_A | A | float32 | R | 8432
106 | Real-time | Input Channel 13 Active Power | P_013_kW | kW | float32 | R | 8434
107 | Real-time | Input Channel 13 Reactive Power | Q_013_kvar | kvar | float32 | R | 8436
108 | Real-time | Input Channel 13 Apparent Power | S_013_kVA | kVA | float32 | R | 8438
109 | Real-time | Input Channel 13 Power Factor | PF_013 |  | float32 | R | 8442
110 | Real-time | Input Channel 13 Current Phase Angle | ANG_I_013 | ° | float32 | R | 8444
111 | Real-time | Input Channel 14 Current | I_014_A | A | float32 | R | 8446
112 | Real-time | Input Channel 14 Active Power | P_014_kW | kW | float32 | R | 8448
113 | Real-time | Input Channel 14 Reactive Power | Q_014_kvar | kvar | float32 | R | 8450
114 | Real-time | Input Channel 14 Apparent Power | S_014_kVA | kVA | float32 | R | 8452
115 | Real-time | Input Channel 14 Power Factor | PF_014 |  | float32 | R | 8456
116 | Real-time | Input Channel 14 Current Phase Angle | ANG_I_014 | ° | float32 | R | 8458
117 | Real-time | Input Channel 15 Current | I_015_A | A | float32 | R | 8460
118 | Real-time | Input Channel 15 Active Power | P_015_kW | kW | float32 | R | 8462
119 | Real-time | Input Channel 15 Reactive Power | Q_015_kvar | kvar | float32 | R | 8464
120 | Real-time | Input Channel 15 Apparent Power | S_015_kVA | kVA | float32 | R | 8466
121 | Real-time | Input Channel 15 Power Factor | PF_015 |  | float32 | R | 8470
122 | Real-time | Input Channel 15 Current Phase Angle | ANG_I_015 | ° | float32 | R | 8472
123 | Real-time | Input Channel 16 Current | I_016_A | A | float32 | R | 8474
124 | Real-time | Input Channel 16 Active Power | P_016_kW | kW | float32 | R | 8476
125 | Real-time | Input Channel 16 Reactive Power | Q_016_kvar | kvar | float32 | R | 8478
126 | Real-time | Input Channel 16 Apparent Power | S_016_kVA | kVA | float32 | R | 8480
127 | Real-time | Input Channel 16 Power Factor | PF_016 |  | float32 | R | 8484
128 | Real-time | Input Channel 16 Current Phase Angle | ANG_I_016 | ° | float32 | R | 8486
129 | Real-time | Input Channel 17 Current | I_017_A | A | float32 | R | 8488
130 | Real-time | Input Channel 17 Active Power | P_017_kW | kW | float32 | R | 8490
131 | Real-time | Input Channel 17 Reactive Power | Q_017_kvar | kvar | float32 | R | 8492
132 | Real-time | Input Channel 17 Apparent Power | S_017_kVA | kVA | float32 | R | 8494
133 | Real-time | Input Channel 17 Power Factor | PF_017 |  | float32 | R | 8498
134 | Real-time | Input Channel 17 Current Phase Angle | ANG_I_017 | ° | float32 | R | 8500
135 | Real-time | Input Channel 18 Current | I_018_A | A | float32 | R | 8502
136 | Real-time | Input Channel 18 Active Power | P_018_kW | kW | float32 | R | 8504
137 | Real-time | Input Channel 18 Reactive Power | Q_018_kvar | kvar | float32 | R | 8506
138 | Real-time | Input Channel 18 Apparent Power | S_018_kVA | kVA | float32 | R | 8508
139 | Real-time | Input Channel 18 Power Factor | PF_018 |  | float32 | R | 8512
140 | Real-time | Input Channel 18 Current Phase Angle | ANG_I_018 | ° | float32 | R | 8514
141 | Real-time | Input Channel 19 Current | I_019_A | A | float32 | R | 8516
142 | Real-time | Input Channel 19 Active Power | P_019_kW | kW | float32 | R | 8518
143 | Real-time | Input Channel 19 Reactive Power | Q_019_kvar | kvar | float32 | R | 8520
144 | Real-time | Input Channel 19 Apparent Power | S_019_kVA | kVA | float32 | R | 8522
145 | Real-time | Input Channel 19 Power Factor | PF_019 |  | float32 | R | 8526
146 | Real-time | Input Channel 19 Current Phase Angle | ANG_I_019 | ° | float32 | R | 8528
147 | Real-time | Input Channel 20 Current | I_020_A | A | float32 | R | 8530
148 | Real-time | Input Channel 20 Active Power | P_020_kW | kW | float32 | R | 8532
149 | Real-time | Input Channel 20 Reactive Power | Q_020_kvar | kvar | float32 | R | 8534
150 | Real-time | Input Channel 20 Apparent Power | S_020_kVA | kVA | float32 | R | 8536
151 | Real-time | Input Channel 20 Power Factor | PF_020 |  | float32 | R | 8540
152 | Real-time | Input Channel 20 Current Phase Angle | ANG_I_020 | ° | float32 | R | 8542
153 | Real-time | Input Channel 21 Current | I_021_A | A | float32 | R | 8544
154 | Real-time | Input Channel 21 Active Power | P_021_kW | kW | float32 | R | 8546
155 | Real-time | Input Channel 21 Reactive Power | Q_021_kvar | kvar | float32 | R | 8548
156 | Real-time | Input Channel 21 Apparent Power | S_021_kVA | kVA | float32 | R | 8550
157 | Real-time | Input Channel 21 Power Factor | PF_021 |  | float32 | R | 8554
158 | Real-time | Input Channel 21 Current Phase Angle | ANG_I_021 | ° | float32 | R | 8556
159 | Real-time | Input Channel 22 Current | I_022_A | A | float32 | R | 8558
160 | Real-time | Input Channel 22 Active Power | P_022_kW | kW | float32 | R | 8560
161 | Real-time | Input Channel 22 Reactive Power | Q_022_kvar | kvar | float32 | R | 8562
162 | Real-time | Input Channel 22 Apparent Power | S_022_kVA | kVA | float32 | R | 8564
163 | Real-time | Input Channel 22 Power Factor | PF_022 |  | float32 | R | 8568
164 | Real-time | Input Channel 22 Current Phase Angle | ANG_I_022 | ° | float32 | R | 8570
165 | Real-time | Input Channel 23 Current | I_023_A | A | float32 | R | 8572
166 | Real-time | Input Channel 23 Active Power | P_023_kW | kW | float32 | R | 8574
167 | Real-time | Input Channel 23 Reactive Power | Q_023_kvar | kvar | float32 | R | 8576
168 | Real-time | Input Channel 23 Apparent Power | S_023_kVA | kVA | float32 | R | 8578
169 | Real-time | Input Channel 23 Power Factor | PF_023 |  | float32 | R | 8582
170 | Real-time | Input Channel 23 Current Phase Angle | ANG_I_023 | ° | float32 | R | 8584
171 | Real-time | Input Channel 24 Current | I_024_A | A | float32 | R | 8586
172 | Real-time | Input Channel 24 Active Power | P_024_kW | kW | float32 | R | 8588
173 | Real-time | Input Channel 24 Reactive Power | Q_024_kvar | kvar | float32 | R | 8590
174 | Real-time | Input Channel 24 Apparent Power | S_024_kVA | kVA | float32 | R | 8592
175 | Real-time | Input Channel 24 Power Factor | PF_024 |  | float32 | R | 8596
176 | Real-time | Input Channel 24 Current Phase Angle | ANG_I_024 | ° | float32 | R | 8598
177 | Real-time | User Channel 1 Current | I_s001_A | A | float32 | R | 8600
178 | Real-time | User Channel 1 Active Power | P_s001_kW | kW | float32 | R | 8602
179 | Real-time | User Channel 1 Reactive Power | Q_s001_kvar | kvar | float32 | R | 8604
180 | Real-time | User Channel 1 Apparent Power | S_s001_kVA | kVA | float32 | R | 8606
181 | Real-time | User Channel 1 Power Factor | PF_s001 |  | float32 | R | 8610
182 | Real-time | User Channel 2 Current | I_s002_A | A | float32 | R | 8612
183 | Real-time | User Channel 2 Active Power | P_s002_kW | kW | float32 | R | 8614
184 | Real-time | User Channel 2 Reactive Power | Q_s002_kvar | kvar | float32 | R | 8616
185 | Real-time | User Channel 2 Apparent Power | S_s002_kVA | kVA | float32 | R | 8618
186 | Real-time | User Channel 2 Power Factor | PF_s002 |  | float32 | R | 8622
187 | Real-time | User Channel 3 Current | I_s003_A | A | float32 | R | 8624
188 | Real-time | User Channel 3 Active Power | P_s003_kW | kW | float32 | R | 8626
189 | Real-time | User Channel 3 Reactive Power | Q_s003_kvar | kvar | float32 | R | 8628
190 | Real-time | User Channel 3 Apparent Power | S_s003_kVA | kVA | float32 | R | 8630
191 | Real-time | User Channel 3 Power Factor | PF_s003 |  | float32 | R | 8634
192 | Real-time | User Channel 4 Current | I_s004_A | A | float32 | R | 8636
193 | Real-time | User Channel 4 Active Power | P_s004_kW | kW | float32 | R | 8638
194 | Real-time | User Channel 4 Reactive Power | Q_s004_kvar | kvar | float32 | R | 8640
195 | Real-time | User Channel 4 Apparent Power | S_s004_kVA | kVA | float32 | R | 8642
196 | Real-time | User Channel 4 Power Factor | PF_s004 |  | float32 | R | 8646
197 | Real-time | User Channel 5 Current | I_s005_A | A | float32 | R | 8648
198 | Real-time | User Channel 5 Active Power | P_s005_kW | kW | float32 | R | 8650
199 | Real-time | User Channel 5 Reactive Power | Q_s005_kvar | kvar | float32 | R | 8652
200 | Real-time | User Channel 5 Apparent Power | S_s005_kVA | kVA | float32 | R | 8654
201 | Real-time | User Channel 5 Power Factor | PF_s005 |  | float32 | R | 8658
202 | Real-time | User Channel 6 Current | I_s006_A | A | float32 | R | 8660
203 | Real-time | User Channel 6 Active Power | P_s006_kW | kW | float32 | R | 8662
204 | Real-time | User Channel 6 Reactive Power | Q_s006_kvar | kvar | float32 | R | 8664
205 | Real-time | User Channel 6 Apparent Power | S_s006_kVA | kVA | float32 | R | 8666
206 | Real-time | User Channel 6 Power Factor | PF_s006 |  | float32 | R | 8670
207 | Real-time | User Channel 7 Current | I_s007_A | A | float32 | R | 8672
208 | Real-time | User Channel 7 Active Power | P_s007_kW | kW | float32 | R | 8674
209 | Real-time | User Channel 7 Reactive Power | Q_s007_kvar | kvar | float32 | R | 8676
210 | Real-time | User Channel 7 Apparent Power | S_s007_kVA | kVA | float32 | R | 8678
211 | Real-time | User Channel 7 Power Factor | PF_s007 |  | float32 | R | 8682
212 | Real-time | User Channel 8 Current | I_s008_A | A | float32 | R | 8684
213 | Real-time | User Channel 8 Active Power | P_s008_kW | kW | float32 | R | 8686
214 | Real-time | User Channel 8 Reactive Power | Q_s008_kvar | kvar | float32 | R | 8688
215 | Real-time | User Channel 8 Apparent Power | S_s008_kVA | kVA | float32 | R | 8690
216 | Real-time | User Channel 8 Power Factor | PF_s008 |  | float32 | R | 8694
217 | Real-time | User Channel 9 Current | I_s009_A | A | float32 | R | 8696
218 | Real-time | User Channel 9 Active Power | P_s009_kW | kW | float32 | R | 8698
219 | Real-time | User Channel 9 Reactive Power | Q_s009_kvar | kvar | float32 | R | 8700
220 | Real-time | User Channel 9 Apparent Power | S_s009_kVA | kVA | float32 | R | 8702
221 | Real-time | User Channel 9 Power Factor | PF_s009 |  | float32 | R | 8706
222 | Real-time | User Channel 10 Current | I_s010_A | A | float32 | R | 8708
223 | Real-time | User Channel 10 Active Power | P_s010_kW | kW | float32 | R | 8710
224 | Real-time | User Channel 10 Reactive Power | Q_s010_kvar | kvar | float32 | R | 8712
225 | Real-time | User Channel 10 Apparent Power | S_s010_kVA | kVA | float32 | R | 8714
226 | Real-time | User Channel 10 Power Factor | PF_s010 |  | float32 | R | 8718
227 | Real-time | User Channel 11 Current | I_s011_A | A | float32 | R | 8720
228 | Real-time | User Channel 11 Active Power | P_s011_kW | kW | float32 | R | 8722
229 | Real-time | User Channel 11 Reactive Power | Q_s011_kvar | kvar | float32 | R | 8724
230 | Real-time | User Channel 11 Apparent Power | S_s011_kVA | kVA | float32 | R | 8726
231 | Real-time | User Channel 11 Power Factor | PF_s011 |  | float32 | R | 8730
232 | Real-time | User Channel 12 Current | I_s012_A | A | float32 | R | 8732
233 | Real-time | User Channel 12 Active Power | P_s012_kW | kW | float32 | R | 8734
234 | Real-time | User Channel 12 Reactive Power | Q_s012_kvar | kvar | float32 | R | 8736
235 | Real-time | User Channel 12 Apparent Power | S_s012_kVA | kVA | float32 | R | 8738
236 | Real-time | User Channel 12 Power Factor | PF_s012 |  | float32 | R | 8742
237 | Demand | Phase A Current Demand | DMD_I_a_A | A | float32 | R | 8960
238 | Demand | Phase A Import Active Power Demand | DMD_IMP_P_a_kW | kW | float32 | R | 8962
239 | Demand | Phase A Export Active Power Demand | DMD_EXP_P_a_kW | kW | float32 | R | 8964
240 | Demand | Phase A Import Reactive Power Demand | DMD_IMP_Q_a_kvar | kvar | float32 | R | 8966
241 | Demand | Phase A Export Reactive Power Demand | DMD_EXP_Q_a_kvar | kvar | float32 | R | 8968
242 | Demand | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA | float32 | R | 8970
243 | Demand | Phase B Current Demand | DMD_I_b_A | A | float32 | R | 8972
244 | Demand | Phase B Import Active Power Demand | DMD_IMP_P_b_kW | kW | float32 | R | 8974
245 | Demand | Phase B Export Active Power Demand | DMD_EXP_P_b_kW | kW | float32 | R | 8976
246 | Demand | Phase B Import Reactive Power Demand | DMD_IMP_Q_b_kvar | kvar | float32 | R | 8978
247 | Demand | Phase B Export Reactive Power Demand | DMD_EXP_Q_b_kvar | kvar | float32 | R | 8980
248 | Demand | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA | float32 | R | 8982
249 | Demand | Phase C Current Demand | DMD_I_c_A | A | float32 | R | 8984
250 | Demand | Phase C Import Active Power Demand | DMD_IMP_P_c_kW | kW | float32 | R | 8986
251 | Demand | Phase C Export Active Power Demand | DMD_EXP_P_c_kW | kW | float32 | R | 8988
252 | Demand | Phase C Import Reactive Power Demand | DMD_IMP_Q_c_kvar | kvar | float32 | R | 8990
253 | Demand | Phase C Export Reactive Power Demand | DMD_EXP_Q_c_kvar | kvar | float32 | R | 8992
254 | Demand | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA | float32 | R | 8994
255 | Demand | System Average Current Demand | DMD_I_avg_A | A | float32 | R | 8996
256 | Demand | System Import Active Power Demand | DMD_IMP_P_kW | kW | float32 | R | 8998
257 | Demand | System Export Active Power Demand | DMD_EXP_P_kW | kW | float32 | R | 9000
258 | Demand | System Import Reactive Power Demand | DMD_IMP_Q_kvar | kvar | float32 | R | 9002
259 | Demand | System Export Reactive Power Demand | DMD_EXP_Q_kvar | kvar | float32 | R | 9004
260 | Demand | System Apparent Power Demand | DMD_S_kVA | kVA | float32 | R | 9006
261 | Demand | Input Channel 1 Current Demand | DMD_I_001_A | A | float32 | R | 9008
262 | Demand | Input Channel 1 Import Active Power Demand | DMD_IMP_P_001_kW | kW | float32 | R | 9010
263 | Demand | Input Channel 1 Export Active Power Demand | DMD_EXP_P_001_kW | kW | float32 | R | 9012
264 | Demand | Input Channel 1 Import Reactive Power Demand | DMD_IMP_Q_001_kvar | kvar | float32 | R | 9014
265 | Demand | Input Channel 1 Export Reactive Power Demand | DMD_EXP_Q_001_kvar | kvar | float32 | R | 9016
266 | Demand | Input Channel 1 Apparent Power Demand | DMD_S_001_kVA | kVA | float32 | R | 9018
267 | Demand | Input Channel 2 Current Demand | DMD_I_002_A | A | float32 | R | 9020
268 | Demand | Input Channel 2 Import Active Power Demand | DMD_IMP_P_002_kW | kW | float32 | R | 9022
269 | Demand | Input Channel 2 Export Active Power Demand | DMD_EXP_P_002_kW | kW | float32 | R | 9024
270 | Demand | Input Channel 2 Import Reactive Power Demand | DMD_IMP_Q_002_kvar | kvar | float32 | R | 9026
271 | Demand | Input Channel 2 Export Reactive Power Demand | DMD_EXP_Q_002_kvar | kvar | float32 | R | 9028
272 | Demand | Input Channel 2 Apparent Power Demand | DMD_S_002_kVA | kVA | float32 | R | 9030
273 | Demand | Input Channel 3 Current Demand | DMD_I_003_A | A | float32 | R | 9032
274 | Demand | Input Channel 3 Import Active Power Demand | DMD_IMP_P_003_kW | kW | float32 | R | 9034
275 | Demand | Input Channel 3 Export Active Power Demand | DMD_EXP_P_003_kW | kW | float32 | R | 9036
276 | Demand | Input Channel 3 Import Reactive Power Demand | DMD_IMP_Q_003_kvar | kvar | float32 | R | 9038
277 | Demand | Input Channel 3 Export Reactive Power Demand | DMD_EXP_Q_003_kvar | kvar | float32 | R | 9040
278 | Demand | Input Channel 3 Apparent Power Demand | DMD_S_003_kVA | kVA | float32 | R | 9042
279 | Demand | Input Channel 4 Current Demand | DMD_I_004_A | A | float32 | R | 9044
280 | Demand | Input Channel 4 Import Active Power Demand | DMD_IMP_P_004_kW | kW | float32 | R | 9046
281 | Demand | Input Channel 4 Export Active Power Demand | DMD_EXP_P_004_kW | kW | float32 | R | 9048
282 | Demand | Input Channel 4 Import Reactive Power Demand | DMD_IMP_Q_004_kvar | kvar | float32 | R | 9050
283 | Demand | Input Channel 4 Export Reactive Power Demand | DMD_EXP_Q_004_kvar | kvar | float32 | R | 9052
284 | Demand | Input Channel 4 Apparent Power Demand | DMD_S_004_kVA | kVA | float32 | R | 9054
285 | Demand | Input Channel 5 Current Demand | DMD_I_005_A | A | float32 | R | 9056
286 | Demand | Input Channel 5 Import Active Power Demand | DMD_IMP_P_005_kW | kW | float32 | R | 9058
287 | Demand | Input Channel 5 Export Active Power Demand | DMD_EXP_P_005_kW | kW | float32 | R | 9060
288 | Demand | Input Channel 5 Import Reactive Power Demand | DMD_IMP_Q_005_kvar | kvar | float32 | R | 9062
289 | Demand | Input Channel 5 Export Reactive Power Demand | DMD_EXP_Q_005_kvar | kvar | float32 | R | 9064
290 | Demand | Input Channel 5 Apparent Power Demand | DMD_S_005_kVA | kVA | float32 | R | 9066
291 | Demand | Input Channel 6 Current Demand | DMD_I_006_A | A | float32 | R | 9068
292 | Demand | Input Channel 6 Import Active Power Demand | DMD_IMP_P_006_kW | kW | float32 | R | 9070
293 | Demand | Input Channel 6 Export Active Power Demand | DMD_EXP_P_006_kW | kW | float32 | R | 9072
294 | Demand | Input Channel 6 Import Reactive Power Demand | DMD_IMP_Q_006_kvar | kvar | float32 | R | 9074
295 | Demand | Input Channel 6 Export Reactive Power Demand | DMD_EXP_Q_006_kvar | kvar | float32 | R | 9076
296 | Demand | Input Channel 6 Apparent Power Demand | DMD_S_006_kVA | kVA | float32 | R | 9078
297 | Demand | Input Channel 7 Current Demand | DMD_I_007_A | A | float32 | R | 9080
298 | Demand | Input Channel 7 Import Active Power Demand | DMD_IMP_P_007_kW | kW | float32 | R | 9082
299 | Demand | Input Channel 7 Export Active Power Demand | DMD_EXP_P_007_kW | kW | float32 | R | 9084
300 | Demand | Input Channel 7 Import Reactive Power Demand | DMD_IMP_Q_007_kvar | kvar | float32 | R | 9086
301 | Demand | Input Channel 7 Export Reactive Power Demand | DMD_EXP_Q_007_kvar | kvar | float32 | R | 9088
302 | Demand | Input Channel 7 Apparent Power Demand | DMD_S_007_kVA | kVA | float32 | R | 9090
303 | Demand | Input Channel 8 Current Demand | DMD_I_008_A | A | float32 | R | 9092
304 | Demand | Input Channel 8 Import Active Power Demand | DMD_IMP_P_008_kW | kW | float32 | R | 9094
305 | Demand | Input Channel 8 Export Active Power Demand | DMD_EXP_P_008_kW | kW | float32 | R | 9096
306 | Demand | Input Channel 8 Import Reactive Power Demand | DMD_IMP_Q_008_kvar | kvar | float32 | R | 9098
307 | Demand | Input Channel 8 Export Reactive Power Demand | DMD_EXP_Q_008_kvar | kvar | float32 | R | 9100
308 | Demand | Input Channel 8 Apparent Power Demand | DMD_S_008_kVA | kVA | float32 | R | 9102
309 | Demand | Input Channel 9 Current Demand | DMD_I_009_A | A | float32 | R | 9104
310 | Demand | Input Channel 9 Import Active Power Demand | DMD_IMP_P_009_kW | kW | float32 | R | 9106
311 | Demand | Input Channel 9 Export Active Power Demand | DMD_EXP_P_009_kW | kW | float32 | R | 9108
312 | Demand | Input Channel 9 Import Reactive Power Demand | DMD_IMP_Q_009_kvar | kvar | float32 | R | 9110
313 | Demand | Input Channel 9 Export Reactive Power Demand | DMD_EXP_Q_009_kvar | kvar | float32 | R | 9112
314 | Demand | Input Channel 9 Apparent Power Demand | DMD_S_009_kVA | kVA | float32 | R | 9114
315 | Demand | Input Channel 10 Current Demand | DMD_I_010_A | A | float32 | R | 9116
316 | Demand | Input Channel 10 Import Active Power Demand | DMD_IMP_P_010_kW | kW | float32 | R | 9118
317 | Demand | Input Channel 10 Export Active Power Demand | DMD_EXP_P_010_kW | kW | float32 | R | 9120
318 | Demand | Input Channel 10 Import Reactive Power Demand | DMD_IMP_Q_010_kvar | kvar | float32 | R | 9122
319 | Demand | Input Channel 10 Export Reactive Power Demand | DMD_EXP_Q_010_kvar | kvar | float32 | R | 9124
320 | Demand | Input Channel 10 Apparent Power Demand | DMD_S_010_kVA | kVA | float32 | R | 9126
321 | Demand | Input Channel 11 Current Demand | DMD_I_011_A | A | float32 | R | 9128
322 | Demand | Input Channel 11 Import Active Power Demand | DMD_IMP_P_011_kW | kW | float32 | R | 9130
323 | Demand | Input Channel 11 Export Active Power Demand | DMD_EXP_P_011_kW | kW | float32 | R | 9132
324 | Demand | Input Channel 11 Import Reactive Power Demand | DMD_IMP_Q_011_kvar | kvar | float32 | R | 9134
325 | Demand | Input Channel 11 Export Reactive Power Demand | DMD_EXP_Q_011_kvar | kvar | float32 | R | 9136
326 | Demand | Input Channel 11 Apparent Power Demand | DMD_S_011_kVA | kVA | float32 | R | 9138
327 | Demand | Input Channel 12 Current Demand | DMD_I_012_A | A | float32 | R | 9140
328 | Demand | Input Channel 12 Import Active Power Demand | DMD_IMP_P_012_kW | kW | float32 | R | 9142
329 | Demand | Input Channel 12 Export Active Power Demand | DMD_EXP_P_012_kW | kW | float32 | R | 9144
330 | Demand | Input Channel 12 Import Reactive Power Demand | DMD_IMP_Q_012_kvar | kvar | float32 | R | 9146
331 | Demand | Input Channel 12 Export Reactive Power Demand | DMD_EXP_Q_012_kvar | kvar | float32 | R | 9148
332 | Demand | Input Channel 12 Apparent Power Demand | DMD_S_012_kVA | kVA | float32 | R | 9150
333 | Demand | Input Channel 13 Current Demand | DMD_I_013_A | A | float32 | R | 9152
334 | Demand | Input Channel 13 Import Active Power Demand | DMD_IMP_P_013_kW | kW | float32 | R | 9154
335 | Demand | Input Channel 13 Export Active Power Demand | DMD_EXP_P_013_kW | kW | float32 | R | 9156
336 | Demand | Input Channel 13 Import Reactive Power Demand | DMD_IMP_Q_013_kvar | kvar | float32 | R | 9158
337 | Demand | Input Channel 13 Export Reactive Power Demand | DMD_EXP_Q_013_kvar | kvar | float32 | R | 9160
338 | Demand | Input Channel 13 Apparent Power Demand | DMD_S_013_kVA | kVA | float32 | R | 9162
339 | Demand | Input Channel 14 Current Demand | DMD_I_014_A | A | float32 | R | 9164
340 | Demand | Input Channel 14 Import Active Power Demand | DMD_IMP_P_014_kW | kW | float32 | R | 9166
341 | Demand | Input Channel 14 Export Active Power Demand | DMD_EXP_P_014_kW | kW | float32 | R | 9168
342 | Demand | Input Channel 14 Import Reactive Power Demand | DMD_IMP_Q_014_kvar | kvar | float32 | R | 9170
343 | Demand | Input Channel 14 Export Reactive Power Demand | DMD_EXP_Q_014_kvar | kvar | float32 | R | 9172
344 | Demand | Input Channel 14 Apparent Power Demand | DMD_S_014_kVA | kVA | float32 | R | 9174
345 | Demand | Input Channel 15 Current Demand | DMD_I_015_A | A | float32 | R | 9176
346 | Demand | Input Channel 15 Import Active Power Demand | DMD_IMP_P_015_kW | kW | float32 | R | 9178
347 | Demand | Input Channel 15 Export Active Power Demand | DMD_EXP_P_015_kW | kW | float32 | R | 9180
348 | Demand | Input Channel 15 Import Reactive Power Demand | DMD_IMP_Q_015_kvar | kvar | float32 | R | 9182
349 | Demand | Input Channel 15 Export Reactive Power Demand | DMD_EXP_Q_015_kvar | kvar | float32 | R | 9184
350 | Demand | Input Channel 15 Apparent Power Demand | DMD_S_015_kVA | kVA | float32 | R | 9186
351 | Demand | Input Channel 16 Current Demand | DMD_I_016_A | A | float32 | R | 9188
352 | Demand | Input Channel 16 Import Active Power Demand | DMD_IMP_P_016_kW | kW | float32 | R | 9190
353 | Demand | Input Channel 16 Export Active Power Demand | DMD_EXP_P_016_kW | kW | float32 | R | 9192
354 | Demand | Input Channel 16 Import Reactive Power Demand | DMD_IMP_Q_016_kvar | kvar | float32 | R | 9194
355 | Demand | Input Channel 16 Export Reactive Power Demand | DMD_EXP_Q_016_kvar | kvar | float32 | R | 9196
356 | Demand | Input Channel 16 Apparent Power Demand | DMD_S_016_kVA | kVA | float32 | R | 9198
357 | Demand | Input Channel 17 Current Demand | DMD_I_017_A | A | float32 | R | 9200
358 | Demand | Input Channel 17 Import Active Power Demand | DMD_IMP_P_017_kW | kW | float32 | R | 9202
359 | Demand | Input Channel 17 Export Active Power Demand | DMD_EXP_P_017_kW | kW | float32 | R | 9204
360 | Demand | Input Channel 17 Import Reactive Power Demand | DMD_IMP_Q_017_kvar | kvar | float32 | R | 9206
361 | Demand | Input Channel 17 Export Reactive Power Demand | DMD_EXP_Q_017_kvar | kvar | float32 | R | 9208
362 | Demand | Input Channel 17 Apparent Power Demand | DMD_S_017_kVA | kVA | float32 | R | 9210
363 | Demand | Input Channel 18 Current Demand | DMD_I_018_A | A | float32 | R | 9212
364 | Demand | Input Channel 18 Import Active Power Demand | DMD_IMP_P_018_kW | kW | float32 | R | 9214
365 | Demand | Input Channel 18 Export Active Power Demand | DMD_EXP_P_018_kW | kW | float32 | R | 9216
366 | Demand | Input Channel 18 Import Reactive Power Demand | DMD_IMP_Q_018_kvar | kvar | float32 | R | 9218
367 | Demand | Input Channel 18 Export Reactive Power Demand | DMD_EXP_Q_018_kvar | kvar | float32 | R | 9220
368 | Demand | Input Channel 18 Apparent Power Demand | DMD_S_018_kVA | kVA | float32 | R | 9222
369 | Demand | Input Channel 19 Current Demand | DMD_I_019_A | A | float32 | R | 9224
370 | Demand | Input Channel 19 Import Active Power Demand | DMD_IMP_P_019_kW | kW | float32 | R | 9226
371 | Demand | Input Channel 19 Export Active Power Demand | DMD_EXP_P_019_kW | kW | float32 | R | 9228
372 | Demand | Input Channel 19 Import Reactive Power Demand | DMD_IMP_Q_019_kvar | kvar | float32 | R | 9230
373 | Demand | Input Channel 19 Export Reactive Power Demand | DMD_EXP_Q_019_kvar | kvar | float32 | R | 9232
374 | Demand | Input Channel 19 Apparent Power Demand | DMD_S_019_kVA | kVA | float32 | R | 9234
375 | Demand | Input Channel 20 Current Demand | DMD_I_020_A | A | float32 | R | 9236
376 | Demand | Input Channel 20 Import Active Power Demand | DMD_IMP_P_020_kW | kW | float32 | R | 9238
377 | Demand | Input Channel 20 Export Active Power Demand | DMD_EXP_P_020_kW | kW | float32 | R | 9240
378 | Demand | Input Channel 20 Import Reactive Power Demand | DMD_IMP_Q_020_kvar | kvar | float32 | R | 9242
379 | Demand | Input Channel 20 Export Reactive Power Demand | DMD_EXP_Q_020_kvar | kvar | float32 | R | 9244
380 | Demand | Input Channel 20 Apparent Power Demand | DMD_S_020_kVA | kVA | float32 | R | 9246
381 | Demand | Input Channel 21 Current Demand | DMD_I_021_A | A | float32 | R | 9248
382 | Demand | Input Channel 21 Import Active Power Demand | DMD_IMP_P_021_kW | kW | float32 | R | 9250
383 | Demand | Input Channel 21 Export Active Power Demand | DMD_EXP_P_021_kW | kW | float32 | R | 9252
384 | Demand | Input Channel 21 Import Reactive Power Demand | DMD_IMP_Q_021_kvar | kvar | float32 | R | 9254
385 | Demand | Input Channel 21 Export Reactive Power Demand | DMD_EXP_Q_021_kvar | kvar | float32 | R | 9256
386 | Demand | Input Channel 21 Apparent Power Demand | DMD_S_021_kVA | kVA | float32 | R | 9258
387 | Demand | Input Channel 22 Current Demand | DMD_I_022_A | A | float32 | R | 9260
388 | Demand | Input Channel 22 Import Active Power Demand | DMD_IMP_P_022_kW | kW | float32 | R | 9262
389 | Demand | Input Channel 22 Export Active Power Demand | DMD_EXP_P_022_kW | kW | float32 | R | 9264
390 | Demand | Input Channel 22 Import Reactive Power Demand | DMD_IMP_Q_022_kvar | kvar | float32 | R | 9266
391 | Demand | Input Channel 22 Export Reactive Power Demand | DMD_EXP_Q_022_kvar | kvar | float32 | R | 9268
392 | Demand | Input Channel 22 Apparent Power Demand | DMD_S_022_kVA | kVA | float32 | R | 9270
393 | Demand | Input Channel 23 Current Demand | DMD_I_023_A | A | float32 | R | 9272
394 | Demand | Input Channel 23 Import Active Power Demand | DMD_IMP_P_023_kW | kW | float32 | R | 9274
395 | Demand | Input Channel 23 Export Active Power Demand | DMD_EXP_P_023_kW | kW | float32 | R | 9276
396 | Demand | Input Channel 23 Import Reactive Power Demand | DMD_IMP_Q_023_kvar | kvar | float32 | R | 9278
397 | Demand | Input Channel 23 Export Reactive Power Demand | DMD_EXP_Q_023_kvar | kvar | float32 | R | 9280
398 | Demand | Input Channel 23 Apparent Power Demand | DMD_S_023_kVA | kVA | float32 | R | 9282
399 | Demand | Input Channel 24 Current Demand | DMD_I_024_A | A | float32 | R | 9284
400 | Demand | Input Channel 24 Import Active Power Demand | DMD_IMP_P_024_kW | kW | float32 | R | 9286
401 | Demand | Input Channel 24 Export Active Power Demand | DMD_EXP_P_024_kW | kW | float32 | R | 9288
402 | Demand | Input Channel 24 Import Reactive Power Demand | DMD_IMP_Q_024_kvar | kvar | float32 | R | 9290
403 | Demand | Input Channel 24 Export Reactive Power Demand | DMD_EXP_Q_024_kvar | kvar | float32 | R | 9292
404 | Demand | Input Channel 24 Apparent Power Demand | DMD_S_024_kVA | kVA | float32 | R | 9294
405 | Demand | User Channel 1 Current Demand | DMD_I_s001_A | A | float32 | R | 9296
406 | Demand | User Channel 1 Import Active Power Demand | DMD_IMP_P_s001_kW | kW | float32 | R | 9298
407 | Demand | User Channel 1 Export Active Power Demand | DMD_EXP_P_s001_kW | kW | float32 | R | 9300
408 | Demand | User Channel 1 Import Reactive Power Demand | DMD_IMP_Q_s001_kvar | kvar | float32 | R | 9302
409 | Demand | User Channel 1 Export Reactive Power Demand | DMD_EXP_Q_s001_kvar | kvar | float32 | R | 9304
410 | Demand | User Channel 1 Apparent Power Demand | DMD_S_s001_kVA | kVA | float32 | R | 9306
411 | Demand | User Channel 2 Current Demand | DMD_I_s002_A | A | float32 | R | 9308
412 | Demand | User Channel 2 Import Active Power Demand | DMD_IMP_P_s002_kW | kW | float32 | R | 9310
413 | Demand | User Channel 2 Export Active Power Demand | DMD_EXP_P_s002_kW | kW | float32 | R | 9312
414 | Demand | User Channel 2 Import Reactive Power Demand | DMD_IMP_Q_s002_kvar | kvar | float32 | R | 9314
415 | Demand | User Channel 2 Export Reactive Power Demand | DMD_EXP_Q_s002_kvar | kvar | float32 | R | 9316
416 | Demand | User Channel 2 Apparent Power Demand | DMD_S_s002_kVA | kVA | float32 | R | 9318
417 | Demand | User Channel 3 Current Demand | DMD_I_s003_A | A | float32 | R | 9320
418 | Demand | User Channel 3 Import Active Power Demand | DMD_IMP_P_s003_kW | kW | float32 | R | 9322
419 | Demand | User Channel 3 Export Active Power Demand | DMD_EXP_P_s003_kW | kW | float32 | R | 9324
420 | Demand | User Channel 3 Import Reactive Power Demand | DMD_IMP_Q_s003_kvar | kvar | float32 | R | 9326
421 | Demand | User Channel 3 Export Reactive Power Demand | DMD_EXP_Q_s003_kvar | kvar | float32 | R | 9328
422 | Demand | User Channel 3 Apparent Power Demand | DMD_S_s003_kVA | kVA | float32 | R | 9330
423 | Demand | User Channel 4 Current Demand | DMD_I_s004_A | A | float32 | R | 9332
424 | Demand | User Channel 4 Import Active Power Demand | DMD_IMP_P_s004_kW | kW | float32 | R | 9334
425 | Demand | User Channel 4 Export Active Power Demand | DMD_EXP_P_s004_kW | kW | float32 | R | 9336
426 | Demand | User Channel 4 Import Reactive Power Demand | DMD_IMP_Q_s004_kvar | kvar | float32 | R | 9338
427 | Demand | User Channel 4 Export Reactive Power Demand | DMD_EXP_Q_s004_kvar | kvar | float32 | R | 9340
428 | Demand | User Channel 4 Apparent Power Demand | DMD_S_s004_kVA | kVA | float32 | R | 9342
429 | Demand | User Channel 5 Current Demand | DMD_I_s005_A | A | float32 | R | 9344
430 | Demand | User Channel 5 Import Active Power Demand | DMD_IMP_P_s005_kW | kW | float32 | R | 9346
431 | Demand | User Channel 5 Export Active Power Demand | DMD_EXP_P_s005_kW | kW | float32 | R | 9348
432 | Demand | User Channel 5 Import Reactive Power Demand | DMD_IMP_Q_s005_kvar | kvar | float32 | R | 9350
433 | Demand | User Channel 5 Export Reactive Power Demand | DMD_EXP_Q_s005_kvar | kvar | float32 | R | 9352
434 | Demand | User Channel 5 Apparent Power Demand | DMD_S_s005_kVA | kVA | float32 | R | 9354
435 | Demand | User Channel 6 Current Demand | DMD_I_s006_A | A | float32 | R | 9356
436 | Demand | User Channel 6 Import Active Power Demand | DMD_IMP_P_s006_kW | kW | float32 | R | 9358
437 | Demand | User Channel 6 Export Active Power Demand | DMD_EXP_P_s006_kW | kW | float32 | R | 9360
438 | Demand | User Channel 6 Import Reactive Power Demand | DMD_IMP_Q_s006_kvar | kvar | float32 | R | 9362
439 | Demand | User Channel 6 Export Reactive Power Demand | DMD_EXP_Q_s006_kvar | kvar | float32 | R | 9364
440 | Demand | User Channel 6 Apparent Power Demand | DMD_S_s006_kVA | kVA | float32 | R | 9366
441 | Demand | User Channel 7 Current Demand | DMD_I_s007_A | A | float32 | R | 9368
442 | Demand | User Channel 7 Import Active Power Demand | DMD_IMP_P_s007_kW | kW | float32 | R | 9370
443 | Demand | User Channel 7 Export Active Power Demand | DMD_EXP_P_s007_kW | kW | float32 | R | 9372
444 | Demand | User Channel 7 Import Reactive Power Demand | DMD_IMP_Q_s007_kvar | kvar | float32 | R | 9374
445 | Demand | User Channel 7 Export Reactive Power Demand | DMD_EXP_Q_s007_kvar | kvar | float32 | R | 9376
446 | Demand | User Channel 7 Apparent Power Demand | DMD_S_s007_kVA | kVA | float32 | R | 9378
447 | Demand | User Channel 8 Current Demand | DMD_I_s008_A | A | float32 | R | 9380
448 | Demand | User Channel 8 Import Active Power Demand | DMD_IMP_P_s008_kW | kW | float32 | R | 9382
449 | Demand | User Channel 8 Export Active Power Demand | DMD_EXP_P_s008_kW | kW | float32 | R | 9384
450 | Demand | User Channel 8 Import Reactive Power Demand | DMD_IMP_Q_s008_kvar | kvar | float32 | R | 9386
451 | Demand | User Channel 8 Export Reactive Power Demand | DMD_EXP_Q_s008_kvar | kvar | float32 | R | 9388
452 | Demand | User Channel 8 Apparent Power Demand | DMD_S_s008_kVA | kVA | float32 | R | 9390
453 | Demand | User Channel 9 Current Demand | DMD_I_s009_A | A | float32 | R | 9392
454 | Demand | User Channel 9 Import Active Power Demand | DMD_IMP_P_s009_kW | kW | float32 | R | 9394
455 | Demand | User Channel 9 Export Active Power Demand | DMD_EXP_P_s009_kW | kW | float32 | R | 9396
456 | Demand | User Channel 9 Import Reactive Power Demand | DMD_IMP_Q_s009_kvar | kvar | float32 | R | 9398
457 | Demand | User Channel 9 Export Reactive Power Demand | DMD_EXP_Q_s009_kvar | kvar | float32 | R | 9400
458 | Demand | User Channel 9 Apparent Power Demand | DMD_S_s009_kVA | kVA | float32 | R | 9402
459 | Demand | User Channel 10 Current Demand | DMD_I_s010_A | A | float32 | R | 9404
460 | Demand | User Channel 10 Import Active Power Demand | DMD_IMP_P_s010_kW | kW | float32 | R | 9406
461 | Demand | User Channel 10 Export Active Power Demand | DMD_EXP_P_s010_kW | kW | float32 | R | 9408
462 | Demand | User Channel 10 Import Reactive Power Demand | DMD_IMP_Q_s010_kvar | kvar | float32 | R | 9410
463 | Demand | User Channel 10 Export Reactive Power Demand | DMD_EXP_Q_s010_kvar | kvar | float32 | R | 9412
464 | Demand | User Channel 10 Apparent Power Demand | DMD_S_s010_kVA | kVA | float32 | R | 9414
465 | Demand | User Channel 11 Current Demand | DMD_I_s011_A | A | float32 | R | 9416
466 | Demand | User Channel 11 Import Active Power Demand | DMD_IMP_P_s011_kW | kW | float32 | R | 9418
467 | Demand | User Channel 11 Export Active Power Demand | DMD_EXP_P_s011_kW | kW | float32 | R | 9420
468 | Demand | User Channel 11 Import Reactive Power Demand | DMD_IMP_Q_s011_kvar | kvar | float32 | R | 9422
469 | Demand | User Channel 11 Export Reactive Power Demand | DMD_EXP_Q_s011_kvar | kvar | float32 | R | 9424
470 | Demand | User Channel 11 Apparent Power Demand | DMD_S_s011_kVA | kVA | float32 | R | 9426
471 | Demand | User Channel 12 Current Demand | DMD_I_s012_A | A | float32 | R | 9428
472 | Demand | User Channel 12 Import Active Power Demand | DMD_IMP_P_s012_kW | kW | float32 | R | 9430
473 | Demand | User Channel 12 Export Active Power Demand | DMD_EXP_P_s012_kW | kW | float32 | R | 9432
474 | Demand | User Channel 12 Import Reactive Power Demand | DMD_IMP_Q_s012_kvar | kvar | float32 | R | 9434
475 | Demand | User Channel 12 Export Reactive Power Demand | DMD_EXP_Q_s012_kvar | kvar | float32 | R | 9436
476 | Demand | User Channel 12 Apparent Power Demand | DMD_S_s012_kVA | kVA | float32 | R | 9438
477 | Sequence | Voltage Positive Sequence Magnitude | MAG_SEQ_POS_V | V | float32 | R | 9728
478 | Sequence | Voltage Zero Sequence Magnitude | MAG_SEQ_ZERO_V | V | float32 | R | 9730
479 | Sequence | Voltage Negative Sequence Magnitude | MAG_SEQ_NEG_V | V | float32 | R | 9732
480 | Sequence | Voltage Positive Sequence Angle | ANG_SEQ_POS_V | ° | float32 | R | 9734
481 | Sequence | Voltage Zero Sequence Angle | ANG_SEQ_ZERO_V | ° | float32 | R | 9736
482 | Sequence | Voltage Negative Sequence Angle | ANG_SEQ_NEG_V | ° | float32 | R | 9738
483 | Sequence | Voltage Unbalance Factor Magnitude | UNBL_V_% | % | float32 | R | 9740
484 | THD | Phase A Voltage THD | THD_V_a_% | % | float32 | R | 9742
485 | THD | Phase A Voltage THD Odd | OTHD_V_a_% | % | float32 | R | 9744
486 | THD | Phase A Voltage THD Even | ETHD_V_a_% | % | float32 | R | 9746
487 | THD | Phase A Voltage Crest Factor | CF_V_a_% | % | float32 | R | 9748
488 | THD | Phase A Voltage THFF Factor | THFF_V_a_% | % | float32 | R | 9750
489 | Harmonics | Phase A Voltage individual Harmonics 2 percentage | HAR2_V_a_% | % | float32 | R | 9752
490 | Harmonics | Phase A Voltage individual Harmonics 3 percentage | HAR3_V_a_% | % | float32 | R | 9754
491 | Harmonics | Phase A Voltage individual Harmonics 4 percentage | HAR4_V_a_% | % | float32 | R | 9756
492 | Harmonics | Phase A Voltage individual Harmonics 5 percentage | HAR5_V_a_% | % | float32 | R | 9758
493 | Harmonics | Phase A Voltage individual Harmonics 6 percentage | HAR6_V_a_% | % | float32 | R | 9760
494 | Harmonics | Phase A Voltage individual Harmonics 7 percentage | HAR7_V_a_% | % | float32 | R | 9762
495 | Harmonics | Phase A Voltage individual Harmonics 8 percentage | HAR8_V_a_% | % | float32 | R | 9764
496 | Harmonics | Phase A Voltage individual Harmonics 9 percentage | HAR9_V_a_% | % | float32 | R | 9766
497 | Harmonics | Phase A Voltage individual Harmonics 10 percentage | HAR10_V_a_% | % | float32 | R | 9768
498 | Harmonics | Phase A Voltage individual Harmonics 11 percentage | HAR11_V_a_% | % | float32 | R | 9770
499 | Harmonics | Phase A Voltage individual Harmonics 12 percentage | HAR12_V_a_% | % | float32 | R | 9772
500 | Harmonics | Phase A Voltage individual Harmonics 13 percentage | HAR13_V_a_% | % | float32 | R | 9774
501 | Harmonics | Phase A Voltage individual Harmonics 14 percentage | HAR14_V_a_% | % | float32 | R | 9776
502 | Harmonics | Phase A Voltage individual Harmonics 15 percentage | HAR15_V_a_% | % | float32 | R | 9778
503 | Harmonics | Phase A Voltage individual Harmonics 16 percentage | HAR16_V_a_% | % | float32 | R | 9780
504 | Harmonics | Phase A Voltage individual Harmonics 17 percentage | HAR17_V_a_% | % | float32 | R | 9782
505 | Harmonics | Phase A Voltage individual Harmonics 18 percentage | HAR18_V_a_% | % | float32 | R | 9784
506 | Harmonics | Phase A Voltage individual Harmonics 19 percentage | HAR19_V_a_% | % | float32 | R | 9786
507 | Harmonics | Phase A Voltage individual Harmonics 20 percentage | HAR20_V_a_% | % | float32 | R | 9788
508 | Harmonics | Phase A Voltage individual Harmonics 21 percentage | HAR21_V_a_% | % | float32 | R | 9790
509 | Harmonics | Phase A Voltage individual Harmonics 22 percentage | HAR22_V_a_% | % | float32 | R | 9792
510 | Harmonics | Phase A Voltage individual Harmonics 23 percentage | HAR23_V_a_% | % | float32 | R | 9794
511 | Harmonics | Phase A Voltage individual Harmonics 24 percentage | HAR24_V_a_% | % | float32 | R | 9796
512 | Harmonics | Phase A Voltage individual Harmonics 25 percentage | HAR25_V_a_% | % | float32 | R | 9798
513 | Harmonics | Phase A Voltage individual Harmonics 26 percentage | HAR26_V_a_% | % | float32 | R | 9800
514 | Harmonics | Phase A Voltage individual Harmonics 27 percentage | HAR27_V_a_% | % | float32 | R | 9802
515 | Harmonics | Phase A Voltage individual Harmonics 28 percentage | HAR28_V_a_% | % | float32 | R | 9804
516 | Harmonics | Phase A Voltage individual Harmonics 29 percentage | HAR29_V_a_% | % | float32 | R | 9806
517 | Harmonics | Phase A Voltage individual Harmonics 30 percentage | HAR30_V_a_% | % | float32 | R | 9808
518 | Harmonics | Phase A Voltage individual Harmonics 31 percentage | HAR31_V_a_% | % | float32 | R | 9810
519 | THD | Phase B Voltage THD | THD_V_b_% | % | float32 | R | 9812
520 | THD | Phase B Voltage THD Odd | OTHD_V_b_% | % | float32 | R | 9814
521 | THD | Phase B Voltage THD Even | ETHD_V_b_% | % | float32 | R | 9816
522 | THD | Phase B Voltage Crest Factor | CF_V_b_% | % | float32 | R | 9818
523 | THD | Phase B Voltage THFF Factor | THFF_V_b_% | % | float32 | R | 9820
524 | Harmonics | Phase B Voltage individual Harmonics 2 percentage | HAR2_V_b_% | % | float32 | R | 9822
525 | Harmonics | Phase B Voltage individual Harmonics 3 percentage | HAR3_V_b_% | % | float32 | R | 9824
526 | Harmonics | Phase B Voltage individual Harmonics 4 percentage | HAR4_V_b_% | % | float32 | R | 9826
527 | Harmonics | Phase B Voltage individual Harmonics 5 percentage | HAR5_V_b_% | % | float32 | R | 9828
528 | Harmonics | Phase B Voltage individual Harmonics 6 percentage | HAR6_V_b_% | % | float32 | R | 9830
529 | Harmonics | Phase B Voltage individual Harmonics 7 percentage | HAR7_V_b_% | % | float32 | R | 9832
530 | Harmonics | Phase B Voltage individual Harmonics 8 percentage | HAR8_V_b_% | % | float32 | R | 9834
531 | Harmonics | Phase B Voltage individual Harmonics 9 percentage | HAR9_V_b_% | % | float32 | R | 9836
532 | Harmonics | Phase B Voltage individual Harmonics 10 percentage | HAR10_V_b_% | % | float32 | R | 9838
533 | Harmonics | Phase B Voltage individual Harmonics 11 percentage | HAR11_V_b_% | % | float32 | R | 9840
534 | Harmonics | Phase B Voltage individual Harmonics 12 percentage | HAR12_V_b_% | % | float32 | R | 9842
535 | Harmonics | Phase B Voltage individual Harmonics 13 percentage | HAR13_V_b_% | % | float32 | R | 9844
536 | Harmonics | Phase B Voltage individual Harmonics 14 percentage | HAR14_V_b_% | % | float32 | R | 9846
537 | Harmonics | Phase B Voltage individual Harmonics 15 percentage | HAR15_V_b_% | % | float32 | R | 9848
538 | Harmonics | Phase B Voltage individual Harmonics 16 percentage | HAR16_V_b_% | % | float32 | R | 9850
539 | Harmonics | Phase B Voltage individual Harmonics 17 percentage | HAR17_V_b_% | % | float32 | R | 9852
540 | Harmonics | Phase B Voltage individual Harmonics 18 percentage | HAR18_V_b_% | % | float32 | R | 9854
541 | Harmonics | Phase B Voltage individual Harmonics 19 percentage | HAR19_V_b_% | % | float32 | R | 9856
542 | Harmonics | Phase B Voltage individual Harmonics 20 percentage | HAR20_V_b_% | % | float32 | R | 9858
543 | Harmonics | Phase B Voltage individual Harmonics 21 percentage | HAR21_V_b_% | % | float32 | R | 9860
544 | Harmonics | Phase B Voltage individual Harmonics 22 percentage | HAR22_V_b_% | % | float32 | R | 9862
545 | Harmonics | Phase B Voltage individual Harmonics 23 percentage | HAR23_V_b_% | % | float32 | R | 9864
546 | Harmonics | Phase B Voltage individual Harmonics 24 percentage | HAR24_V_b_% | % | float32 | R | 9866
547 | Harmonics | Phase B Voltage individual Harmonics 25 percentage | HAR25_V_b_% | % | float32 | R | 9868
548 | Harmonics | Phase B Voltage individual Harmonics 26 percentage | HAR26_V_b_% | % | float32 | R | 9870
549 | Harmonics | Phase B Voltage individual Harmonics 27 percentage | HAR27_V_b_% | % | float32 | R | 9872
550 | Harmonics | Phase B Voltage individual Harmonics 28 percentage | HAR28_V_b_% | % | float32 | R | 9874
551 | Harmonics | Phase B Voltage individual Harmonics 29 percentage | HAR29_V_b_% | % | float32 | R | 9876
552 | Harmonics | Phase B Voltage individual Harmonics 30 percentage | HAR30_V_b_% | % | float32 | R | 9878
553 | Harmonics | Phase B Voltage individual Harmonics 31 percentage | HAR31_V_b_% | % | float32 | R | 9880
554 | THD | Phase C Voltage THD | THD_V_c_% | % | float32 | R | 9882
555 | THD | Phase C Voltage THD Odd | OTHD_V_c_% | % | float32 | R | 9884
556 | THD | Phase C Voltage THD Even | ETHD_V_c_% | % | float32 | R | 9886
557 | THD | Phase C Voltage Crest Factor | CF_V_c_% | % | float32 | R | 9888
558 | THD | Phase C Voltage THFF Factor | THFF_V_c_% | % | float32 | R | 9890
559 | Harmonics | Phase C Voltage individual Harmonics 2 percentage | HAR2_V_c_% | % | float32 | R | 9892
560 | Harmonics | Phase C Voltage individual Harmonics 3 percentage | HAR3_V_c_% | % | float32 | R | 9894
561 | Harmonics | Phase C Voltage individual Harmonics 4 percentage | HAR4_V_c_% | % | float32 | R | 9896
562 | Harmonics | Phase C Voltage individual Harmonics 5 percentage | HAR5_V_c_% | % | float32 | R | 9898
563 | Harmonics | Phase C Voltage individual Harmonics 6 percentage | HAR6_V_c_% | % | float32 | R | 9900
564 | Harmonics | Phase C Voltage individual Harmonics 7 percentage | HAR7_V_c_% | % | float32 | R | 9902
565 | Harmonics | Phase C Voltage individual Harmonics 8 percentage | HAR8_V_c_% | % | float32 | R | 9904
566 | Harmonics | Phase C Voltage individual Harmonics 9 percentage | HAR9_V_c_% | % | float32 | R | 9906
567 | Harmonics | Phase C Voltage individual Harmonics 10 percentage | HAR10_V_c_% | % | float32 | R | 9908
568 | Harmonics | Phase C Voltage individual Harmonics 11 percentage | HAR11_V_c_% | % | float32 | R | 9910
569 | Harmonics | Phase C Voltage individual Harmonics 12 percentage | HAR12_V_c_% | % | float32 | R | 9912
570 | Harmonics | Phase C Voltage individual Harmonics 13 percentage | HAR13_V_c_% | % | float32 | R | 9914
571 | Harmonics | Phase C Voltage individual Harmonics 14 percentage | HAR14_V_c_% | % | float32 | R | 9916
572 | Harmonics | Phase C Voltage individual Harmonics 15 percentage | HAR15_V_c_% | % | float32 | R | 9918
573 | Harmonics | Phase C Voltage individual Harmonics 16 percentage | HAR16_V_c_% | % | float32 | R | 9920
574 | Harmonics | Phase C Voltage individual Harmonics 17 percentage | HAR17_V_c_% | % | float32 | R | 9922
575 | Harmonics | Phase C Voltage individual Harmonics 18 percentage | HAR18_V_c_% | % | float32 | R | 9924
576 | Harmonics | Phase C Voltage individual Harmonics 19 percentage | HAR19_V_c_% | % | float32 | R | 9926
577 | Harmonics | Phase C Voltage individual Harmonics 20 percentage | HAR20_V_c_% | % | float32 | R | 9928
578 | Harmonics | Phase C Voltage individual Harmonics 21 percentage | HAR21_V_c_% | % | float32 | R | 9930
579 | Harmonics | Phase C Voltage individual Harmonics 22 percentage | HAR22_V_c_% | % | float32 | R | 9932
580 | Harmonics | Phase C Voltage individual Harmonics 23 percentage | HAR23_V_c_% | % | float32 | R | 9934
581 | Harmonics | Phase C Voltage individual Harmonics 24 percentage | HAR24_V_c_% | % | float32 | R | 9936
582 | Harmonics | Phase C Voltage individual Harmonics 25 percentage | HAR25_V_c_% | % | float32 | R | 9938
583 | Harmonics | Phase C Voltage individual Harmonics 26 percentage | HAR26_V_c_% | % | float32 | R | 9940
584 | Harmonics | Phase C Voltage individual Harmonics 27 percentage | HAR27_V_c_% | % | float32 | R | 9942
585 | Harmonics | Phase C Voltage individual Harmonics 28 percentage | HAR28_V_c_% | % | float32 | R | 9944
586 | Harmonics | Phase C Voltage individual Harmonics 29 percentage | HAR29_V_c_% | % | float32 | R | 9946
587 | Harmonics | Phase C Voltage individual Harmonics 30 percentage | HAR30_V_c_% | % | float32 | R | 9948
588 | Harmonics | Phase C Voltage individual Harmonics 31 percentage | HAR31_V_c_% | % | float32 | R | 9950
589 | THD | Average Voltage THD | THD_V_avg_% | % | float32 | R | 9952
590 | THD | Average Voltage THD Odd | OTHD_V_avg_% | % | float32 | R | 9954
591 | THD | Average Voltage THD Even | ETHD_V_avg_% | % | float32 | R | 9956
592 | THD | Input Channel 1 Current THD | THD_I_001_% | % | float32 | R | 9958
593 | THD | Input Channel 1 Current THD Odd | OTHD_I_001_% | % | float32 | R | 9960
594 | THD | Input Channel 1 Current THD Even | ETHD_I_001_% | % | float32 | R | 9962
595 | THD | Input Channel 1 Current K Factor | KF_I_001_% | % | float32 | R | 9964
596 | Harmonics | Input Channel 1 Current individual Harmonics 2 percentage | HAR2_I_001_% | % | float32 | R | 9966
597 | Harmonics | Input Channel 1 Current individual Harmonics 3 percentage | HAR3_I_001_% | % | float32 | R | 9968
598 | Harmonics | Input Channel 1 Current individual Harmonics 4 percentage | HAR4_I_001_% | % | float32 | R | 9970
599 | Harmonics | Input Channel 1 Current individual Harmonics 5 percentage | HAR5_I_001_% | % | float32 | R | 9972
600 | Harmonics | Input Channel 1 Current individual Harmonics 6 percentage | HAR6_I_001_% | % | float32 | R | 9974
601 | Harmonics | Input Channel 1 Current individual Harmonics 7 percentage | HAR7_I_001_% | % | float32 | R | 9976
602 | Harmonics | Input Channel 1 Current individual Harmonics 8 percentage | HAR8_I_001_% | % | float32 | R | 9978
603 | Harmonics | Input Channel 1 Current individual Harmonics 9 percentage | HAR9_I_001_% | % | float32 | R | 9980
604 | Harmonics | Input Channel 1 Current individual Harmonics 10 percentage | HAR10_I_001_% | % | float32 | R | 9982
605 | Harmonics | Input Channel 1 Current individual Harmonics 11 percentage | HAR11_I_001_% | % | float32 | R | 9984
606 | Harmonics | Input Channel 1 Current individual Harmonics 12 percentage | HAR12_I_001_% | % | float32 | R | 9986
607 | Harmonics | Input Channel 1 Current individual Harmonics 13 percentage | HAR13_I_001_% | % | float32 | R | 9988
608 | Harmonics | Input Channel 1 Current individual Harmonics 14 percentage | HAR14_I_001_% | % | float32 | R | 9990
609 | Harmonics | Input Channel 1 Current individual Harmonics 15 percentage | HAR15_I_001_% | % | float32 | R | 9992
610 | Harmonics | Input Channel 1 Current individual Harmonics 16 percentage | HAR16_I_001_% | % | float32 | R | 9994
611 | Harmonics | Input Channel 1 Current individual Harmonics 17 percentage | HAR17_I_001_% | % | float32 | R | 9996
612 | Harmonics | Input Channel 1 Current individual Harmonics 18 percentage | HAR18_I_001_% | % | float32 | R | 9998
613 | Harmonics | Input Channel 1 Current individual Harmonics 19 percentage | HAR19_I_001_% | % | float32 | R | 10000
614 | Harmonics | Input Channel 1 Current individual Harmonics 20 percentage | HAR20_I_001_% | % | float32 | R | 10002
615 | Harmonics | Input Channel 1 Current individual Harmonics 21 percentage | HAR21_I_001_% | % | float32 | R | 10004
616 | Harmonics | Input Channel 1 Current individual Harmonics 22 percentage | HAR22_I_001_% | % | float32 | R | 10006
617 | Harmonics | Input Channel 1 Current individual Harmonics 23 percentage | HAR23_I_001_% | % | float32 | R | 10008
618 | Harmonics | Input Channel 1 Current individual Harmonics 24 percentage | HAR24_I_001_% | % | float32 | R | 10010
619 | Harmonics | Input Channel 1 Current individual Harmonics 25 percentage | HAR25_I_001_% | % | float32 | R | 10012
620 | Harmonics | Input Channel 1 Current individual Harmonics 26 percentage | HAR26_I_001_% | % | float32 | R | 10014
621 | Harmonics | Input Channel 1 Current individual Harmonics 27 percentage | HAR27_I_001_% | % | float32 | R | 10016
622 | Harmonics | Input Channel 1 Current individual Harmonics 28 percentage | HAR28_I_001_% | % | float32 | R | 10018
623 | Harmonics | Input Channel 1 Current individual Harmonics 29 percentage | HAR29_I_001_% | % | float32 | R | 10020
624 | Harmonics | Input Channel 1 Current individual Harmonics 30 percentage | HAR30_I_001_% | % | float32 | R | 10022
625 | Harmonics | Input Channel 1 Current individual Harmonics 31 percentage | HAR31_I_001_% | % | float32 | R | 10024
626 | THD | Input Channel 2 Current THD | THD_I_002_% | % | float32 | R | 10026
627 | THD | Input Channel 2 Current THD Odd | OTHD_I_002_% | % | float32 | R | 10028
628 | THD | Input Channel 2 Current THD Even | ETHD_I_002_% | % | float32 | R | 10030
629 | THD | Input Channel 2 Current K Factor | KF_I_002_% | % | float32 | R | 10032
630 | Harmonics | Input Channel 2 Current individual Harmonics 2 percentage | HAR2_I_002_% | % | float32 | R | 10034
631 | Harmonics | Input Channel 2 Current individual Harmonics 3 percentage | HAR3_I_002_% | % | float32 | R | 10036
632 | Harmonics | Input Channel 2 Current individual Harmonics 4 percentage | HAR4_I_002_% | % | float32 | R | 10038
633 | Harmonics | Input Channel 2 Current individual Harmonics 5 percentage | HAR5_I_002_% | % | float32 | R | 10040
634 | Harmonics | Input Channel 2 Current individual Harmonics 6 percentage | HAR6_I_002_% | % | float32 | R | 10042
635 | Harmonics | Input Channel 2 Current individual Harmonics 7 percentage | HAR7_I_002_% | % | float32 | R | 10044
636 | Harmonics | Input Channel 2 Current individual Harmonics 8 percentage | HAR8_I_002_% | % | float32 | R | 10046
637 | Harmonics | Input Channel 2 Current individual Harmonics 9 percentage | HAR9_I_002_% | % | float32 | R | 10048
638 | Harmonics | Input Channel 2 Current individual Harmonics 10 percentage | HAR10_I_002_% | % | float32 | R | 10050
639 | Harmonics | Input Channel 2 Current individual Harmonics 11 percentage | HAR11_I_002_% | % | float32 | R | 10052
640 | Harmonics | Input Channel 2 Current individual Harmonics 12 percentage | HAR12_I_002_% | % | float32 | R | 10054
641 | Harmonics | Input Channel 2 Current individual Harmonics 13 percentage | HAR13_I_002_% | % | float32 | R | 10056
642 | Harmonics | Input Channel 2 Current individual Harmonics 14 percentage | HAR14_I_002_% | % | float32 | R | 10058
643 | Harmonics | Input Channel 2 Current individual Harmonics 15 percentage | HAR15_I_002_% | % | float32 | R | 10060
644 | Harmonics | Input Channel 2 Current individual Harmonics 16 percentage | HAR16_I_002_% | % | float32 | R | 10062
645 | Harmonics | Input Channel 2 Current individual Harmonics 17 percentage | HAR17_I_002_% | % | float32 | R | 10064
646 | Harmonics | Input Channel 2 Current individual Harmonics 18 percentage | HAR18_I_002_% | % | float32 | R | 10066
647 | Harmonics | Input Channel 2 Current individual Harmonics 19 percentage | HAR19_I_002_% | % | float32 | R | 10068
648 | Harmonics | Input Channel 2 Current individual Harmonics 20 percentage | HAR20_I_002_% | % | float32 | R | 10070
649 | Harmonics | Input Channel 2 Current individual Harmonics 21 percentage | HAR21_I_002_% | % | float32 | R | 10072
650 | Harmonics | Input Channel 2 Current individual Harmonics 22 percentage | HAR22_I_002_% | % | float32 | R | 10074
651 | Harmonics | Input Channel 2 Current individual Harmonics 23 percentage | HAR23_I_002_% | % | float32 | R | 10076
652 | Harmonics | Input Channel 2 Current individual Harmonics 24 percentage | HAR24_I_002_% | % | float32 | R | 10078
653 | Harmonics | Input Channel 2 Current individual Harmonics 25 percentage | HAR25_I_002_% | % | float32 | R | 10080
654 | Harmonics | Input Channel 2 Current individual Harmonics 26 percentage | HAR26_I_002_% | % | float32 | R | 10082
655 | Harmonics | Input Channel 2 Current individual Harmonics 27 percentage | HAR27_I_002_% | % | float32 | R | 10084
656 | Harmonics | Input Channel 2 Current individual Harmonics 28 percentage | HAR28_I_002_% | % | float32 | R | 10086
657 | Harmonics | Input Channel 2 Current individual Harmonics 29 percentage | HAR29_I_002_% | % | float32 | R | 10088
658 | Harmonics | Input Channel 2 Current individual Harmonics 30 percentage | HAR30_I_002_% | % | float32 | R | 10090
659 | Harmonics | Input Channel 2 Current individual Harmonics 31 percentage | HAR31_I_002_% | % | float32 | R | 10092
660 | THD | Input Channel 3 Current THD | THD_I_003_% | % | float32 | R | 10094
661 | THD | Input Channel 3 Current THD Odd | OTHD_I_003_% | % | float32 | R | 10096
662 | THD | Input Channel 3 Current THD Even | ETHD_I_003_% | % | float32 | R | 10098
663 | THD | Input Channel 3 Current K Factor | KF_I_003_% | % | float32 | R | 10100
664 | Harmonics | Input Channel 3 Current individual Harmonics 2 percentage | HAR2_I_003_% | % | float32 | R | 10102
665 | Harmonics | Input Channel 3 Current individual Harmonics 3 percentage | HAR3_I_003_% | % | float32 | R | 10104
666 | Harmonics | Input Channel 3 Current individual Harmonics 4 percentage | HAR4_I_003_% | % | float32 | R | 10106
667 | Harmonics | Input Channel 3 Current individual Harmonics 5 percentage | HAR5_I_003_% | % | float32 | R | 10108
668 | Harmonics | Input Channel 3 Current individual Harmonics 6 percentage | HAR6_I_003_% | % | float32 | R | 10110
669 | Harmonics | Input Channel 3 Current individual Harmonics 7 percentage | HAR7_I_003_% | % | float32 | R | 10112
670 | Harmonics | Input Channel 3 Current individual Harmonics 8 percentage | HAR8_I_003_% | % | float32 | R | 10114
671 | Harmonics | Input Channel 3 Current individual Harmonics 9 percentage | HAR9_I_003_% | % | float32 | R | 10116
672 | Harmonics | Input Channel 3 Current individual Harmonics 10 percentage | HAR10_I_003_% | % | float32 | R | 10118
673 | Harmonics | Input Channel 3 Current individual Harmonics 11 percentage | HAR11_I_003_% | % | float32 | R | 10120
674 | Harmonics | Input Channel 3 Current individual Harmonics 12 percentage | HAR12_I_003_% | % | float32 | R | 10122
675 | Harmonics | Input Channel 3 Current individual Harmonics 13 percentage | HAR13_I_003_% | % | float32 | R | 10124
676 | Harmonics | Input Channel 3 Current individual Harmonics 14 percentage | HAR14_I_003_% | % | float32 | R | 10126
677 | Harmonics | Input Channel 3 Current individual Harmonics 15 percentage | HAR15_I_003_% | % | float32 | R | 10128
678 | Harmonics | Input Channel 3 Current individual Harmonics 16 percentage | HAR16_I_003_% | % | float32 | R | 10130
679 | Harmonics | Input Channel 3 Current individual Harmonics 17 percentage | HAR17_I_003_% | % | float32 | R | 10132
680 | Harmonics | Input Channel 3 Current individual Harmonics 18 percentage | HAR18_I_003_% | % | float32 | R | 10134
681 | Harmonics | Input Channel 3 Current individual Harmonics 19 percentage | HAR19_I_003_% | % | float32 | R | 10136
682 | Harmonics | Input Channel 3 Current individual Harmonics 20 percentage | HAR20_I_003_% | % | float32 | R | 10138
683 | Harmonics | Input Channel 3 Current individual Harmonics 21 percentage | HAR21_I_003_% | % | float32 | R | 10140
684 | Harmonics | Input Channel 3 Current individual Harmonics 22 percentage | HAR22_I_003_% | % | float32 | R | 10142
685 | Harmonics | Input Channel 3 Current individual Harmonics 23 percentage | HAR23_I_003_% | % | float32 | R | 10144
686 | Harmonics | Input Channel 3 Current individual Harmonics 24 percentage | HAR24_I_003_% | % | float32 | R | 10146
687 | Harmonics | Input Channel 3 Current individual Harmonics 25 percentage | HAR25_I_003_% | % | float32 | R | 10148
688 | Harmonics | Input Channel 3 Current individual Harmonics 26 percentage | HAR26_I_003_% | % | float32 | R | 10150
689 | Harmonics | Input Channel 3 Current individual Harmonics 27 percentage | HAR27_I_003_% | % | float32 | R | 10152
690 | Harmonics | Input Channel 3 Current individual Harmonics 28 percentage | HAR28_I_003_% | % | float32 | R | 10154
691 | Harmonics | Input Channel 3 Current individual Harmonics 29 percentage | HAR29_I_003_% | % | float32 | R | 10156
692 | Harmonics | Input Channel 3 Current individual Harmonics 30 percentage | HAR30_I_003_% | % | float32 | R | 10158
693 | Harmonics | Input Channel 3 Current individual Harmonics 31 percentage | HAR31_I_003_% | % | float32 | R | 10160
694 | THD | Input Channel 4 Current THD | THD_I_004_% | % | float32 | R | 10162
695 | THD | Input Channel 4 Current THD Odd | OTHD_I_004_% | % | float32 | R | 10164
696 | THD | Input Channel 4 Current THD Even | ETHD_I_004_% | % | float32 | R | 10166
697 | THD | Input Channel 4 Current K Factor | KF_I_004_% | % | float32 | R | 10168
698 | Harmonics | Input Channel 4 Current individual Harmonics 2 percentage | HAR2_I_004_% | % | float32 | R | 10170
699 | Harmonics | Input Channel 4 Current individual Harmonics 3 percentage | HAR3_I_004_% | % | float32 | R | 10172
700 | Harmonics | Input Channel 4 Current individual Harmonics 4 percentage | HAR4_I_004_% | % | float32 | R | 10174
701 | Harmonics | Input Channel 4 Current individual Harmonics 5 percentage | HAR5_I_004_% | % | float32 | R | 10176
702 | Harmonics | Input Channel 4 Current individual Harmonics 6 percentage | HAR6_I_004_% | % | float32 | R | 10178
703 | Harmonics | Input Channel 4 Current individual Harmonics 7 percentage | HAR7_I_004_% | % | float32 | R | 10180
704 | Harmonics | Input Channel 4 Current individual Harmonics 8 percentage | HAR8_I_004_% | % | float32 | R | 10182
705 | Harmonics | Input Channel 4 Current individual Harmonics 9 percentage | HAR9_I_004_% | % | float32 | R | 10184
706 | Harmonics | Input Channel 4 Current individual Harmonics 10 percentage | HAR10_I_004_% | % | float32 | R | 10186
707 | Harmonics | Input Channel 4 Current individual Harmonics 11 percentage | HAR11_I_004_% | % | float32 | R | 10188
708 | Harmonics | Input Channel 4 Current individual Harmonics 12 percentage | HAR12_I_004_% | % | float32 | R | 10190
709 | Harmonics | Input Channel 4 Current individual Harmonics 13 percentage | HAR13_I_004_% | % | float32 | R | 10192
710 | Harmonics | Input Channel 4 Current individual Harmonics 14 percentage | HAR14_I_004_% | % | float32 | R | 10194
711 | Harmonics | Input Channel 4 Current individual Harmonics 15 percentage | HAR15_I_004_% | % | float32 | R | 10196
712 | Harmonics | Input Channel 4 Current individual Harmonics 16 percentage | HAR16_I_004_% | % | float32 | R | 10198
713 | Harmonics | Input Channel 4 Current individual Harmonics 17 percentage | HAR17_I_004_% | % | float32 | R | 10200
714 | Harmonics | Input Channel 4 Current individual Harmonics 18 percentage | HAR18_I_004_% | % | float32 | R | 10202
715 | Harmonics | Input Channel 4 Current individual Harmonics 19 percentage | HAR19_I_004_% | % | float32 | R | 10204
716 | Harmonics | Input Channel 4 Current individual Harmonics 20 percentage | HAR20_I_004_% | % | float32 | R | 10206
717 | Harmonics | Input Channel 4 Current individual Harmonics 21 percentage | HAR21_I_004_% | % | float32 | R | 10208
718 | Harmonics | Input Channel 4 Current individual Harmonics 22 percentage | HAR22_I_004_% | % | float32 | R | 10210
719 | Harmonics | Input Channel 4 Current individual Harmonics 23 percentage | HAR23_I_004_% | % | float32 | R | 10212
720 | Harmonics | Input Channel 4 Current individual Harmonics 24 percentage | HAR24_I_004_% | % | float32 | R | 10214
721 | Harmonics | Input Channel 4 Current individual Harmonics 25 percentage | HAR25_I_004_% | % | float32 | R | 10216
722 | Harmonics | Input Channel 4 Current individual Harmonics 26 percentage | HAR26_I_004_% | % | float32 | R | 10218
723 | Harmonics | Input Channel 4 Current individual Harmonics 27 percentage | HAR27_I_004_% | % | float32 | R | 10220
724 | Harmonics | Input Channel 4 Current individual Harmonics 28 percentage | HAR28_I_004_% | % | float32 | R | 10222
725 | Harmonics | Input Channel 4 Current individual Harmonics 29 percentage | HAR29_I_004_% | % | float32 | R | 10224
726 | Harmonics | Input Channel 4 Current individual Harmonics 30 percentage | HAR30_I_004_% | % | float32 | R | 10226
727 | Harmonics | Input Channel 4 Current individual Harmonics 31 percentage | HAR31_I_004_% | % | float32 | R | 10228
728 | THD | Input Channel 5 Current THD | THD_I_005_% | % | float32 | R | 10230
729 | THD | Input Channel 5 Current THD Odd | OTHD_I_005_% | % | float32 | R | 10232
730 | THD | Input Channel 5 Current THD Even | ETHD_I_005_% | % | float32 | R | 10234
731 | THD | Input Channel 5 Current K Factor | KF_I_005_% | % | float32 | R | 10236
732 | Harmonics | Input Channel 5 Current individual Harmonics 2 percentage | HAR2_I_005_% | % | float32 | R | 10238
733 | Harmonics | Input Channel 5 Current individual Harmonics 3 percentage | HAR3_I_005_% | % | float32 | R | 10240
734 | Harmonics | Input Channel 5 Current individual Harmonics 4 percentage | HAR4_I_005_% | % | float32 | R | 10242
735 | Harmonics | Input Channel 5 Current individual Harmonics 5 percentage | HAR5_I_005_% | % | float32 | R | 10244
736 | Harmonics | Input Channel 5 Current individual Harmonics 6 percentage | HAR6_I_005_% | % | float32 | R | 10246
737 | Harmonics | Input Channel 5 Current individual Harmonics 7 percentage | HAR7_I_005_% | % | float32 | R | 10248
738 | Harmonics | Input Channel 5 Current individual Harmonics 8 percentage | HAR8_I_005_% | % | float32 | R | 10250
739 | Harmonics | Input Channel 5 Current individual Harmonics 9 percentage | HAR9_I_005_% | % | float32 | R | 10252
740 | Harmonics | Input Channel 5 Current individual Harmonics 10 percentage | HAR10_I_005_% | % | float32 | R | 10254
741 | Harmonics | Input Channel 5 Current individual Harmonics 11 percentage | HAR11_I_005_% | % | float32 | R | 10256
742 | Harmonics | Input Channel 5 Current individual Harmonics 12 percentage | HAR12_I_005_% | % | float32 | R | 10258
743 | Harmonics | Input Channel 5 Current individual Harmonics 13 percentage | HAR13_I_005_% | % | float32 | R | 10260
744 | Harmonics | Input Channel 5 Current individual Harmonics 14 percentage | HAR14_I_005_% | % | float32 | R | 10262
745 | Harmonics | Input Channel 5 Current individual Harmonics 15 percentage | HAR15_I_005_% | % | float32 | R | 10264
746 | Harmonics | Input Channel 5 Current individual Harmonics 16 percentage | HAR16_I_005_% | % | float32 | R | 10266
747 | Harmonics | Input Channel 5 Current individual Harmonics 17 percentage | HAR17_I_005_% | % | float32 | R | 10268
748 | Harmonics | Input Channel 5 Current individual Harmonics 18 percentage | HAR18_I_005_% | % | float32 | R | 10270
749 | Harmonics | Input Channel 5 Current individual Harmonics 19 percentage | HAR19_I_005_% | % | float32 | R | 10272
750 | Harmonics | Input Channel 5 Current individual Harmonics 20 percentage | HAR20_I_005_% | % | float32 | R | 10274
751 | Harmonics | Input Channel 5 Current individual Harmonics 21 percentage | HAR21_I_005_% | % | float32 | R | 10276
752 | Harmonics | Input Channel 5 Current individual Harmonics 22 percentage | HAR22_I_005_% | % | float32 | R | 10278
753 | Harmonics | Input Channel 5 Current individual Harmonics 23 percentage | HAR23_I_005_% | % | float32 | R | 10280
754 | Harmonics | Input Channel 5 Current individual Harmonics 24 percentage | HAR24_I_005_% | % | float32 | R | 10282
755 | Harmonics | Input Channel 5 Current individual Harmonics 25 percentage | HAR25_I_005_% | % | float32 | R | 10284
756 | Harmonics | Input Channel 5 Current individual Harmonics 26 percentage | HAR26_I_005_% | % | float32 | R | 10286
757 | Harmonics | Input Channel 5 Current individual Harmonics 27 percentage | HAR27_I_005_% | % | float32 | R | 10288
758 | Harmonics | Input Channel 5 Current individual Harmonics 28 percentage | HAR28_I_005_% | % | float32 | R | 10290
759 | Harmonics | Input Channel 5 Current individual Harmonics 29 percentage | HAR29_I_005_% | % | float32 | R | 10292
760 | Harmonics | Input Channel 5 Current individual Harmonics 30 percentage | HAR30_I_005_% | % | float32 | R | 10294
761 | Harmonics | Input Channel 5 Current individual Harmonics 31 percentage | HAR31_I_005_% | % | float32 | R | 10296
762 | THD | Input Channel 6 Current THD | THD_I_006_% | % | float32 | R | 10298
763 | THD | Input Channel 6 Current THD Odd | OTHD_I_006_% | % | float32 | R | 10300
764 | THD | Input Channel 6 Current THD Even | ETHD_I_006_% | % | float32 | R | 10302
765 | THD | Input Channel 6 Current K Factor | KF_I_006_% | % | float32 | R | 10304
766 | Harmonics | Input Channel 6 Current individual Harmonics 2 percentage | HAR2_I_006_% | % | float32 | R | 10306
767 | Harmonics | Input Channel 6 Current individual Harmonics 3 percentage | HAR3_I_006_% | % | float32 | R | 10308
768 | Harmonics | Input Channel 6 Current individual Harmonics 4 percentage | HAR4_I_006_% | % | float32 | R | 10310
769 | Harmonics | Input Channel 6 Current individual Harmonics 5 percentage | HAR5_I_006_% | % | float32 | R | 10312
770 | Harmonics | Input Channel 6 Current individual Harmonics 6 percentage | HAR6_I_006_% | % | float32 | R | 10314
771 | Harmonics | Input Channel 6 Current individual Harmonics 7 percentage | HAR7_I_006_% | % | float32 | R | 10316
772 | Harmonics | Input Channel 6 Current individual Harmonics 8 percentage | HAR8_I_006_% | % | float32 | R | 10318
773 | Harmonics | Input Channel 6 Current individual Harmonics 9 percentage | HAR9_I_006_% | % | float32 | R | 10320
774 | Harmonics | Input Channel 6 Current individual Harmonics 10 percentage | HAR10_I_006_% | % | float32 | R | 10322
775 | Harmonics | Input Channel 6 Current individual Harmonics 11 percentage | HAR11_I_006_% | % | float32 | R | 10324
776 | Harmonics | Input Channel 6 Current individual Harmonics 12 percentage | HAR12_I_006_% | % | float32 | R | 10326
777 | Harmonics | Input Channel 6 Current individual Harmonics 13 percentage | HAR13_I_006_% | % | float32 | R | 10328
778 | Harmonics | Input Channel 6 Current individual Harmonics 14 percentage | HAR14_I_006_% | % | float32 | R | 10330
779 | Harmonics | Input Channel 6 Current individual Harmonics 15 percentage | HAR15_I_006_% | % | float32 | R | 10332
780 | Harmonics | Input Channel 6 Current individual Harmonics 16 percentage | HAR16_I_006_% | % | float32 | R | 10334
781 | Harmonics | Input Channel 6 Current individual Harmonics 17 percentage | HAR17_I_006_% | % | float32 | R | 10336
782 | Harmonics | Input Channel 6 Current individual Harmonics 18 percentage | HAR18_I_006_% | % | float32 | R | 10338
783 | Harmonics | Input Channel 6 Current individual Harmonics 19 percentage | HAR19_I_006_% | % | float32 | R | 10340
784 | Harmonics | Input Channel 6 Current individual Harmonics 20 percentage | HAR20_I_006_% | % | float32 | R | 10342
785 | Harmonics | Input Channel 6 Current individual Harmonics 21 percentage | HAR21_I_006_% | % | float32 | R | 10344
786 | Harmonics | Input Channel 6 Current individual Harmonics 22 percentage | HAR22_I_006_% | % | float32 | R | 10346
787 | Harmonics | Input Channel 6 Current individual Harmonics 23 percentage | HAR23_I_006_% | % | float32 | R | 10348
788 | Harmonics | Input Channel 6 Current individual Harmonics 24 percentage | HAR24_I_006_% | % | float32 | R | 10350
789 | Harmonics | Input Channel 6 Current individual Harmonics 25 percentage | HAR25_I_006_% | % | float32 | R | 10352
790 | Harmonics | Input Channel 6 Current individual Harmonics 26 percentage | HAR26_I_006_% | % | float32 | R | 10354
791 | Harmonics | Input Channel 6 Current individual Harmonics 27 percentage | HAR27_I_006_% | % | float32 | R | 10356
792 | Harmonics | Input Channel 6 Current individual Harmonics 28 percentage | HAR28_I_006_% | % | float32 | R | 10358
793 | Harmonics | Input Channel 6 Current individual Harmonics 29 percentage | HAR29_I_006_% | % | float32 | R | 10360
794 | Harmonics | Input Channel 6 Current individual Harmonics 30 percentage | HAR30_I_006_% | % | float32 | R | 10362
795 | Harmonics | Input Channel 6 Current individual Harmonics 31 percentage | HAR31_I_006_% | % | float32 | R | 10364
796 | THD | Input Channel 7 Current THD | THD_I_007_% | % | float32 | R | 10366
797 | THD | Input Channel 7 Current THD Odd | OTHD_I_007_% | % | float32 | R | 10368
798 | THD | Input Channel 7 Current THD Even | ETHD_I_007_% | % | float32 | R | 10370
799 | THD | Input Channel 7 Current K Factor | KF_I_007_% | % | float32 | R | 10372
800 | Harmonics | Input Channel 7 Current individual Harmonics 2 percentage | HAR2_I_007_% | % | float32 | R | 10374
801 | Harmonics | Input Channel 7 Current individual Harmonics 3 percentage | HAR3_I_007_% | % | float32 | R | 10376
802 | Harmonics | Input Channel 7 Current individual Harmonics 4 percentage | HAR4_I_007_% | % | float32 | R | 10378
803 | Harmonics | Input Channel 7 Current individual Harmonics 5 percentage | HAR5_I_007_% | % | float32 | R | 10380
804 | Harmonics | Input Channel 7 Current individual Harmonics 6 percentage | HAR6_I_007_% | % | float32 | R | 10382
805 | Harmonics | Input Channel 7 Current individual Harmonics 7 percentage | HAR7_I_007_% | % | float32 | R | 10384
806 | Harmonics | Input Channel 7 Current individual Harmonics 8 percentage | HAR8_I_007_% | % | float32 | R | 10386
807 | Harmonics | Input Channel 7 Current individual Harmonics 9 percentage | HAR9_I_007_% | % | float32 | R | 10388
808 | Harmonics | Input Channel 7 Current individual Harmonics 10 percentage | HAR10_I_007_% | % | float32 | R | 10390
809 | Harmonics | Input Channel 7 Current individual Harmonics 11 percentage | HAR11_I_007_% | % | float32 | R | 10392
810 | Harmonics | Input Channel 7 Current individual Harmonics 12 percentage | HAR12_I_007_% | % | float32 | R | 10394
811 | Harmonics | Input Channel 7 Current individual Harmonics 13 percentage | HAR13_I_007_% | % | float32 | R | 10396
812 | Harmonics | Input Channel 7 Current individual Harmonics 14 percentage | HAR14_I_007_% | % | float32 | R | 10398
813 | Harmonics | Input Channel 7 Current individual Harmonics 15 percentage | HAR15_I_007_% | % | float32 | R | 10400
814 | Harmonics | Input Channel 7 Current individual Harmonics 16 percentage | HAR16_I_007_% | % | float32 | R | 10402
815 | Harmonics | Input Channel 7 Current individual Harmonics 17 percentage | HAR17_I_007_% | % | float32 | R | 10404
816 | Harmonics | Input Channel 7 Current individual Harmonics 18 percentage | HAR18_I_007_% | % | float32 | R | 10406
817 | Harmonics | Input Channel 7 Current individual Harmonics 19 percentage | HAR19_I_007_% | % | float32 | R | 10408
818 | Harmonics | Input Channel 7 Current individual Harmonics 20 percentage | HAR20_I_007_% | % | float32 | R | 10410
819 | Harmonics | Input Channel 7 Current individual Harmonics 21 percentage | HAR21_I_007_% | % | float32 | R | 10412
820 | Harmonics | Input Channel 7 Current individual Harmonics 22 percentage | HAR22_I_007_% | % | float32 | R | 10414
821 | Harmonics | Input Channel 7 Current individual Harmonics 23 percentage | HAR23_I_007_% | % | float32 | R | 10416
822 | Harmonics | Input Channel 7 Current individual Harmonics 24 percentage | HAR24_I_007_% | % | float32 | R | 10418
823 | Harmonics | Input Channel 7 Current individual Harmonics 25 percentage | HAR25_I_007_% | % | float32 | R | 10420
824 | Harmonics | Input Channel 7 Current individual Harmonics 26 percentage | HAR26_I_007_% | % | float32 | R | 10422
825 | Harmonics | Input Channel 7 Current individual Harmonics 27 percentage | HAR27_I_007_% | % | float32 | R | 10424
826 | Harmonics | Input Channel 7 Current individual Harmonics 28 percentage | HAR28_I_007_% | % | float32 | R | 10426
827 | Harmonics | Input Channel 7 Current individual Harmonics 29 percentage | HAR29_I_007_% | % | float32 | R | 10428
828 | Harmonics | Input Channel 7 Current individual Harmonics 30 percentage | HAR30_I_007_% | % | float32 | R | 10430
829 | Harmonics | Input Channel 7 Current individual Harmonics 31 percentage | HAR31_I_007_% | % | float32 | R | 10432
830 | THD | Input Channel 8 Current THD | THD_I_008_% | % | float32 | R | 10434
831 | THD | Input Channel 8 Current THD Odd | OTHD_I_008_% | % | float32 | R | 10436
832 | THD | Input Channel 8 Current THD Even | ETHD_I_008_% | % | float32 | R | 10438
833 | THD | Input Channel 8 Current K Factor | KF_I_008_% | % | float32 | R | 10440
834 | Harmonics | Input Channel 8 Current individual Harmonics 2 percentage | HAR2_I_008_% | % | float32 | R | 10442
835 | Harmonics | Input Channel 8 Current individual Harmonics 3 percentage | HAR3_I_008_% | % | float32 | R | 10444
836 | Harmonics | Input Channel 8 Current individual Harmonics 4 percentage | HAR4_I_008_% | % | float32 | R | 10446
837 | Harmonics | Input Channel 8 Current individual Harmonics 5 percentage | HAR5_I_008_% | % | float32 | R | 10448
838 | Harmonics | Input Channel 8 Current individual Harmonics 6 percentage | HAR6_I_008_% | % | float32 | R | 10450
839 | Harmonics | Input Channel 8 Current individual Harmonics 7 percentage | HAR7_I_008_% | % | float32 | R | 10452
840 | Harmonics | Input Channel 8 Current individual Harmonics 8 percentage | HAR8_I_008_% | % | float32 | R | 10454
841 | Harmonics | Input Channel 8 Current individual Harmonics 9 percentage | HAR9_I_008_% | % | float32 | R | 10456
842 | Harmonics | Input Channel 8 Current individual Harmonics 10 percentage | HAR10_I_008_% | % | float32 | R | 10458
843 | Harmonics | Input Channel 8 Current individual Harmonics 11 percentage | HAR11_I_008_% | % | float32 | R | 10460
844 | Harmonics | Input Channel 8 Current individual Harmonics 12 percentage | HAR12_I_008_% | % | float32 | R | 10462
845 | Harmonics | Input Channel 8 Current individual Harmonics 13 percentage | HAR13_I_008_% | % | float32 | R | 10464
846 | Harmonics | Input Channel 8 Current individual Harmonics 14 percentage | HAR14_I_008_% | % | float32 | R | 10466
847 | Harmonics | Input Channel 8 Current individual Harmonics 15 percentage | HAR15_I_008_% | % | float32 | R | 10468
848 | Harmonics | Input Channel 8 Current individual Harmonics 16 percentage | HAR16_I_008_% | % | float32 | R | 10470
849 | Harmonics | Input Channel 8 Current individual Harmonics 17 percentage | HAR17_I_008_% | % | float32 | R | 10472
850 | Harmonics | Input Channel 8 Current individual Harmonics 18 percentage | HAR18_I_008_% | % | float32 | R | 10474
851 | Harmonics | Input Channel 8 Current individual Harmonics 19 percentage | HAR19_I_008_% | % | float32 | R | 10476
852 | Harmonics | Input Channel 8 Current individual Harmonics 20 percentage | HAR20_I_008_% | % | float32 | R | 10478
853 | Harmonics | Input Channel 8 Current individual Harmonics 21 percentage | HAR21_I_008_% | % | float32 | R | 10480
854 | Harmonics | Input Channel 8 Current individual Harmonics 22 percentage | HAR22_I_008_% | % | float32 | R | 10482
855 | Harmonics | Input Channel 8 Current individual Harmonics 23 percentage | HAR23_I_008_% | % | float32 | R | 10484
856 | Harmonics | Input Channel 8 Current individual Harmonics 24 percentage | HAR24_I_008_% | % | float32 | R | 10486
857 | Harmonics | Input Channel 8 Current individual Harmonics 25 percentage | HAR25_I_008_% | % | float32 | R | 10488
858 | Harmonics | Input Channel 8 Current individual Harmonics 26 percentage | HAR26_I_008_% | % | float32 | R | 10490
859 | Harmonics | Input Channel 8 Current individual Harmonics 27 percentage | HAR27_I_008_% | % | float32 | R | 10492
860 | Harmonics | Input Channel 8 Current individual Harmonics 28 percentage | HAR28_I_008_% | % | float32 | R | 10494
861 | Harmonics | Input Channel 8 Current individual Harmonics 29 percentage | HAR29_I_008_% | % | float32 | R | 10496
862 | Harmonics | Input Channel 8 Current individual Harmonics 30 percentage | HAR30_I_008_% | % | float32 | R | 10498
863 | Harmonics | Input Channel 8 Current individual Harmonics 31 percentage | HAR31_I_008_% | % | float32 | R | 10500
864 | THD | Input Channel 9 Current THD | THD_I_009_% | % | float32 | R | 10502
865 | THD | Input Channel 9 Current THD Odd | OTHD_I_009_% | % | float32 | R | 10504
866 | THD | Input Channel 9 Current THD Even | ETHD_I_009_% | % | float32 | R | 10506
867 | THD | Input Channel 9 Current K Factor | KF_I_009_% | % | float32 | R | 10508
868 | Harmonics | Input Channel 9 Current individual Harmonics 2 percentage | HAR2_I_009_% | % | float32 | R | 10510
869 | Harmonics | Input Channel 9 Current individual Harmonics 3 percentage | HAR3_I_009_% | % | float32 | R | 10512
870 | Harmonics | Input Channel 9 Current individual Harmonics 4 percentage | HAR4_I_009_% | % | float32 | R | 10514
871 | Harmonics | Input Channel 9 Current individual Harmonics 5 percentage | HAR5_I_009_% | % | float32 | R | 10516
872 | Harmonics | Input Channel 9 Current individual Harmonics 6 percentage | HAR6_I_009_% | % | float32 | R | 10518
873 | Harmonics | Input Channel 9 Current individual Harmonics 7 percentage | HAR7_I_009_% | % | float32 | R | 10520
874 | Harmonics | Input Channel 9 Current individual Harmonics 8 percentage | HAR8_I_009_% | % | float32 | R | 10522
875 | Harmonics | Input Channel 9 Current individual Harmonics 9 percentage | HAR9_I_009_% | % | float32 | R | 10524
876 | Harmonics | Input Channel 9 Current individual Harmonics 10 percentage | HAR10_I_009_% | % | float32 | R | 10526
877 | Harmonics | Input Channel 9 Current individual Harmonics 11 percentage | HAR11_I_009_% | % | float32 | R | 10528
878 | Harmonics | Input Channel 9 Current individual Harmonics 12 percentage | HAR12_I_009_% | % | float32 | R | 10530
879 | Harmonics | Input Channel 9 Current individual Harmonics 13 percentage | HAR13_I_009_% | % | float32 | R | 10532
880 | Harmonics | Input Channel 9 Current individual Harmonics 14 percentage | HAR14_I_009_% | % | float32 | R | 10534
881 | Harmonics | Input Channel 9 Current individual Harmonics 15 percentage | HAR15_I_009_% | % | float32 | R | 10536
882 | Harmonics | Input Channel 9 Current individual Harmonics 16 percentage | HAR16_I_009_% | % | float32 | R | 10538
883 | Harmonics | Input Channel 9 Current individual Harmonics 17 percentage | HAR17_I_009_% | % | float32 | R | 10540
884 | Harmonics | Input Channel 9 Current individual Harmonics 18 percentage | HAR18_I_009_% | % | float32 | R | 10542
885 | Harmonics | Input Channel 9 Current individual Harmonics 19 percentage | HAR19_I_009_% | % | float32 | R | 10544
886 | Harmonics | Input Channel 9 Current individual Harmonics 20 percentage | HAR20_I_009_% | % | float32 | R | 10546
887 | Harmonics | Input Channel 9 Current individual Harmonics 21 percentage | HAR21_I_009_% | % | float32 | R | 10548
888 | Harmonics | Input Channel 9 Current individual Harmonics 22 percentage | HAR22_I_009_% | % | float32 | R | 10550
889 | Harmonics | Input Channel 9 Current individual Harmonics 23 percentage | HAR23_I_009_% | % | float32 | R | 10552
890 | Harmonics | Input Channel 9 Current individual Harmonics 24 percentage | HAR24_I_009_% | % | float32 | R | 10554
891 | Harmonics | Input Channel 9 Current individual Harmonics 25 percentage | HAR25_I_009_% | % | float32 | R | 10556
892 | Harmonics | Input Channel 9 Current individual Harmonics 26 percentage | HAR26_I_009_% | % | float32 | R | 10558
893 | Harmonics | Input Channel 9 Current individual Harmonics 27 percentage | HAR27_I_009_% | % | float32 | R | 10560
894 | Harmonics | Input Channel 9 Current individual Harmonics 28 percentage | HAR28_I_009_% | % | float32 | R | 10562
895 | Harmonics | Input Channel 9 Current individual Harmonics 29 percentage | HAR29_I_009_% | % | float32 | R | 10564
896 | Harmonics | Input Channel 9 Current individual Harmonics 30 percentage | HAR30_I_009_% | % | float32 | R | 10566
897 | Harmonics | Input Channel 9 Current individual Harmonics 31 percentage | HAR31_I_009_% | % | float32 | R | 10568
898 | THD | Input Channel 10 Current THD | THD_I_010_% | % | float32 | R | 10570
899 | THD | Input Channel 10 Current THD Odd | OTHD_I_010_% | % | float32 | R | 10572
900 | THD | Input Channel 10 Current THD Even | ETHD_I_010_% | % | float32 | R | 10574
901 | THD | Input Channel 10 Current K Factor | KF_I_010_% | % | float32 | R | 10576
902 | Harmonics | Input Channel 10 Current individual Harmonics 2 percentage | HAR2_I_010_% | % | float32 | R | 10578
903 | Harmonics | Input Channel 10 Current individual Harmonics 3 percentage | HAR3_I_010_% | % | float32 | R | 10580
904 | Harmonics | Input Channel 10 Current individual Harmonics 4 percentage | HAR4_I_010_% | % | float32 | R | 10582
905 | Harmonics | Input Channel 10 Current individual Harmonics 5 percentage | HAR5_I_010_% | % | float32 | R | 10584
906 | Harmonics | Input Channel 10 Current individual Harmonics 6 percentage | HAR6_I_010_% | % | float32 | R | 10586
907 | Harmonics | Input Channel 10 Current individual Harmonics 7 percentage | HAR7_I_010_% | % | float32 | R | 10588
908 | Harmonics | Input Channel 10 Current individual Harmonics 8 percentage | HAR8_I_010_% | % | float32 | R | 10590
909 | Harmonics | Input Channel 10 Current individual Harmonics 9 percentage | HAR9_I_010_% | % | float32 | R | 10592
910 | Harmonics | Input Channel 10 Current individual Harmonics 10 percentage | HAR10_I_010_% | % | float32 | R | 10594
911 | Harmonics | Input Channel 10 Current individual Harmonics 11 percentage | HAR11_I_010_% | % | float32 | R | 10596
912 | Harmonics | Input Channel 10 Current individual Harmonics 12 percentage | HAR12_I_010_% | % | float32 | R | 10598
913 | Harmonics | Input Channel 10 Current individual Harmonics 13 percentage | HAR13_I_010_% | % | float32 | R | 10600
914 | Harmonics | Input Channel 10 Current individual Harmonics 14 percentage | HAR14_I_010_% | % | float32 | R | 10602
915 | Harmonics | Input Channel 10 Current individual Harmonics 15 percentage | HAR15_I_010_% | % | float32 | R | 10604
916 | Harmonics | Input Channel 10 Current individual Harmonics 16 percentage | HAR16_I_010_% | % | float32 | R | 10606
917 | Harmonics | Input Channel 10 Current individual Harmonics 17 percentage | HAR17_I_010_% | % | float32 | R | 10608
918 | Harmonics | Input Channel 10 Current individual Harmonics 18 percentage | HAR18_I_010_% | % | float32 | R | 10610
919 | Harmonics | Input Channel 10 Current individual Harmonics 19 percentage | HAR19_I_010_% | % | float32 | R | 10612
920 | Harmonics | Input Channel 10 Current individual Harmonics 20 percentage | HAR20_I_010_% | % | float32 | R | 10614
921 | Harmonics | Input Channel 10 Current individual Harmonics 21 percentage | HAR21_I_010_% | % | float32 | R | 10616
922 | Harmonics | Input Channel 10 Current individual Harmonics 22 percentage | HAR22_I_010_% | % | float32 | R | 10618
923 | Harmonics | Input Channel 10 Current individual Harmonics 23 percentage | HAR23_I_010_% | % | float32 | R | 10620
924 | Harmonics | Input Channel 10 Current individual Harmonics 24 percentage | HAR24_I_010_% | % | float32 | R | 10622
925 | Harmonics | Input Channel 10 Current individual Harmonics 25 percentage | HAR25_I_010_% | % | float32 | R | 10624
926 | Harmonics | Input Channel 10 Current individual Harmonics 26 percentage | HAR26_I_010_% | % | float32 | R | 10626
927 | Harmonics | Input Channel 10 Current individual Harmonics 27 percentage | HAR27_I_010_% | % | float32 | R | 10628
928 | Harmonics | Input Channel 10 Current individual Harmonics 28 percentage | HAR28_I_010_% | % | float32 | R | 10630
929 | Harmonics | Input Channel 10 Current individual Harmonics 29 percentage | HAR29_I_010_% | % | float32 | R | 10632
930 | Harmonics | Input Channel 10 Current individual Harmonics 30 percentage | HAR30_I_010_% | % | float32 | R | 10634
931 | Harmonics | Input Channel 10 Current individual Harmonics 31 percentage | HAR31_I_010_% | % | float32 | R | 10636
932 | THD | Input Channel 11 Current THD | THD_I_011_% | % | float32 | R | 10638
933 | THD | Input Channel 11 Current THD Odd | OTHD_I_011_% | % | float32 | R | 10640
934 | THD | Input Channel 11 Current THD Even | ETHD_I_011_% | % | float32 | R | 10642
935 | THD | Input Channel 11 Current K Factor | KF_I_011_% | % | float32 | R | 10644
936 | Harmonics | Input Channel 11 Current individual Harmonics 2 percentage | HAR2_I_011_% | % | float32 | R | 10646
937 | Harmonics | Input Channel 11 Current individual Harmonics 3 percentage | HAR3_I_011_% | % | float32 | R | 10648
938 | Harmonics | Input Channel 11 Current individual Harmonics 4 percentage | HAR4_I_011_% | % | float32 | R | 10650
939 | Harmonics | Input Channel 11 Current individual Harmonics 5 percentage | HAR5_I_011_% | % | float32 | R | 10652
940 | Harmonics | Input Channel 11 Current individual Harmonics 6 percentage | HAR6_I_011_% | % | float32 | R | 10654
941 | Harmonics | Input Channel 11 Current individual Harmonics 7 percentage | HAR7_I_011_% | % | float32 | R | 10656
942 | Harmonics | Input Channel 11 Current individual Harmonics 8 percentage | HAR8_I_011_% | % | float32 | R | 10658
943 | Harmonics | Input Channel 11 Current individual Harmonics 9 percentage | HAR9_I_011_% | % | float32 | R | 10660
944 | Harmonics | Input Channel 11 Current individual Harmonics 10 percentage | HAR10_I_011_% | % | float32 | R | 10662
945 | Harmonics | Input Channel 11 Current individual Harmonics 11 percentage | HAR11_I_011_% | % | float32 | R | 10664
946 | Harmonics | Input Channel 11 Current individual Harmonics 12 percentage | HAR12_I_011_% | % | float32 | R | 10666
947 | Harmonics | Input Channel 11 Current individual Harmonics 13 percentage | HAR13_I_011_% | % | float32 | R | 10668
948 | Harmonics | Input Channel 11 Current individual Harmonics 14 percentage | HAR14_I_011_% | % | float32 | R | 10670
949 | Harmonics | Input Channel 11 Current individual Harmonics 15 percentage | HAR15_I_011_% | % | float32 | R | 10672
950 | Harmonics | Input Channel 11 Current individual Harmonics 16 percentage | HAR16_I_011_% | % | float32 | R | 10674
951 | Harmonics | Input Channel 11 Current individual Harmonics 17 percentage | HAR17_I_011_% | % | float32 | R | 10676
952 | Harmonics | Input Channel 11 Current individual Harmonics 18 percentage | HAR18_I_011_% | % | float32 | R | 10678
953 | Harmonics | Input Channel 11 Current individual Harmonics 19 percentage | HAR19_I_011_% | % | float32 | R | 10680
954 | Harmonics | Input Channel 11 Current individual Harmonics 20 percentage | HAR20_I_011_% | % | float32 | R | 10682
955 | Harmonics | Input Channel 11 Current individual Harmonics 21 percentage | HAR21_I_011_% | % | float32 | R | 10684
956 | Harmonics | Input Channel 11 Current individual Harmonics 22 percentage | HAR22_I_011_% | % | float32 | R | 10686
957 | Harmonics | Input Channel 11 Current individual Harmonics 23 percentage | HAR23_I_011_% | % | float32 | R | 10688
958 | Harmonics | Input Channel 11 Current individual Harmonics 24 percentage | HAR24_I_011_% | % | float32 | R | 10690
959 | Harmonics | Input Channel 11 Current individual Harmonics 25 percentage | HAR25_I_011_% | % | float32 | R | 10692
960 | Harmonics | Input Channel 11 Current individual Harmonics 26 percentage | HAR26_I_011_% | % | float32 | R | 10694
961 | Harmonics | Input Channel 11 Current individual Harmonics 27 percentage | HAR27_I_011_% | % | float32 | R | 10696
962 | Harmonics | Input Channel 11 Current individual Harmonics 28 percentage | HAR28_I_011_% | % | float32 | R | 10698
963 | Harmonics | Input Channel 11 Current individual Harmonics 29 percentage | HAR29_I_011_% | % | float32 | R | 10700
964 | Harmonics | Input Channel 11 Current individual Harmonics 30 percentage | HAR30_I_011_% | % | float32 | R | 10702
965 | Harmonics | Input Channel 11 Current individual Harmonics 31 percentage | HAR31_I_011_% | % | float32 | R | 10704
966 | THD | Input Channel 12 Current THD | THD_I_012_% | % | float32 | R | 10706
967 | THD | Input Channel 12 Current THD Odd | OTHD_I_012_% | % | float32 | R | 10708
968 | THD | Input Channel 12 Current THD Even | ETHD_I_012_% | % | float32 | R | 10710
969 | THD | Input Channel 12 Current K Factor | KF_I_012_% | % | float32 | R | 10712
970 | Harmonics | Input Channel 12 Current individual Harmonics 2 percentage | HAR2_I_012_% | % | float32 | R | 10714
971 | Harmonics | Input Channel 12 Current individual Harmonics 3 percentage | HAR3_I_012_% | % | float32 | R | 10716
972 | Harmonics | Input Channel 12 Current individual Harmonics 4 percentage | HAR4_I_012_% | % | float32 | R | 10718
973 | Harmonics | Input Channel 12 Current individual Harmonics 5 percentage | HAR5_I_012_% | % | float32 | R | 10720
974 | Harmonics | Input Channel 12 Current individual Harmonics 6 percentage | HAR6_I_012_% | % | float32 | R | 10722
975 | Harmonics | Input Channel 12 Current individual Harmonics 7 percentage | HAR7_I_012_% | % | float32 | R | 10724
976 | Harmonics | Input Channel 12 Current individual Harmonics 8 percentage | HAR8_I_012_% | % | float32 | R | 10726
977 | Harmonics | Input Channel 12 Current individual Harmonics 9 percentage | HAR9_I_012_% | % | float32 | R | 10728
978 | Harmonics | Input Channel 12 Current individual Harmonics 10 percentage | HAR10_I_012_% | % | float32 | R | 10730
979 | Harmonics | Input Channel 12 Current individual Harmonics 11 percentage | HAR11_I_012_% | % | float32 | R | 10732
980 | Harmonics | Input Channel 12 Current individual Harmonics 12 percentage | HAR12_I_012_% | % | float32 | R | 10734
981 | Harmonics | Input Channel 12 Current individual Harmonics 13 percentage | HAR13_I_012_% | % | float32 | R | 10736
982 | Harmonics | Input Channel 12 Current individual Harmonics 14 percentage | HAR14_I_012_% | % | float32 | R | 10738
983 | Harmonics | Input Channel 12 Current individual Harmonics 15 percentage | HAR15_I_012_% | % | float32 | R | 10740
984 | Harmonics | Input Channel 12 Current individual Harmonics 16 percentage | HAR16_I_012_% | % | float32 | R | 10742
985 | Harmonics | Input Channel 12 Current individual Harmonics 17 percentage | HAR17_I_012_% | % | float32 | R | 10744
986 | Harmonics | Input Channel 12 Current individual Harmonics 18 percentage | HAR18_I_012_% | % | float32 | R | 10746
987 | Harmonics | Input Channel 12 Current individual Harmonics 19 percentage | HAR19_I_012_% | % | float32 | R | 10748
988 | Harmonics | Input Channel 12 Current individual Harmonics 20 percentage | HAR20_I_012_% | % | float32 | R | 10750
989 | Harmonics | Input Channel 12 Current individual Harmonics 21 percentage | HAR21_I_012_% | % | float32 | R | 10752
990 | Harmonics | Input Channel 12 Current individual Harmonics 22 percentage | HAR22_I_012_% | % | float32 | R | 10754
991 | Harmonics | Input Channel 12 Current individual Harmonics 23 percentage | HAR23_I_012_% | % | float32 | R | 10756
992 | Harmonics | Input Channel 12 Current individual Harmonics 24 percentage | HAR24_I_012_% | % | float32 | R | 10758
993 | Harmonics | Input Channel 12 Current individual Harmonics 25 percentage | HAR25_I_012_% | % | float32 | R | 10760
994 | Harmonics | Input Channel 12 Current individual Harmonics 26 percentage | HAR26_I_012_% | % | float32 | R | 10762
995 | Harmonics | Input Channel 12 Current individual Harmonics 27 percentage | HAR27_I_012_% | % | float32 | R | 10764
996 | Harmonics | Input Channel 12 Current individual Harmonics 28 percentage | HAR28_I_012_% | % | float32 | R | 10766
997 | Harmonics | Input Channel 12 Current individual Harmonics 29 percentage | HAR29_I_012_% | % | float32 | R | 10768
998 | Harmonics | Input Channel 12 Current individual Harmonics 30 percentage | HAR30_I_012_% | % | float32 | R | 10770
999 | Harmonics | Input Channel 12 Current individual Harmonics 31 percentage | HAR31_I_012_% | % | float32 | R | 10772
1000 | THD | Input Channel 13 Current THD | THD_I_013_% | % | float32 | R | 10774
1001 | THD | Input Channel 13 Current THD Odd | OTHD_I_013_% | % | float32 | R | 10776
1002 | THD | Input Channel 13 Current THD Even | ETHD_I_013_% | % | float32 | R | 10778
1003 | THD | Input Channel 13 Current K Factor | KF_I_013_% | % | float32 | R | 10780
1004 | Harmonics | Input Channel 13 Current individual Harmonics 2 percentage | HAR2_I_013_% | % | float32 | R | 10782
1005 | Harmonics | Input Channel 13 Current individual Harmonics 3 percentage | HAR3_I_013_% | % | float32 | R | 10784
1006 | Harmonics | Input Channel 13 Current individual Harmonics 4 percentage | HAR4_I_013_% | % | float32 | R | 10786
1007 | Harmonics | Input Channel 13 Current individual Harmonics 5 percentage | HAR5_I_013_% | % | float32 | R | 10788
1008 | Harmonics | Input Channel 13 Current individual Harmonics 6 percentage | HAR6_I_013_% | % | float32 | R | 10790
1009 | Harmonics | Input Channel 13 Current individual Harmonics 7 percentage | HAR7_I_013_% | % | float32 | R | 10792
1010 | Harmonics | Input Channel 13 Current individual Harmonics 8 percentage | HAR8_I_013_% | % | float32 | R | 10794
1011 | Harmonics | Input Channel 13 Current individual Harmonics 9 percentage | HAR9_I_013_% | % | float32 | R | 10796
1012 | Harmonics | Input Channel 13 Current individual Harmonics 10 percentage | HAR10_I_013_% | % | float32 | R | 10798
1013 | Harmonics | Input Channel 13 Current individual Harmonics 11 percentage | HAR11_I_013_% | % | float32 | R | 10800
1014 | Harmonics | Input Channel 13 Current individual Harmonics 12 percentage | HAR12_I_013_% | % | float32 | R | 10802
1015 | Harmonics | Input Channel 13 Current individual Harmonics 13 percentage | HAR13_I_013_% | % | float32 | R | 10804
1016 | Harmonics | Input Channel 13 Current individual Harmonics 14 percentage | HAR14_I_013_% | % | float32 | R | 10806
1017 | Harmonics | Input Channel 13 Current individual Harmonics 15 percentage | HAR15_I_013_% | % | float32 | R | 10808
1018 | Harmonics | Input Channel 13 Current individual Harmonics 16 percentage | HAR16_I_013_% | % | float32 | R | 10810
1019 | Harmonics | Input Channel 13 Current individual Harmonics 17 percentage | HAR17_I_013_% | % | float32 | R | 10812
1020 | Harmonics | Input Channel 13 Current individual Harmonics 18 percentage | HAR18_I_013_% | % | float32 | R | 10814
1021 | Harmonics | Input Channel 13 Current individual Harmonics 19 percentage | HAR19_I_013_% | % | float32 | R | 10816
1022 | Harmonics | Input Channel 13 Current individual Harmonics 20 percentage | HAR20_I_013_% | % | float32 | R | 10818
1023 | Harmonics | Input Channel 13 Current individual Harmonics 21 percentage | HAR21_I_013_% | % | float32 | R | 10820
1024 | Harmonics | Input Channel 13 Current individual Harmonics 22 percentage | HAR22_I_013_% | % | float32 | R | 10822
1025 | Harmonics | Input Channel 13 Current individual Harmonics 23 percentage | HAR23_I_013_% | % | float32 | R | 10824
1026 | Harmonics | Input Channel 13 Current individual Harmonics 24 percentage | HAR24_I_013_% | % | float32 | R | 10826
1027 | Harmonics | Input Channel 13 Current individual Harmonics 25 percentage | HAR25_I_013_% | % | float32 | R | 10828
1028 | Harmonics | Input Channel 13 Current individual Harmonics 26 percentage | HAR26_I_013_% | % | float32 | R | 10830
1029 | Harmonics | Input Channel 13 Current individual Harmonics 27 percentage | HAR27_I_013_% | % | float32 | R | 10832
1030 | Harmonics | Input Channel 13 Current individual Harmonics 28 percentage | HAR28_I_013_% | % | float32 | R | 10834
1031 | Harmonics | Input Channel 13 Current individual Harmonics 29 percentage | HAR29_I_013_% | % | float32 | R | 10836
1032 | Harmonics | Input Channel 13 Current individual Harmonics 30 percentage | HAR30_I_013_% | % | float32 | R | 10838
1033 | Harmonics | Input Channel 13 Current individual Harmonics 31 percentage | HAR31_I_013_% | % | float32 | R | 10840
1034 | THD | Input Channel 14 Current THD | THD_I_014_% | % | float32 | R | 10842
1035 | THD | Input Channel 14 Current THD Odd | OTHD_I_014_% | % | float32 | R | 10844
1036 | THD | Input Channel 14 Current THD Even | ETHD_I_014_% | % | float32 | R | 10846
1037 | THD | Input Channel 14 Current K Factor | KF_I_014_% | % | float32 | R | 10848
1038 | Harmonics | Input Channel 14 Current individual Harmonics 2 percentage | HAR2_I_014_% | % | float32 | R | 10850
1039 | Harmonics | Input Channel 14 Current individual Harmonics 3 percentage | HAR3_I_014_% | % | float32 | R | 10852
1040 | Harmonics | Input Channel 14 Current individual Harmonics 4 percentage | HAR4_I_014_% | % | float32 | R | 10854
1041 | Harmonics | Input Channel 14 Current individual Harmonics 5 percentage | HAR5_I_014_% | % | float32 | R | 10856
1042 | Harmonics | Input Channel 14 Current individual Harmonics 6 percentage | HAR6_I_014_% | % | float32 | R | 10858
1043 | Harmonics | Input Channel 14 Current individual Harmonics 7 percentage | HAR7_I_014_% | % | float32 | R | 10860
1044 | Harmonics | Input Channel 14 Current individual Harmonics 8 percentage | HAR8_I_014_% | % | float32 | R | 10862
1045 | Harmonics | Input Channel 14 Current individual Harmonics 9 percentage | HAR9_I_014_% | % | float32 | R | 10864
1046 | Harmonics | Input Channel 14 Current individual Harmonics 10 percentage | HAR10_I_014_% | % | float32 | R | 10866
1047 | Harmonics | Input Channel 14 Current individual Harmonics 11 percentage | HAR11_I_014_% | % | float32 | R | 10868
1048 | Harmonics | Input Channel 14 Current individual Harmonics 12 percentage | HAR12_I_014_% | % | float32 | R | 10870
1049 | Harmonics | Input Channel 14 Current individual Harmonics 13 percentage | HAR13_I_014_% | % | float32 | R | 10872
1050 | Harmonics | Input Channel 14 Current individual Harmonics 14 percentage | HAR14_I_014_% | % | float32 | R | 10874
1051 | Harmonics | Input Channel 14 Current individual Harmonics 15 percentage | HAR15_I_014_% | % | float32 | R | 10876
1052 | Harmonics | Input Channel 14 Current individual Harmonics 16 percentage | HAR16_I_014_% | % | float32 | R | 10878
1053 | Harmonics | Input Channel 14 Current individual Harmonics 17 percentage | HAR17_I_014_% | % | float32 | R | 10880
1054 | Harmonics | Input Channel 14 Current individual Harmonics 18 percentage | HAR18_I_014_% | % | float32 | R | 10882
1055 | Harmonics | Input Channel 14 Current individual Harmonics 19 percentage | HAR19_I_014_% | % | float32 | R | 10884
1056 | Harmonics | Input Channel 14 Current individual Harmonics 20 percentage | HAR20_I_014_% | % | float32 | R | 10886
1057 | Harmonics | Input Channel 14 Current individual Harmonics 21 percentage | HAR21_I_014_% | % | float32 | R | 10888
1058 | Harmonics | Input Channel 14 Current individual Harmonics 22 percentage | HAR22_I_014_% | % | float32 | R | 10890
1059 | Harmonics | Input Channel 14 Current individual Harmonics 23 percentage | HAR23_I_014_% | % | float32 | R | 10892
1060 | Harmonics | Input Channel 14 Current individual Harmonics 24 percentage | HAR24_I_014_% | % | float32 | R | 10894
1061 | Harmonics | Input Channel 14 Current individual Harmonics 25 percentage | HAR25_I_014_% | % | float32 | R | 10896
1062 | Harmonics | Input Channel 14 Current individual Harmonics 26 percentage | HAR26_I_014_% | % | float32 | R | 10898
1063 | Harmonics | Input Channel 14 Current individual Harmonics 27 percentage | HAR27_I_014_% | % | float32 | R | 10900
1064 | Harmonics | Input Channel 14 Current individual Harmonics 28 percentage | HAR28_I_014_% | % | float32 | R | 10902
1065 | Harmonics | Input Channel 14 Current individual Harmonics 29 percentage | HAR29_I_014_% | % | float32 | R | 10904
1066 | Harmonics | Input Channel 14 Current individual Harmonics 30 percentage | HAR30_I_014_% | % | float32 | R | 10906
1067 | Harmonics | Input Channel 14 Current individual Harmonics 31 percentage | HAR31_I_014_% | % | float32 | R | 10908
1068 | THD | Input Channel 15 Current THD | THD_I_015_% | % | float32 | R | 10910
1069 | THD | Input Channel 15 Current THD Odd | OTHD_I_015_% | % | float32 | R | 10912
1070 | THD | Input Channel 15 Current THD Even | ETHD_I_015_% | % | float32 | R | 10914
1071 | THD | Input Channel 15 Current K Factor | KF_I_015_% | % | float32 | R | 10916
1072 | Harmonics | Input Channel 15 Current individual Harmonics 2 percentage | HAR2_I_015_% | % | float32 | R | 10918
1073 | Harmonics | Input Channel 15 Current individual Harmonics 3 percentage | HAR3_I_015_% | % | float32 | R | 10920
1074 | Harmonics | Input Channel 15 Current individual Harmonics 4 percentage | HAR4_I_015_% | % | float32 | R | 10922
1075 | Harmonics | Input Channel 15 Current individual Harmonics 5 percentage | HAR5_I_015_% | % | float32 | R | 10924
1076 | Harmonics | Input Channel 15 Current individual Harmonics 6 percentage | HAR6_I_015_% | % | float32 | R | 10926
1077 | Harmonics | Input Channel 15 Current individual Harmonics 7 percentage | HAR7_I_015_% | % | float32 | R | 10928
1078 | Harmonics | Input Channel 15 Current individual Harmonics 8 percentage | HAR8_I_015_% | % | float32 | R | 10930
1079 | Harmonics | Input Channel 15 Current individual Harmonics 9 percentage | HAR9_I_015_% | % | float32 | R | 10932
1080 | Harmonics | Input Channel 15 Current individual Harmonics 10 percentage | HAR10_I_015_% | % | float32 | R | 10934
1081 | Harmonics | Input Channel 15 Current individual Harmonics 11 percentage | HAR11_I_015_% | % | float32 | R | 10936
1082 | Harmonics | Input Channel 15 Current individual Harmonics 12 percentage | HAR12_I_015_% | % | float32 | R | 10938
1083 | Harmonics | Input Channel 15 Current individual Harmonics 13 percentage | HAR13_I_015_% | % | float32 | R | 10940
1084 | Harmonics | Input Channel 15 Current individual Harmonics 14 percentage | HAR14_I_015_% | % | float32 | R | 10942
1085 | Harmonics | Input Channel 15 Current individual Harmonics 15 percentage | HAR15_I_015_% | % | float32 | R | 10944
1086 | Harmonics | Input Channel 15 Current individual Harmonics 16 percentage | HAR16_I_015_% | % | float32 | R | 10946
1087 | Harmonics | Input Channel 15 Current individual Harmonics 17 percentage | HAR17_I_015_% | % | float32 | R | 10948
1088 | Harmonics | Input Channel 15 Current individual Harmonics 18 percentage | HAR18_I_015_% | % | float32 | R | 10950
1089 | Harmonics | Input Channel 15 Current individual Harmonics 19 percentage | HAR19_I_015_% | % | float32 | R | 10952
1090 | Harmonics | Input Channel 15 Current individual Harmonics 20 percentage | HAR20_I_015_% | % | float32 | R | 10954
1091 | Harmonics | Input Channel 15 Current individual Harmonics 21 percentage | HAR21_I_015_% | % | float32 | R | 10956
1092 | Harmonics | Input Channel 15 Current individual Harmonics 22 percentage | HAR22_I_015_% | % | float32 | R | 10958
1093 | Harmonics | Input Channel 15 Current individual Harmonics 23 percentage | HAR23_I_015_% | % | float32 | R | 10960
1094 | Harmonics | Input Channel 15 Current individual Harmonics 24 percentage | HAR24_I_015_% | % | float32 | R | 10962
1095 | Harmonics | Input Channel 15 Current individual Harmonics 25 percentage | HAR25_I_015_% | % | float32 | R | 10964
1096 | Harmonics | Input Channel 15 Current individual Harmonics 26 percentage | HAR26_I_015_% | % | float32 | R | 10966
1097 | Harmonics | Input Channel 15 Current individual Harmonics 27 percentage | HAR27_I_015_% | % | float32 | R | 10968
1098 | Harmonics | Input Channel 15 Current individual Harmonics 28 percentage | HAR28_I_015_% | % | float32 | R | 10970
1099 | Harmonics | Input Channel 15 Current individual Harmonics 29 percentage | HAR29_I_015_% | % | float32 | R | 10972
1100 | Harmonics | Input Channel 15 Current individual Harmonics 30 percentage | HAR30_I_015_% | % | float32 | R | 10974
1101 | Harmonics | Input Channel 15 Current individual Harmonics 31 percentage | HAR31_I_015_% | % | float32 | R | 10976
1102 | THD | Input Channel 16 Current THD | THD_I_016_% | % | float32 | R | 10978
1103 | THD | Input Channel 16 Current THD Odd | OTHD_I_016_% | % | float32 | R | 10980
1104 | THD | Input Channel 16 Current THD Even | ETHD_I_016_% | % | float32 | R | 10982
1105 | THD | Input Channel 16 Current K Factor | KF_I_016_% | % | float32 | R | 10984
1106 | Harmonics | Input Channel 16 Current individual Harmonics 2 percentage | HAR2_I_016_% | % | float32 | R | 10986
1107 | Harmonics | Input Channel 16 Current individual Harmonics 3 percentage | HAR3_I_016_% | % | float32 | R | 10988
1108 | Harmonics | Input Channel 16 Current individual Harmonics 4 percentage | HAR4_I_016_% | % | float32 | R | 10990
1109 | Harmonics | Input Channel 16 Current individual Harmonics 5 percentage | HAR5_I_016_% | % | float32 | R | 10992
1110 | Harmonics | Input Channel 16 Current individual Harmonics 6 percentage | HAR6_I_016_% | % | float32 | R | 10994
1111 | Harmonics | Input Channel 16 Current individual Harmonics 7 percentage | HAR7_I_016_% | % | float32 | R | 10996
1112 | Harmonics | Input Channel 16 Current individual Harmonics 8 percentage | HAR8_I_016_% | % | float32 | R | 10998
1113 | Harmonics | Input Channel 16 Current individual Harmonics 9 percentage | HAR9_I_016_% | % | float32 | R | 11000
1114 | Harmonics | Input Channel 16 Current individual Harmonics 10 percentage | HAR10_I_016_% | % | float32 | R | 11002
1115 | Harmonics | Input Channel 16 Current individual Harmonics 11 percentage | HAR11_I_016_% | % | float32 | R | 11004
1116 | Harmonics | Input Channel 16 Current individual Harmonics 12 percentage | HAR12_I_016_% | % | float32 | R | 11006
1117 | Harmonics | Input Channel 16 Current individual Harmonics 13 percentage | HAR13_I_016_% | % | float32 | R | 11008
1118 | Harmonics | Input Channel 16 Current individual Harmonics 14 percentage | HAR14_I_016_% | % | float32 | R | 11010
1119 | Harmonics | Input Channel 16 Current individual Harmonics 15 percentage | HAR15_I_016_% | % | float32 | R | 11012
1120 | Harmonics | Input Channel 16 Current individual Harmonics 16 percentage | HAR16_I_016_% | % | float32 | R | 11014
1121 | Harmonics | Input Channel 16 Current individual Harmonics 17 percentage | HAR17_I_016_% | % | float32 | R | 11016
1122 | Harmonics | Input Channel 16 Current individual Harmonics 18 percentage | HAR18_I_016_% | % | float32 | R | 11018
1123 | Harmonics | Input Channel 16 Current individual Harmonics 19 percentage | HAR19_I_016_% | % | float32 | R | 11020
1124 | Harmonics | Input Channel 16 Current individual Harmonics 20 percentage | HAR20_I_016_% | % | float32 | R | 11022
1125 | Harmonics | Input Channel 16 Current individual Harmonics 21 percentage | HAR21_I_016_% | % | float32 | R | 11024
1126 | Harmonics | Input Channel 16 Current individual Harmonics 22 percentage | HAR22_I_016_% | % | float32 | R | 11026
1127 | Harmonics | Input Channel 16 Current individual Harmonics 23 percentage | HAR23_I_016_% | % | float32 | R | 11028
1128 | Harmonics | Input Channel 16 Current individual Harmonics 24 percentage | HAR24_I_016_% | % | float32 | R | 11030
1129 | Harmonics | Input Channel 16 Current individual Harmonics 25 percentage | HAR25_I_016_% | % | float32 | R | 11032
1130 | Harmonics | Input Channel 16 Current individual Harmonics 26 percentage | HAR26_I_016_% | % | float32 | R | 11034
1131 | Harmonics | Input Channel 16 Current individual Harmonics 27 percentage | HAR27_I_016_% | % | float32 | R | 11036
1132 | Harmonics | Input Channel 16 Current individual Harmonics 28 percentage | HAR28_I_016_% | % | float32 | R | 11038
1133 | Harmonics | Input Channel 16 Current individual Harmonics 29 percentage | HAR29_I_016_% | % | float32 | R | 11040
1134 | Harmonics | Input Channel 16 Current individual Harmonics 30 percentage | HAR30_I_016_% | % | float32 | R | 11042
1135 | Harmonics | Input Channel 16 Current individual Harmonics 31 percentage | HAR31_I_016_% | % | float32 | R | 11044
1136 | THD | Input Channel 17 Current THD | THD_I_017_% | % | float32 | R | 11046
1137 | THD | Input Channel 17 Current THD Odd | OTHD_I_017_% | % | float32 | R | 11048
1138 | THD | Input Channel 17 Current THD Even | ETHD_I_017_% | % | float32 | R | 11050
1139 | THD | Input Channel 17 Current K Factor | KF_I_017_% | % | float32 | R | 11052
1140 | Harmonics | Input Channel 17 Current individual Harmonics 2 percentage | HAR2_I_017_% | % | float32 | R | 11054
1141 | Harmonics | Input Channel 17 Current individual Harmonics 3 percentage | HAR3_I_017_% | % | float32 | R | 11056
1142 | Harmonics | Input Channel 17 Current individual Harmonics 4 percentage | HAR4_I_017_% | % | float32 | R | 11058
1143 | Harmonics | Input Channel 17 Current individual Harmonics 5 percentage | HAR5_I_017_% | % | float32 | R | 11060
1144 | Harmonics | Input Channel 17 Current individual Harmonics 6 percentage | HAR6_I_017_% | % | float32 | R | 11062
1145 | Harmonics | Input Channel 17 Current individual Harmonics 7 percentage | HAR7_I_017_% | % | float32 | R | 11064
1146 | Harmonics | Input Channel 17 Current individual Harmonics 8 percentage | HAR8_I_017_% | % | float32 | R | 11066
1147 | Harmonics | Input Channel 17 Current individual Harmonics 9 percentage | HAR9_I_017_% | % | float32 | R | 11068
1148 | Harmonics | Input Channel 17 Current individual Harmonics 10 percentage | HAR10_I_017_% | % | float32 | R | 11070
1149 | Harmonics | Input Channel 17 Current individual Harmonics 11 percentage | HAR11_I_017_% | % | float32 | R | 11072
1150 | Harmonics | Input Channel 17 Current individual Harmonics 12 percentage | HAR12_I_017_% | % | float32 | R | 11074
1151 | Harmonics | Input Channel 17 Current individual Harmonics 13 percentage | HAR13_I_017_% | % | float32 | R | 11076
1152 | Harmonics | Input Channel 17 Current individual Harmonics 14 percentage | HAR14_I_017_% | % | float32 | R | 11078
1153 | Harmonics | Input Channel 17 Current individual Harmonics 15 percentage | HAR15_I_017_% | % | float32 | R | 11080
1154 | Harmonics | Input Channel 17 Current individual Harmonics 16 percentage | HAR16_I_017_% | % | float32 | R | 11082
1155 | Harmonics | Input Channel 17 Current individual Harmonics 17 percentage | HAR17_I_017_% | % | float32 | R | 11084
1156 | Harmonics | Input Channel 17 Current individual Harmonics 18 percentage | HAR18_I_017_% | % | float32 | R | 11086
1157 | Harmonics | Input Channel 17 Current individual Harmonics 19 percentage | HAR19_I_017_% | % | float32 | R | 11088
1158 | Harmonics | Input Channel 17 Current individual Harmonics 20 percentage | HAR20_I_017_% | % | float32 | R | 11090
1159 | Harmonics | Input Channel 17 Current individual Harmonics 21 percentage | HAR21_I_017_% | % | float32 | R | 11092
1160 | Harmonics | Input Channel 17 Current individual Harmonics 22 percentage | HAR22_I_017_% | % | float32 | R | 11094
1161 | Harmonics | Input Channel 17 Current individual Harmonics 23 percentage | HAR23_I_017_% | % | float32 | R | 11096
1162 | Harmonics | Input Channel 17 Current individual Harmonics 24 percentage | HAR24_I_017_% | % | float32 | R | 11098
1163 | Harmonics | Input Channel 17 Current individual Harmonics 25 percentage | HAR25_I_017_% | % | float32 | R | 11100
1164 | Harmonics | Input Channel 17 Current individual Harmonics 26 percentage | HAR26_I_017_% | % | float32 | R | 11102
1165 | Harmonics | Input Channel 17 Current individual Harmonics 27 percentage | HAR27_I_017_% | % | float32 | R | 11104
1166 | Harmonics | Input Channel 17 Current individual Harmonics 28 percentage | HAR28_I_017_% | % | float32 | R | 11106
1167 | Harmonics | Input Channel 17 Current individual Harmonics 29 percentage | HAR29_I_017_% | % | float32 | R | 11108
1168 | Harmonics | Input Channel 17 Current individual Harmonics 30 percentage | HAR30_I_017_% | % | float32 | R | 11110
1169 | Harmonics | Input Channel 17 Current individual Harmonics 31 percentage | HAR31_I_017_% | % | float32 | R | 11112
1170 | THD | Input Channel 18 Current THD | THD_I_018_% | % | float32 | R | 11114
1171 | THD | Input Channel 18 Current THD Odd | OTHD_I_018_% | % | float32 | R | 11116
1172 | THD | Input Channel 18 Current THD Even | ETHD_I_018_% | % | float32 | R | 11118
1173 | THD | Input Channel 18 Current K Factor | KF_I_018_% | % | float32 | R | 11120
1174 | Harmonics | Input Channel 18 Current individual Harmonics 2 percentage | HAR2_I_018_% | % | float32 | R | 11122
1175 | Harmonics | Input Channel 18 Current individual Harmonics 3 percentage | HAR3_I_018_% | % | float32 | R | 11124
1176 | Harmonics | Input Channel 18 Current individual Harmonics 4 percentage | HAR4_I_018_% | % | float32 | R | 11126
1177 | Harmonics | Input Channel 18 Current individual Harmonics 5 percentage | HAR5_I_018_% | % | float32 | R | 11128
1178 | Harmonics | Input Channel 18 Current individual Harmonics 6 percentage | HAR6_I_018_% | % | float32 | R | 11130
1179 | Harmonics | Input Channel 18 Current individual Harmonics 7 percentage | HAR7_I_018_% | % | float32 | R | 11132
1180 | Harmonics | Input Channel 18 Current individual Harmonics 8 percentage | HAR8_I_018_% | % | float32 | R | 11134
1181 | Harmonics | Input Channel 18 Current individual Harmonics 9 percentage | HAR9_I_018_% | % | float32 | R | 11136
1182 | Harmonics | Input Channel 18 Current individual Harmonics 10 percentage | HAR10_I_018_% | % | float32 | R | 11138
1183 | Harmonics | Input Channel 18 Current individual Harmonics 11 percentage | HAR11_I_018_% | % | float32 | R | 11140
1184 | Harmonics | Input Channel 18 Current individual Harmonics 12 percentage | HAR12_I_018_% | % | float32 | R | 11142
1185 | Harmonics | Input Channel 18 Current individual Harmonics 13 percentage | HAR13_I_018_% | % | float32 | R | 11144
1186 | Harmonics | Input Channel 18 Current individual Harmonics 14 percentage | HAR14_I_018_% | % | float32 | R | 11146
1187 | Harmonics | Input Channel 18 Current individual Harmonics 15 percentage | HAR15_I_018_% | % | float32 | R | 11148
1188 | Harmonics | Input Channel 18 Current individual Harmonics 16 percentage | HAR16_I_018_% | % | float32 | R | 11150
1189 | Harmonics | Input Channel 18 Current individual Harmonics 17 percentage | HAR17_I_018_% | % | float32 | R | 11152
1190 | Harmonics | Input Channel 18 Current individual Harmonics 18 percentage | HAR18_I_018_% | % | float32 | R | 11154
1191 | Harmonics | Input Channel 18 Current individual Harmonics 19 percentage | HAR19_I_018_% | % | float32 | R | 11156
1192 | Harmonics | Input Channel 18 Current individual Harmonics 20 percentage | HAR20_I_018_% | % | float32 | R | 11158
1193 | Harmonics | Input Channel 18 Current individual Harmonics 21 percentage | HAR21_I_018_% | % | float32 | R | 11160
1194 | Harmonics | Input Channel 18 Current individual Harmonics 22 percentage | HAR22_I_018_% | % | float32 | R | 11162
1195 | Harmonics | Input Channel 18 Current individual Harmonics 23 percentage | HAR23_I_018_% | % | float32 | R | 11164
1196 | Harmonics | Input Channel 18 Current individual Harmonics 24 percentage | HAR24_I_018_% | % | float32 | R | 11166
1197 | Harmonics | Input Channel 18 Current individual Harmonics 25 percentage | HAR25_I_018_% | % | float32 | R | 11168
1198 | Harmonics | Input Channel 18 Current individual Harmonics 26 percentage | HAR26_I_018_% | % | float32 | R | 11170
1199 | Harmonics | Input Channel 18 Current individual Harmonics 27 percentage | HAR27_I_018_% | % | float32 | R | 11172
1200 | Harmonics | Input Channel 18 Current individual Harmonics 28 percentage | HAR28_I_018_% | % | float32 | R | 11174
1201 | Harmonics | Input Channel 18 Current individual Harmonics 29 percentage | HAR29_I_018_% | % | float32 | R | 11176
1202 | Harmonics | Input Channel 18 Current individual Harmonics 30 percentage | HAR30_I_018_% | % | float32 | R | 11178
1203 | Harmonics | Input Channel 18 Current individual Harmonics 31 percentage | HAR31_I_018_% | % | float32 | R | 11180
1204 | THD | Input Channel 19 Current THD | THD_I_019_% | % | float32 | R | 11182
1205 | THD | Input Channel 19 Current THD Odd | OTHD_I_019_% | % | float32 | R | 11184
1206 | THD | Input Channel 19 Current THD Even | ETHD_I_019_% | % | float32 | R | 11186
1207 | THD | Input Channel 19 Current K Factor | KF_I_019_% | % | float32 | R | 11188
1208 | Harmonics | Input Channel 19 Current individual Harmonics 2 percentage | HAR2_I_019_% | % | float32 | R | 11190
1209 | Harmonics | Input Channel 19 Current individual Harmonics 3 percentage | HAR3_I_019_% | % | float32 | R | 11192
1210 | Harmonics | Input Channel 19 Current individual Harmonics 4 percentage | HAR4_I_019_% | % | float32 | R | 11194
1211 | Harmonics | Input Channel 19 Current individual Harmonics 5 percentage | HAR5_I_019_% | % | float32 | R | 11196
1212 | Harmonics | Input Channel 19 Current individual Harmonics 6 percentage | HAR6_I_019_% | % | float32 | R | 11198
1213 | Harmonics | Input Channel 19 Current individual Harmonics 7 percentage | HAR7_I_019_% | % | float32 | R | 11200
1214 | Harmonics | Input Channel 19 Current individual Harmonics 8 percentage | HAR8_I_019_% | % | float32 | R | 11202
1215 | Harmonics | Input Channel 19 Current individual Harmonics 9 percentage | HAR9_I_019_% | % | float32 | R | 11204
1216 | Harmonics | Input Channel 19 Current individual Harmonics 10 percentage | HAR10_I_019_% | % | float32 | R | 11206
1217 | Harmonics | Input Channel 19 Current individual Harmonics 11 percentage | HAR11_I_019_% | % | float32 | R | 11208
1218 | Harmonics | Input Channel 19 Current individual Harmonics 12 percentage | HAR12_I_019_% | % | float32 | R | 11210
1219 | Harmonics | Input Channel 19 Current individual Harmonics 13 percentage | HAR13_I_019_% | % | float32 | R | 11212
1220 | Harmonics | Input Channel 19 Current individual Harmonics 14 percentage | HAR14_I_019_% | % | float32 | R | 11214
1221 | Harmonics | Input Channel 19 Current individual Harmonics 15 percentage | HAR15_I_019_% | % | float32 | R | 11216
1222 | Harmonics | Input Channel 19 Current individual Harmonics 16 percentage | HAR16_I_019_% | % | float32 | R | 11218
1223 | Harmonics | Input Channel 19 Current individual Harmonics 17 percentage | HAR17_I_019_% | % | float32 | R | 11220
1224 | Harmonics | Input Channel 19 Current individual Harmonics 18 percentage | HAR18_I_019_% | % | float32 | R | 11222
1225 | Harmonics | Input Channel 19 Current individual Harmonics 19 percentage | HAR19_I_019_% | % | float32 | R | 11224
1226 | Harmonics | Input Channel 19 Current individual Harmonics 20 percentage | HAR20_I_019_% | % | float32 | R | 11226
1227 | Harmonics | Input Channel 19 Current individual Harmonics 21 percentage | HAR21_I_019_% | % | float32 | R | 11228
1228 | Harmonics | Input Channel 19 Current individual Harmonics 22 percentage | HAR22_I_019_% | % | float32 | R | 11230
1229 | Harmonics | Input Channel 19 Current individual Harmonics 23 percentage | HAR23_I_019_% | % | float32 | R | 11232
1230 | Harmonics | Input Channel 19 Current individual Harmonics 24 percentage | HAR24_I_019_% | % | float32 | R | 11234
1231 | Harmonics | Input Channel 19 Current individual Harmonics 25 percentage | HAR25_I_019_% | % | float32 | R | 11236
1232 | Harmonics | Input Channel 19 Current individual Harmonics 26 percentage | HAR26_I_019_% | % | float32 | R | 11238
1233 | Harmonics | Input Channel 19 Current individual Harmonics 27 percentage | HAR27_I_019_% | % | float32 | R | 11240
1234 | Harmonics | Input Channel 19 Current individual Harmonics 28 percentage | HAR28_I_019_% | % | float32 | R | 11242
1235 | Harmonics | Input Channel 19 Current individual Harmonics 29 percentage | HAR29_I_019_% | % | float32 | R | 11244
1236 | Harmonics | Input Channel 19 Current individual Harmonics 30 percentage | HAR30_I_019_% | % | float32 | R | 11246
1237 | Harmonics | Input Channel 19 Current individual Harmonics 31 percentage | HAR31_I_019_% | % | float32 | R | 11248
1238 | THD | Input Channel 20 Current THD | THD_I_020_% | % | float32 | R | 11250
1239 | THD | Input Channel 20 Current THD Odd | OTHD_I_020_% | % | float32 | R | 11252
1240 | THD | Input Channel 20 Current THD Even | ETHD_I_020_% | % | float32 | R | 11254
1241 | THD | Input Channel 20 Current K Factor | KF_I_020_% | % | float32 | R | 11256
1242 | Harmonics | Input Channel 20 Current individual Harmonics 2 percentage | HAR2_I_020_% | % | float32 | R | 11258
1243 | Harmonics | Input Channel 20 Current individual Harmonics 3 percentage | HAR3_I_020_% | % | float32 | R | 11260
1244 | Harmonics | Input Channel 20 Current individual Harmonics 4 percentage | HAR4_I_020_% | % | float32 | R | 11262
1245 | Harmonics | Input Channel 20 Current individual Harmonics 5 percentage | HAR5_I_020_% | % | float32 | R | 11264
1246 | Harmonics | Input Channel 20 Current individual Harmonics 6 percentage | HAR6_I_020_% | % | float32 | R | 11266
1247 | Harmonics | Input Channel 20 Current individual Harmonics 7 percentage | HAR7_I_020_% | % | float32 | R | 11268
1248 | Harmonics | Input Channel 20 Current individual Harmonics 8 percentage | HAR8_I_020_% | % | float32 | R | 11270
1249 | Harmonics | Input Channel 20 Current individual Harmonics 9 percentage | HAR9_I_020_% | % | float32 | R | 11272
1250 | Harmonics | Input Channel 20 Current individual Harmonics 10 percentage | HAR10_I_020_% | % | float32 | R | 11274
1251 | Harmonics | Input Channel 20 Current individual Harmonics 11 percentage | HAR11_I_020_% | % | float32 | R | 11276
1252 | Harmonics | Input Channel 20 Current individual Harmonics 12 percentage | HAR12_I_020_% | % | float32 | R | 11278
1253 | Harmonics | Input Channel 20 Current individual Harmonics 13 percentage | HAR13_I_020_% | % | float32 | R | 11280
1254 | Harmonics | Input Channel 20 Current individual Harmonics 14 percentage | HAR14_I_020_% | % | float32 | R | 11282
1255 | Harmonics | Input Channel 20 Current individual Harmonics 15 percentage | HAR15_I_020_% | % | float32 | R | 11284
1256 | Harmonics | Input Channel 20 Current individual Harmonics 16 percentage | HAR16_I_020_% | % | float32 | R | 11286
1257 | Harmonics | Input Channel 20 Current individual Harmonics 17 percentage | HAR17_I_020_% | % | float32 | R | 11288
1258 | Harmonics | Input Channel 20 Current individual Harmonics 18 percentage | HAR18_I_020_% | % | float32 | R | 11290
1259 | Harmonics | Input Channel 20 Current individual Harmonics 19 percentage | HAR19_I_020_% | % | float32 | R | 11292
1260 | Harmonics | Input Channel 20 Current individual Harmonics 20 percentage | HAR20_I_020_% | % | float32 | R | 11294
1261 | Harmonics | Input Channel 20 Current individual Harmonics 21 percentage | HAR21_I_020_% | % | float32 | R | 11296
1262 | Harmonics | Input Channel 20 Current individual Harmonics 22 percentage | HAR22_I_020_% | % | float32 | R | 11298
1263 | Harmonics | Input Channel 20 Current individual Harmonics 23 percentage | HAR23_I_020_% | % | float32 | R | 11300
1264 | Harmonics | Input Channel 20 Current individual Harmonics 24 percentage | HAR24_I_020_% | % | float32 | R | 11302
1265 | Harmonics | Input Channel 20 Current individual Harmonics 25 percentage | HAR25_I_020_% | % | float32 | R | 11304
1266 | Harmonics | Input Channel 20 Current individual Harmonics 26 percentage | HAR26_I_020_% | % | float32 | R | 11306
1267 | Harmonics | Input Channel 20 Current individual Harmonics 27 percentage | HAR27_I_020_% | % | float32 | R | 11308
1268 | Harmonics | Input Channel 20 Current individual Harmonics 28 percentage | HAR28_I_020_% | % | float32 | R | 11310
1269 | Harmonics | Input Channel 20 Current individual Harmonics 29 percentage | HAR29_I_020_% | % | float32 | R | 11312
1270 | Harmonics | Input Channel 20 Current individual Harmonics 30 percentage | HAR30_I_020_% | % | float32 | R | 11314
1271 | Harmonics | Input Channel 20 Current individual Harmonics 31 percentage | HAR31_I_020_% | % | float32 | R | 11316
1272 | THD | Input Channel 21 Current THD | THD_I_021_% | % | float32 | R | 11318
1273 | THD | Input Channel 21 Current THD Odd | OTHD_I_021_% | % | float32 | R | 11320
1274 | THD | Input Channel 21 Current THD Even | ETHD_I_021_% | % | float32 | R | 11322
1275 | THD | Input Channel 21 Current K Factor | KF_I_021_% | % | float32 | R | 11324
1276 | Harmonics | Input Channel 21 Current individual Harmonics 2 percentage | HAR2_I_021_% | % | float32 | R | 11326
1277 | Harmonics | Input Channel 21 Current individual Harmonics 3 percentage | HAR3_I_021_% | % | float32 | R | 11328
1278 | Harmonics | Input Channel 21 Current individual Harmonics 4 percentage | HAR4_I_021_% | % | float32 | R | 11330
1279 | Harmonics | Input Channel 21 Current individual Harmonics 5 percentage | HAR5_I_021_% | % | float32 | R | 11332
1280 | Harmonics | Input Channel 21 Current individual Harmonics 6 percentage | HAR6_I_021_% | % | float32 | R | 11334
1281 | Harmonics | Input Channel 21 Current individual Harmonics 7 percentage | HAR7_I_021_% | % | float32 | R | 11336
1282 | Harmonics | Input Channel 21 Current individual Harmonics 8 percentage | HAR8_I_021_% | % | float32 | R | 11338
1283 | Harmonics | Input Channel 21 Current individual Harmonics 9 percentage | HAR9_I_021_% | % | float32 | R | 11340
1284 | Harmonics | Input Channel 21 Current individual Harmonics 10 percentage | HAR10_I_021_% | % | float32 | R | 11342
1285 | Harmonics | Input Channel 21 Current individual Harmonics 11 percentage | HAR11_I_021_% | % | float32 | R | 11344
1286 | Harmonics | Input Channel 21 Current individual Harmonics 12 percentage | HAR12_I_021_% | % | float32 | R | 11346
1287 | Harmonics | Input Channel 21 Current individual Harmonics 13 percentage | HAR13_I_021_% | % | float32 | R | 11348
1288 | Harmonics | Input Channel 21 Current individual Harmonics 14 percentage | HAR14_I_021_% | % | float32 | R | 11350
1289 | Harmonics | Input Channel 21 Current individual Harmonics 15 percentage | HAR15_I_021_% | % | float32 | R | 11352
1290 | Harmonics | Input Channel 21 Current individual Harmonics 16 percentage | HAR16_I_021_% | % | float32 | R | 11354
1291 | Harmonics | Input Channel 21 Current individual Harmonics 17 percentage | HAR17_I_021_% | % | float32 | R | 11356
1292 | Harmonics | Input Channel 21 Current individual Harmonics 18 percentage | HAR18_I_021_% | % | float32 | R | 11358
1293 | Harmonics | Input Channel 21 Current individual Harmonics 19 percentage | HAR19_I_021_% | % | float32 | R | 11360
1294 | Harmonics | Input Channel 21 Current individual Harmonics 20 percentage | HAR20_I_021_% | % | float32 | R | 11362
1295 | Harmonics | Input Channel 21 Current individual Harmonics 21 percentage | HAR21_I_021_% | % | float32 | R | 11364
1296 | Harmonics | Input Channel 21 Current individual Harmonics 22 percentage | HAR22_I_021_% | % | float32 | R | 11366
1297 | Harmonics | Input Channel 21 Current individual Harmonics 23 percentage | HAR23_I_021_% | % | float32 | R | 11368
1298 | Harmonics | Input Channel 21 Current individual Harmonics 24 percentage | HAR24_I_021_% | % | float32 | R | 11370
1299 | Harmonics | Input Channel 21 Current individual Harmonics 25 percentage | HAR25_I_021_% | % | float32 | R | 11372
1300 | Harmonics | Input Channel 21 Current individual Harmonics 26 percentage | HAR26_I_021_% | % | float32 | R | 11374
1301 | Harmonics | Input Channel 21 Current individual Harmonics 27 percentage | HAR27_I_021_% | % | float32 | R | 11376
1302 | Harmonics | Input Channel 21 Current individual Harmonics 28 percentage | HAR28_I_021_% | % | float32 | R | 11378
1303 | Harmonics | Input Channel 21 Current individual Harmonics 29 percentage | HAR29_I_021_% | % | float32 | R | 11380
1304 | Harmonics | Input Channel 21 Current individual Harmonics 30 percentage | HAR30_I_021_% | % | float32 | R | 11382
1305 | Harmonics | Input Channel 21 Current individual Harmonics 31 percentage | HAR31_I_021_% | % | float32 | R | 11384
1306 | THD | Input Channel 22 Current THD | THD_I_022_% | % | float32 | R | 11386
1307 | THD | Input Channel 22 Current THD Odd | OTHD_I_022_% | % | float32 | R | 11388
1308 | THD | Input Channel 22 Current THD Even | ETHD_I_022_% | % | float32 | R | 11390
1309 | THD | Input Channel 22 Current K Factor | KF_I_022_% | % | float32 | R | 11392
1310 | Harmonics | Input Channel 22 Current individual Harmonics 2 percentage | HAR2_I_022_% | % | float32 | R | 11394
1311 | Harmonics | Input Channel 22 Current individual Harmonics 3 percentage | HAR3_I_022_% | % | float32 | R | 11396
1312 | Harmonics | Input Channel 22 Current individual Harmonics 4 percentage | HAR4_I_022_% | % | float32 | R | 11398
1313 | Harmonics | Input Channel 22 Current individual Harmonics 5 percentage | HAR5_I_022_% | % | float32 | R | 11400
1314 | Harmonics | Input Channel 22 Current individual Harmonics 6 percentage | HAR6_I_022_% | % | float32 | R | 11402
1315 | Harmonics | Input Channel 22 Current individual Harmonics 7 percentage | HAR7_I_022_% | % | float32 | R | 11404
1316 | Harmonics | Input Channel 22 Current individual Harmonics 8 percentage | HAR8_I_022_% | % | float32 | R | 11406
1317 | Harmonics | Input Channel 22 Current individual Harmonics 9 percentage | HAR9_I_022_% | % | float32 | R | 11408
1318 | Harmonics | Input Channel 22 Current individual Harmonics 10 percentage | HAR10_I_022_% | % | float32 | R | 11410
1319 | Harmonics | Input Channel 22 Current individual Harmonics 11 percentage | HAR11_I_022_% | % | float32 | R | 11412
1320 | Harmonics | Input Channel 22 Current individual Harmonics 12 percentage | HAR12_I_022_% | % | float32 | R | 11414
1321 | Harmonics | Input Channel 22 Current individual Harmonics 13 percentage | HAR13_I_022_% | % | float32 | R | 11416
1322 | Harmonics | Input Channel 22 Current individual Harmonics 14 percentage | HAR14_I_022_% | % | float32 | R | 11418
1323 | Harmonics | Input Channel 22 Current individual Harmonics 15 percentage | HAR15_I_022_% | % | float32 | R | 11420
1324 | Harmonics | Input Channel 22 Current individual Harmonics 16 percentage | HAR16_I_022_% | % | float32 | R | 11422
1325 | Harmonics | Input Channel 22 Current individual Harmonics 17 percentage | HAR17_I_022_% | % | float32 | R | 11424
1326 | Harmonics | Input Channel 22 Current individual Harmonics 18 percentage | HAR18_I_022_% | % | float32 | R | 11426
1327 | Harmonics | Input Channel 22 Current individual Harmonics 19 percentage | HAR19_I_022_% | % | float32 | R | 11428
1328 | Harmonics | Input Channel 22 Current individual Harmonics 20 percentage | HAR20_I_022_% | % | float32 | R | 11430
1329 | Harmonics | Input Channel 22 Current individual Harmonics 21 percentage | HAR21_I_022_% | % | float32 | R | 11432
1330 | Harmonics | Input Channel 22 Current individual Harmonics 22 percentage | HAR22_I_022_% | % | float32 | R | 11434
1331 | Harmonics | Input Channel 22 Current individual Harmonics 23 percentage | HAR23_I_022_% | % | float32 | R | 11436
1332 | Harmonics | Input Channel 22 Current individual Harmonics 24 percentage | HAR24_I_022_% | % | float32 | R | 11438
1333 | Harmonics | Input Channel 22 Current individual Harmonics 25 percentage | HAR25_I_022_% | % | float32 | R | 11440
1334 | Harmonics | Input Channel 22 Current individual Harmonics 26 percentage | HAR26_I_022_% | % | float32 | R | 11442
1335 | Harmonics | Input Channel 22 Current individual Harmonics 27 percentage | HAR27_I_022_% | % | float32 | R | 11444
1336 | Harmonics | Input Channel 22 Current individual Harmonics 28 percentage | HAR28_I_022_% | % | float32 | R | 11446
1337 | Harmonics | Input Channel 22 Current individual Harmonics 29 percentage | HAR29_I_022_% | % | float32 | R | 11448
1338 | Harmonics | Input Channel 22 Current individual Harmonics 30 percentage | HAR30_I_022_% | % | float32 | R | 11450
1339 | Harmonics | Input Channel 22 Current individual Harmonics 31 percentage | HAR31_I_022_% | % | float32 | R | 11452
1340 | THD | Input Channel 23 Current THD | THD_I_023_% | % | float32 | R | 11454
1341 | THD | Input Channel 23 Current THD Odd | OTHD_I_023_% | % | float32 | R | 11456
1342 | THD | Input Channel 23 Current THD Even | ETHD_I_023_% | % | float32 | R | 11458
1343 | THD | Input Channel 23 Current K Factor | KF_I_023_% | % | float32 | R | 11460
1344 | Harmonics | Input Channel 23 Current individual Harmonics 2 percentage | HAR2_I_023_% | % | float32 | R | 11462
1345 | Harmonics | Input Channel 23 Current individual Harmonics 3 percentage | HAR3_I_023_% | % | float32 | R | 11464
1346 | Harmonics | Input Channel 23 Current individual Harmonics 4 percentage | HAR4_I_023_% | % | float32 | R | 11466
1347 | Harmonics | Input Channel 23 Current individual Harmonics 5 percentage | HAR5_I_023_% | % | float32 | R | 11468
1348 | Harmonics | Input Channel 23 Current individual Harmonics 6 percentage | HAR6_I_023_% | % | float32 | R | 11470
1349 | Harmonics | Input Channel 23 Current individual Harmonics 7 percentage | HAR7_I_023_% | % | float32 | R | 11472
1350 | Harmonics | Input Channel 23 Current individual Harmonics 8 percentage | HAR8_I_023_% | % | float32 | R | 11474
1351 | Harmonics | Input Channel 23 Current individual Harmonics 9 percentage | HAR9_I_023_% | % | float32 | R | 11476
1352 | Harmonics | Input Channel 23 Current individual Harmonics 10 percentage | HAR10_I_023_% | % | float32 | R | 11478
1353 | Harmonics | Input Channel 23 Current individual Harmonics 11 percentage | HAR11_I_023_% | % | float32 | R | 11480
1354 | Harmonics | Input Channel 23 Current individual Harmonics 12 percentage | HAR12_I_023_% | % | float32 | R | 11482
1355 | Harmonics | Input Channel 23 Current individual Harmonics 13 percentage | HAR13_I_023_% | % | float32 | R | 11484
1356 | Harmonics | Input Channel 23 Current individual Harmonics 14 percentage | HAR14_I_023_% | % | float32 | R | 11486
1357 | Harmonics | Input Channel 23 Current individual Harmonics 15 percentage | HAR15_I_023_% | % | float32 | R | 11488
1358 | Harmonics | Input Channel 23 Current individual Harmonics 16 percentage | HAR16_I_023_% | % | float32 | R | 11490
1359 | Harmonics | Input Channel 23 Current individual Harmonics 17 percentage | HAR17_I_023_% | % | float32 | R | 11492
1360 | Harmonics | Input Channel 23 Current individual Harmonics 18 percentage | HAR18_I_023_% | % | float32 | R | 11494
1361 | Harmonics | Input Channel 23 Current individual Harmonics 19 percentage | HAR19_I_023_% | % | float32 | R | 11496
1362 | Harmonics | Input Channel 23 Current individual Harmonics 20 percentage | HAR20_I_023_% | % | float32 | R | 11498
1363 | Harmonics | Input Channel 23 Current individual Harmonics 21 percentage | HAR21_I_023_% | % | float32 | R | 11500
1364 | Harmonics | Input Channel 23 Current individual Harmonics 22 percentage | HAR22_I_023_% | % | float32 | R | 11502
1365 | Harmonics | Input Channel 23 Current individual Harmonics 23 percentage | HAR23_I_023_% | % | float32 | R | 11504
1366 | Harmonics | Input Channel 23 Current individual Harmonics 24 percentage | HAR24_I_023_% | % | float32 | R | 11506
1367 | Harmonics | Input Channel 23 Current individual Harmonics 25 percentage | HAR25_I_023_% | % | float32 | R | 11508
1368 | Harmonics | Input Channel 23 Current individual Harmonics 26 percentage | HAR26_I_023_% | % | float32 | R | 11510
1369 | Harmonics | Input Channel 23 Current individual Harmonics 27 percentage | HAR27_I_023_% | % | float32 | R | 11512
1370 | Harmonics | Input Channel 23 Current individual Harmonics 28 percentage | HAR28_I_023_% | % | float32 | R | 11514
1371 | Harmonics | Input Channel 23 Current individual Harmonics 29 percentage | HAR29_I_023_% | % | float32 | R | 11516
1372 | Harmonics | Input Channel 23 Current individual Harmonics 30 percentage | HAR30_I_023_% | % | float32 | R | 11518
1373 | Harmonics | Input Channel 23 Current individual Harmonics 31 percentage | HAR31_I_023_% | % | float32 | R | 11520
1374 | THD | Input Channel 24 Current THD | THD_I_024_% | % | float32 | R | 11522
1375 | THD | Input Channel 24 Current THD Odd | OTHD_I_024_% | % | float32 | R | 11524
1376 | THD | Input Channel 24 Current THD Even | ETHD_I_024_% | % | float32 | R | 11526
1377 | THD | Input Channel 24 Current K Factor | KF_I_024_% | % | float32 | R | 11528
1378 | Harmonics | Input Channel 24 Current individual Harmonics 2 percentage | HAR2_I_024_% | % | float32 | R | 11530
1379 | Harmonics | Input Channel 24 Current individual Harmonics 3 percentage | HAR3_I_024_% | % | float32 | R | 11532
1380 | Harmonics | Input Channel 24 Current individual Harmonics 4 percentage | HAR4_I_024_% | % | float32 | R | 11534
1381 | Harmonics | Input Channel 24 Current individual Harmonics 5 percentage | HAR5_I_024_% | % | float32 | R | 11536
1382 | Harmonics | Input Channel 24 Current individual Harmonics 6 percentage | HAR6_I_024_% | % | float32 | R | 11538
1383 | Harmonics | Input Channel 24 Current individual Harmonics 7 percentage | HAR7_I_024_% | % | float32 | R | 11540
1384 | Harmonics | Input Channel 24 Current individual Harmonics 8 percentage | HAR8_I_024_% | % | float32 | R | 11542
1385 | Harmonics | Input Channel 24 Current individual Harmonics 9 percentage | HAR9_I_024_% | % | float32 | R | 11544
1386 | Harmonics | Input Channel 24 Current individual Harmonics 10 percentage | HAR10_I_024_% | % | float32 | R | 11546
1387 | Harmonics | Input Channel 24 Current individual Harmonics 11 percentage | HAR11_I_024_% | % | float32 | R | 11548
1388 | Harmonics | Input Channel 24 Current individual Harmonics 12 percentage | HAR12_I_024_% | % | float32 | R | 11550
1389 | Harmonics | Input Channel 24 Current individual Harmonics 13 percentage | HAR13_I_024_% | % | float32 | R | 11552
1390 | Harmonics | Input Channel 24 Current individual Harmonics 14 percentage | HAR14_I_024_% | % | float32 | R | 11554
1391 | Harmonics | Input Channel 24 Current individual Harmonics 15 percentage | HAR15_I_024_% | % | float32 | R | 11556
1392 | Harmonics | Input Channel 24 Current individual Harmonics 16 percentage | HAR16_I_024_% | % | float32 | R | 11558
1393 | Harmonics | Input Channel 24 Current individual Harmonics 17 percentage | HAR17_I_024_% | % | float32 | R | 11560
1394 | Harmonics | Input Channel 24 Current individual Harmonics 18 percentage | HAR18_I_024_% | % | float32 | R | 11562
1395 | Harmonics | Input Channel 24 Current individual Harmonics 19 percentage | HAR19_I_024_% | % | float32 | R | 11564
1396 | Harmonics | Input Channel 24 Current individual Harmonics 20 percentage | HAR20_I_024_% | % | float32 | R | 11566
1397 | Harmonics | Input Channel 24 Current individual Harmonics 21 percentage | HAR21_I_024_% | % | float32 | R | 11568
1398 | Harmonics | Input Channel 24 Current individual Harmonics 22 percentage | HAR22_I_024_% | % | float32 | R | 11570
1399 | Harmonics | Input Channel 24 Current individual Harmonics 23 percentage | HAR23_I_024_% | % | float32 | R | 11572
1400 | Harmonics | Input Channel 24 Current individual Harmonics 24 percentage | HAR24_I_024_% | % | float32 | R | 11574
1401 | Harmonics | Input Channel 24 Current individual Harmonics 25 percentage | HAR25_I_024_% | % | float32 | R | 11576
1402 | Harmonics | Input Channel 24 Current individual Harmonics 26 percentage | HAR26_I_024_% | % | float32 | R | 11578
1403 | Harmonics | Input Channel 24 Current individual Harmonics 27 percentage | HAR27_I_024_% | % | float32 | R | 11580
1404 | Harmonics | Input Channel 24 Current individual Harmonics 28 percentage | HAR28_I_024_% | % | float32 | R | 11582
1405 | Harmonics | Input Channel 24 Current individual Harmonics 29 percentage | HAR29_I_024_% | % | float32 | R | 11584
1406 | Harmonics | Input Channel 24 Current individual Harmonics 30 percentage | HAR30_I_024_% | % | float32 | R | 11586
1407 | Harmonics | Input Channel 24 Current individual Harmonics 31 percentage | HAR31_I_024_% | % | float32 | R | 11588
1408 | Sequence | User Channel 1 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s001 | A | float32 | R | 11590
1409 | Sequence | User Channel 1 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s001 | A | float32 | R | 11592
1410 | Sequence | User Channel 1 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s001 | A | float32 | R | 11594
1411 | Sequence | User Channel 1 Current Positive Sequence Angle | ANG_SEQ_POS_I_s001 | ° | float32 | R | 11596
1412 | Sequence | User Channel 1 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s001 | ° | float32 | R | 11598
1413 | Sequence | User Channel 1 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s001 | ° | float32 | R | 11600
1414 | Sequence | User Channel 1 Current Unbalance Factor Magnitude | UNBL_I_s001_% | % | float32 | R | 11602
1415 | Sequence | User Channel 2 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s002 | A | float32 | R | 11604
1416 | Sequence | User Channel 2 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s002 | A | float32 | R | 11606
1417 | Sequence | User Channel 2 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s002 | A | float32 | R | 11608
1418 | Sequence | User Channel 2 Current Positive Sequence Angle | ANG_SEQ_POS_I_s002 | ° | float32 | R | 11610
1419 | Sequence | User Channel 2 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s002 | ° | float32 | R | 11612
1420 | Sequence | User Channel 2 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s002 | ° | float32 | R | 11614
1421 | Sequence | User Channel 2 Current Unbalance Factor Magnitude | UNBL_I_s002_% | % | float32 | R | 11616
1422 | Sequence | User Channel 3 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s003 | A | float32 | R | 11618
1423 | Sequence | User Channel 3 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s003 | A | float32 | R | 11620
1424 | Sequence | User Channel 3 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s003 | A | float32 | R | 11622
1425 | Sequence | User Channel 3 Current Positive Sequence Angle | ANG_SEQ_POS_I_s003 | ° | float32 | R | 11624
1426 | Sequence | User Channel 3 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s003 | ° | float32 | R | 11626
1427 | Sequence | User Channel 3 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s003 | ° | float32 | R | 11628
1428 | Sequence | User Channel 3 Current Unbalance Factor Magnitude | UNBL_I_s003_% | % | float32 | R | 11630
1429 | Sequence | User Channel 4 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s004 | A | float32 | R | 11632
1430 | Sequence | User Channel 4 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s004 | A | float32 | R | 11634
1431 | Sequence | User Channel 4 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s004 | A | float32 | R | 11636
1432 | Sequence | User Channel 4 Current Positive Sequence Angle | ANG_SEQ_POS_I_s004 | ° | float32 | R | 11638
1433 | Sequence | User Channel 4 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s004 | ° | float32 | R | 11640
1434 | Sequence | User Channel 4 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s004 | ° | float32 | R | 11642
1435 | Sequence | User Channel 4 Current Unbalance Factor Magnitude | UNBL_I_s004_% | % | float32 | R | 11644
1436 | Sequence | User Channel 5 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s005 | A | float32 | R | 11646
1437 | Sequence | User Channel 5 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s005 | A | float32 | R | 11648
1438 | Sequence | User Channel 5 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s005 | A | float32 | R | 11650
1439 | Sequence | User Channel 5 Current Positive Sequence Angle | ANG_SEQ_POS_I_s005 | ° | float32 | R | 11652
1440 | Sequence | User Channel 5 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s005 | ° | float32 | R | 11654
1441 | Sequence | User Channel 5 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s005 | ° | float32 | R | 11656
1442 | Sequence | User Channel 5 Current Unbalance Factor Magnitude | UNBL_I_s005_% | % | float32 | R | 11658
1443 | Sequence | User Channel 6 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s006 | A | float32 | R | 11660
1444 | Sequence | User Channel 6 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s006 | A | float32 | R | 11662
1445 | Sequence | User Channel 6 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s006 | A | float32 | R | 11664
1446 | Sequence | User Channel 6 Current Positive Sequence Angle | ANG_SEQ_POS_I_s006 | ° | float32 | R | 11666
1447 | Sequence | User Channel 6 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s006 | ° | float32 | R | 11668
1448 | Sequence | User Channel 6 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s006 | ° | float32 | R | 11670
1449 | Sequence | User Channel 6 Current Unbalance Factor Magnitude | UNBL_I_s006_% | % | float32 | R | 11672
1450 | Sequence | User Channel 7 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s007 | A | float32 | R | 11674
1451 | Sequence | User Channel 7 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s007 | A | float32 | R | 11676
1452 | Sequence | User Channel 7 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s007 | A | float32 | R | 11678
1453 | Sequence | User Channel 7 Current Positive Sequence Angle | ANG_SEQ_POS_I_s007 | ° | float32 | R | 11680
1454 | Sequence | User Channel 7 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s007 | ° | float32 | R | 11682
1455 | Sequence | User Channel 7 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s007 | ° | float32 | R | 11684
1456 | Sequence | User Channel 7 Current Unbalance Factor Magnitude | UNBL_I_s007_% | % | float32 | R | 11686
1457 | Sequence | User Channel 8 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s008 | A | float32 | R | 11688
1458 | Sequence | User Channel 8 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s008 | A | float32 | R | 11690
1459 | Sequence | User Channel 8 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s008 | A | float32 | R | 11692
1460 | Sequence | User Channel 8 Current Positive Sequence Angle | ANG_SEQ_POS_I_s008 | ° | float32 | R | 11694
1461 | Sequence | User Channel 8 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s008 | ° | float32 | R | 11696
1462 | Sequence | User Channel 8 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s008 | ° | float32 | R | 11698
1463 | Sequence | User Channel 8 Current Unbalance Factor Magnitude | UNBL_I_s008_% | % | float32 | R | 11700
1464 | Sequence | User Channel 9 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s009 | A | float32 | R | 11702
1465 | Sequence | User Channel 9 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s009 | A | float32 | R | 11704
1466 | Sequence | User Channel 9 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s009 | A | float32 | R | 11706
1467 | Sequence | User Channel 9 Current Positive Sequence Angle | ANG_SEQ_POS_I_s009 | ° | float32 | R | 11708
1468 | Sequence | User Channel 9 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s009 | ° | float32 | R | 11710
1469 | Sequence | User Channel 9 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s009 | ° | float32 | R | 11712
1470 | Sequence | User Channel 9 Current Unbalance Factor Magnitude | UNBL_I_s009_% | % | float32 | R | 11714
1471 | Sequence | User Channel 10 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s010 | A | float32 | R | 11716
1472 | Sequence | User Channel 10 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s010 | A | float32 | R | 11718
1473 | Sequence | User Channel 10 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s010 | A | float32 | R | 11720
1474 | Sequence | User Channel 10 Current Positive Sequence Angle | ANG_SEQ_POS_I_s010 | ° | float32 | R | 11722
1475 | Sequence | User Channel 10 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s010 | ° | float32 | R | 11724
1476 | Sequence | User Channel 10 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s010 | ° | float32 | R | 11726
1477 | Sequence | User Channel 10 Current Unbalance Factor Magnitude | UNBL_I_s010_% | % | float32 | R | 11728
1478 | Sequence | User Channel 11 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s011 | A | float32 | R | 11730
1479 | Sequence | User Channel 11 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s011 | A | float32 | R | 11732
1480 | Sequence | User Channel 11 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s011 | A | float32 | R | 11734
1481 | Sequence | User Channel 11 Current Positive Sequence Angle | ANG_SEQ_POS_I_s011 | ° | float32 | R | 11736
1482 | Sequence | User Channel 11 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s011 | ° | float32 | R | 11738
1483 | Sequence | User Channel 11 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s011 | ° | float32 | R | 11740
1484 | Sequence | User Channel 11 Current Unbalance Factor Magnitude | UNBL_I_s011_% | % | float32 | R | 11742
1485 | Sequence | User Channel 12 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s012 | A | float32 | R | 11744
1486 | Sequence | User Channel 12 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s012 | A | float32 | R | 11746
1487 | Sequence | User Channel 12 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s012 | A | float32 | R | 11748
1488 | Sequence | User Channel 12 Current Positive Sequence Angle | ANG_SEQ_POS_I_s012 | ° | float32 | R | 11750
1489 | Sequence | User Channel 12 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s012 | ° | float32 | R | 11752
1490 | Sequence | User Channel 12 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s012 | ° | float32 | R | 11754
1491 | Sequence | User Channel 12 Current Unbalance Factor Magnitude | UNBL_I_s012_% | % | float32 | R | 11756
1492 | Energy | Phase A active energy import | EP_IMP_a_kWh | kWh | double | R | 12288
1493 | Energy | Phase A active energy export | EP_EXP_a_kWh | kWh | double | R | 12292
1494 | Energy | Phase A active energy net | EP_NET_a_kWh | kWh | double | R | 12296
1495 | Energy | Phase A active energy total | EP_TOTAL_a_kWh | kWh | double | R | 12300
1496 | Energy | Phase A reactive energy import | EQ_IMP_a_kvarh | kvarh | double | R | 12304
1497 | Energy | Phase A reactive energy export | EQ_EXP_a_kvarh | kvarh | double | R | 12308
1498 | Energy | Phase A reactive energy net | EQ_NET_a_kvarh | kvarh | double | R | 12312
1499 | Energy | Phase A reactive energy total | EQ_TOTAL_a_kvarh | kvarh | double | R | 12316
1500 | Energy | Phase A apparent energy | ES_a_kVAh | kVAh | double | R | 12320
1501 | Energy | Phase B active energy import | EP_IMP_b_kWh | kWh | double | R | 12324
1502 | Energy | Phase B active energy export | EP_EXP_b_kWh | kWh | double | R | 12328
1503 | Energy | Phase B active energy net | EP_NET_b_kWh | kWh | double | R | 12332
1504 | Energy | Phase B active energy total | EP_TOTAL_b_kWh | kWh | double | R | 12336
1505 | Energy | Phase B reactive energy import | EQ_IMP_b_kvarh | kvarh | double | R | 12340
1506 | Energy | Phase B reactive energy export | EQ_EXP_b_kvarh | kvarh | double | R | 12344
1507 | Energy | Phase B reactive energy net | EQ_NET_b_kvarh | kvarh | double | R | 12348
1508 | Energy | Phase B reactive energy total | EQ_TOTAL_b_kvarh | kvarh | double | R | 12352
1509 | Energy | Phase B apparent energy | ES_b_kVAh | kVAh | double | R | 12356
1510 | Energy | Phase C active energy import | EP_IMP_c_kWh | kWh | double | R | 12360
1511 | Energy | Phase C active energy export | EP_EXP_c_kWh | kWh | double | R | 12364
1512 | Energy | Phase C active energy net | EP_NET_c_kWh | kWh | double | R | 12368
1513 | Energy | Phase C active energy total | EP_TOTAL_c_kWh | kWh | double | R | 12372
1514 | Energy | Phase C reactive energy import | EQ_IMP_c_kvarh | kvarh | double | R | 12376
1515 | Energy | Phase C reactive energy export | EQ_EXP_c_kvarh | kvarh | double | R | 12380
1516 | Energy | Phase C reactive energy net | EQ_NET_c_kvarh | kvarh | double | R | 12384
1517 | Energy | Phase C reactive energy total | EQ_TOTAL_c_kvarh | kvarh | double | R | 12388
1518 | Energy | Phase C apparent energy | ES_c_kVAh | kVAh | double | R | 12392
1519 | Energy | System active energy import | EP_IMP_kWh | kWh | double | R | 12396
1520 | Energy | System active energy export | EP_EXP_kWh | kWh | double | R | 12400
1521 | Energy | System active energy net | EP_NET_kWh | kWh | double | R | 12404
1522 | Energy | System active energy total | EP_TOTAL_kWh | kWh | double | R | 12408
1523 | Energy | System reactive energy import | EQ_IMP_kvarh | kvarh | double | R | 12412
1524 | Energy | System reactive energy export | EQ_EXP_kvarh | kvarh | double | R | 12416
1525 | Energy | System reactive energy net | EQ_NET_kvarh | kvarh | double | R | 12420
1526 | Energy | System reactive energy total | EQ_TOTAL_kvarh | kvarh | double | R | 12424
1527 | Energy | System apparent energy | ES_kVAh | kVAh | double | R | 12428
1528 | Energy | Input Channel 1 active energy import | EP_IMP_001_kWh | kWh | double | R | 12432
1529 | Energy | Input Channel 1 active energy export | EP_EXP_001_kWh | kWh | double | R | 12436
1530 | Energy | Input Channel 1 active energy net | EP_NET_001_kWh | kWh | double | R | 12440
1531 | Energy | Input Channel 1 active energy total | EP_TOTAL_001_kWh | kWh | double | R | 12444
1532 | Energy | Input Channel 1 reactive energy import | EQ_IMP_001_kvarh | kvarh | double | R | 12448
1533 | Energy | Input Channel 1 reactive energy export | EQ_EXP_001_kvarh | kvarh | double | R | 12452
1534 | Energy | Input Channel 1 reactive energy net | EQ_NET_001_kvarh | kvarh | double | R | 12456
1535 | Energy | Input Channel 1 reactive energy total | EQ_TOTAL_001_kvarh | kvarh | double | R | 12460
1536 | Energy | Input Channel 1 apparent energy | ES_001_kVAh | kVAh | double | R | 12464
1537 | Energy | Input Channel 2 active energy import | EP_IMP_002_kWh | kWh | double | R | 12468
1538 | Energy | Input Channel 2 active energy export | EP_EXP_002_kWh | kWh | double | R | 12472
1539 | Energy | Input Channel 2 active energy net | EP_NET_002_kWh | kWh | double | R | 12476
1540 | Energy | Input Channel 2 active energy total | EP_TOTAL_002_kWh | kWh | double | R | 12480
1541 | Energy | Input Channel 2 reactive energy import | EQ_IMP_002_kvarh | kvarh | double | R | 12484
1542 | Energy | Input Channel 2 reactive energy export | EQ_EXP_002_kvarh | kvarh | double | R | 12488
1543 | Energy | Input Channel 2 reactive energy net | EQ_NET_002_kvarh | kvarh | double | R | 12492
1544 | Energy | Input Channel 2 reactive energy total | EQ_TOTAL_002_kvarh | kvarh | double | R | 12496
1545 | Energy | Input Channel 2 apparent energy | ES_002_kVAh | kVAh | double | R | 12500
1546 | Energy | Input Channel 3 active energy import | EP_IMP_003_kWh | kWh | double | R | 12504
1547 | Energy | Input Channel 3 active energy export | EP_EXP_003_kWh | kWh | double | R | 12508
1548 | Energy | Input Channel 3 active energy net | EP_NET_003_kWh | kWh | double | R | 12512
1549 | Energy | Input Channel 3 active energy total | EP_TOTAL_003_kWh | kWh | double | R | 12516
1550 | Energy | Input Channel 3 reactive energy import | EQ_IMP_003_kvarh | kvarh | double | R | 12520
1551 | Energy | Input Channel 3 reactive energy export | EQ_EXP_003_kvarh | kvarh | double | R | 12524
1552 | Energy | Input Channel 3 reactive energy net | EQ_NET_003_kvarh | kvarh | double | R | 12528
1553 | Energy | Input Channel 3 reactive energy total | EQ_TOTAL_003_kvarh | kvarh | double | R | 12532
1554 | Energy | Input Channel 3 apparent energy | ES_003_kVAh | kVAh | double | R | 12536
1555 | Energy | Input Channel 4 active energy import | EP_IMP_004_kWh | kWh | double | R | 12540
1556 | Energy | Input Channel 4 active energy export | EP_EXP_004_kWh | kWh | double | R | 12544
1557 | Energy | Input Channel 4 active energy net | EP_NET_004_kWh | kWh | double | R | 12548
1558 | Energy | Input Channel 4 active energy total | EP_TOTAL_004_kWh | kWh | double | R | 12552
1559 | Energy | Input Channel 4 reactive energy import | EQ_IMP_004_kvarh | kvarh | double | R | 12556
1560 | Energy | Input Channel 4 reactive energy export | EQ_EXP_004_kvarh | kvarh | double | R | 12560
1561 | Energy | Input Channel 4 reactive energy net | EQ_NET_004_kvarh | kvarh | double | R | 12564
1562 | Energy | Input Channel 4 reactive energy total | EQ_TOTAL_004_kvarh | kvarh | double | R | 12568
1563 | Energy | Input Channel 4 apparent energy | ES_004_kVAh | kVAh | double | R | 12572
1564 | Energy | Input Channel 5 active energy import | EP_IMP_005_kWh | kWh | double | R | 12576
1565 | Energy | Input Channel 5 active energy export | EP_EXP_005_kWh | kWh | double | R | 12580
1566 | Energy | Input Channel 5 active energy net | EP_NET_005_kWh | kWh | double | R | 12584
1567 | Energy | Input Channel 5 active energy total | EP_TOTAL_005_kWh | kWh | double | R | 12588
1568 | Energy | Input Channel 5 reactive energy import | EQ_IMP_005_kvarh | kvarh | double | R | 12592
1569 | Energy | Input Channel 5 reactive energy export | EQ_EXP_005_kvarh | kvarh | double | R | 12596
1570 | Energy | Input Channel 5 reactive energy net | EQ_NET_005_kvarh | kvarh | double | R | 12600
1571 | Energy | Input Channel 5 reactive energy total | EQ_TOTAL_005_kvarh | kvarh | double | R | 12604
1572 | Energy | Input Channel 5 apparent energy | ES_005_kVAh | kVAh | double | R | 12608
1573 | Energy | Input Channel 6 active energy import | EP_IMP_006_kWh | kWh | double | R | 12612
1574 | Energy | Input Channel 6 active energy export | EP_EXP_006_kWh | kWh | double | R | 12616
1575 | Energy | Input Channel 6 active energy net | EP_NET_006_kWh | kWh | double | R | 12620
1576 | Energy | Input Channel 6 active energy total | EP_TOTAL_006_kWh | kWh | double | R | 12624
1577 | Energy | Input Channel 6 reactive energy import | EQ_IMP_006_kvarh | kvarh | double | R | 12628
1578 | Energy | Input Channel 6 reactive energy export | EQ_EXP_006_kvarh | kvarh | double | R | 12632
1579 | Energy | Input Channel 6 reactive energy net | EQ_NET_006_kvarh | kvarh | double | R | 12636
1580 | Energy | Input Channel 6 reactive energy total | EQ_TOTAL_006_kvarh | kvarh | double | R | 12640
1581 | Energy | Input Channel 6 apparent energy | ES_006_kVAh | kVAh | double | R | 12644
1582 | Energy | Input Channel 7 active energy import | EP_IMP_007_kWh | kWh | double | R | 12648
1583 | Energy | Input Channel 7 active energy export | EP_EXP_007_kWh | kWh | double | R | 12652
1584 | Energy | Input Channel 7 active energy net | EP_NET_007_kWh | kWh | double | R | 12656
1585 | Energy | Input Channel 7 active energy total | EP_TOTAL_007_kWh | kWh | double | R | 12660
1586 | Energy | Input Channel 7 reactive energy import | EQ_IMP_007_kvarh | kvarh | double | R | 12664
1587 | Energy | Input Channel 7 reactive energy export | EQ_EXP_007_kvarh | kvarh | double | R | 12668
1588 | Energy | Input Channel 7 reactive energy net | EQ_NET_007_kvarh | kvarh | double | R | 12672
1589 | Energy | Input Channel 7 reactive energy total | EQ_TOTAL_007_kvarh | kvarh | double | R | 12676
1590 | Energy | Input Channel 7 apparent energy | ES_007_kVAh | kVAh | double | R | 12680
1591 | Energy | Input Channel 8 active energy import | EP_IMP_008_kWh | kWh | double | R | 12684
1592 | Energy | Input Channel 8 active energy export | EP_EXP_008_kWh | kWh | double | R | 12688
1593 | Energy | Input Channel 8 active energy net | EP_NET_008_kWh | kWh | double | R | 12692
1594 | Energy | Input Channel 8 active energy total | EP_TOTAL_008_kWh | kWh | double | R | 12696
1595 | Energy | Input Channel 8 reactive energy import | EQ_IMP_008_kvarh | kvarh | double | R | 12700
1596 | Energy | Input Channel 8 reactive energy export | EQ_EXP_008_kvarh | kvarh | double | R | 12704
1597 | Energy | Input Channel 8 reactive energy net | EQ_NET_008_kvarh | kvarh | double | R | 12708
1598 | Energy | Input Channel 8 reactive energy total | EQ_TOTAL_008_kvarh | kvarh | double | R | 12712
1599 | Energy | Input Channel 8 apparent energy | ES_008_kVAh | kVAh | double | R | 12716
1600 | Energy | Input Channel 9 active energy import | EP_IMP_009_kWh | kWh | double | R | 12720
1601 | Energy | Input Channel 9 active energy export | EP_EXP_009_kWh | kWh | double | R | 12724
1602 | Energy | Input Channel 9 active energy net | EP_NET_009_kWh | kWh | double | R | 12728
1603 | Energy | Input Channel 9 active energy total | EP_TOTAL_009_kWh | kWh | double | R | 12732
1604 | Energy | Input Channel 9 reactive energy import | EQ_IMP_009_kvarh | kvarh | double | R | 12736
1605 | Energy | Input Channel 9 reactive energy export | EQ_EXP_009_kvarh | kvarh | double | R | 12740
1606 | Energy | Input Channel 9 reactive energy net | EQ_NET_009_kvarh | kvarh | double | R | 12744
1607 | Energy | Input Channel 9 reactive energy total | EQ_TOTAL_009_kvarh | kvarh | double | R | 12748
1608 | Energy | Input Channel 9 apparent energy | ES_009_kVAh | kVAh | double | R | 12752
1609 | Energy | Input Channel 10 active energy import | EP_IMP_010_kWh | kWh | double | R | 12756
1610 | Energy | Input Channel 10 active energy export | EP_EXP_010_kWh | kWh | double | R | 12760
1611 | Energy | Input Channel 10 active energy net | EP_NET_010_kWh | kWh | double | R | 12764
1612 | Energy | Input Channel 10 active energy total | EP_TOTAL_010_kWh | kWh | double | R | 12768
1613 | Energy | Input Channel 10 reactive energy import | EQ_IMP_010_kvarh | kvarh | double | R | 12772
1614 | Energy | Input Channel 10 reactive energy export | EQ_EXP_010_kvarh | kvarh | double | R | 12776
1615 | Energy | Input Channel 10 reactive energy net | EQ_NET_010_kvarh | kvarh | double | R | 12780
1616 | Energy | Input Channel 10 reactive energy total | EQ_TOTAL_010_kvarh | kvarh | double | R | 12784
1617 | Energy | Input Channel 10 apparent energy | ES_010_kVAh | kVAh | double | R | 12788
1618 | Energy | Input Channel 11 active energy import | EP_IMP_011_kWh | kWh | double | R | 12792
1619 | Energy | Input Channel 11 active energy export | EP_EXP_011_kWh | kWh | double | R | 12796
1620 | Energy | Input Channel 11 active energy net | EP_NET_011_kWh | kWh | double | R | 12800
1621 | Energy | Input Channel 11 active energy total | EP_TOTAL_011_kWh | kWh | double | R | 12804
1622 | Energy | Input Channel 11 reactive energy import | EQ_IMP_011_kvarh | kvarh | double | R | 12808
1623 | Energy | Input Channel 11 reactive energy export | EQ_EXP_011_kvarh | kvarh | double | R | 12812
1624 | Energy | Input Channel 11 reactive energy net | EQ_NET_011_kvarh | kvarh | double | R | 12816
1625 | Energy | Input Channel 11 reactive energy total | EQ_TOTAL_011_kvarh | kvarh | double | R | 12820
1626 | Energy | Input Channel 11 apparent energy | ES_011_kVAh | kVAh | double | R | 12824
1627 | Energy | Input Channel 12 active energy import | EP_IMP_012_kWh | kWh | double | R | 12828
1628 | Energy | Input Channel 12 active energy export | EP_EXP_012_kWh | kWh | double | R | 12832
1629 | Energy | Input Channel 12 active energy net | EP_NET_012_kWh | kWh | double | R | 12836
1630 | Energy | Input Channel 12 active energy total | EP_TOTAL_012_kWh | kWh | double | R | 12840
1631 | Energy | Input Channel 12 reactive energy import | EQ_IMP_012_kvarh | kvarh | double | R | 12844
1632 | Energy | Input Channel 12 reactive energy export | EQ_EXP_012_kvarh | kvarh | double | R | 12848
1633 | Energy | Input Channel 12 reactive energy net | EQ_NET_012_kvarh | kvarh | double | R | 12852
1634 | Energy | Input Channel 12 reactive energy total | EQ_TOTAL_012_kvarh | kvarh | double | R | 12856
1635 | Energy | Input Channel 12 apparent energy | ES_012_kVAh | kVAh | double | R | 12860
1636 | Energy | Input Channel 13 active energy import | EP_IMP_013_kWh | kWh | double | R | 12864
1637 | Energy | Input Channel 13 active energy export | EP_EXP_013_kWh | kWh | double | R | 12868
1638 | Energy | Input Channel 13 active energy net | EP_NET_013_kWh | kWh | double | R | 12872
1639 | Energy | Input Channel 13 active energy total | EP_TOTAL_013_kWh | kWh | double | R | 12876
1640 | Energy | Input Channel 13 reactive energy import | EQ_IMP_013_kvarh | kvarh | double | R | 12880
1641 | Energy | Input Channel 13 reactive energy export | EQ_EXP_013_kvarh | kvarh | double | R | 12884
1642 | Energy | Input Channel 13 reactive energy net | EQ_NET_013_kvarh | kvarh | double | R | 12888
1643 | Energy | Input Channel 13 reactive energy total | EQ_TOTAL_013_kvarh | kvarh | double | R | 12892
1644 | Energy | Input Channel 13 apparent energy | ES_013_kVAh | kVAh | double | R | 12896
1645 | Energy | Input Channel 14 active energy import | EP_IMP_014_kWh | kWh | double | R | 12900
1646 | Energy | Input Channel 14 active energy export | EP_EXP_014_kWh | kWh | double | R | 12904
1647 | Energy | Input Channel 14 active energy net | EP_NET_014_kWh | kWh | double | R | 12908
1648 | Energy | Input Channel 14 active energy total | EP_TOTAL_014_kWh | kWh | double | R | 12912
1649 | Energy | Input Channel 14 reactive energy import | EQ_IMP_014_kvarh | kvarh | double | R | 12916
1650 | Energy | Input Channel 14 reactive energy export | EQ_EXP_014_kvarh | kvarh | double | R | 12920
1651 | Energy | Input Channel 14 reactive energy net | EQ_NET_014_kvarh | kvarh | double | R | 12924
1652 | Energy | Input Channel 14 reactive energy total | EQ_TOTAL_014_kvarh | kvarh | double | R | 12928
1653 | Energy | Input Channel 14 apparent energy | ES_014_kVAh | kVAh | double | R | 12932
1654 | Energy | Input Channel 15 active energy import | EP_IMP_015_kWh | kWh | double | R | 12936
1655 | Energy | Input Channel 15 active energy export | EP_EXP_015_kWh | kWh | double | R | 12940
1656 | Energy | Input Channel 15 active energy net | EP_NET_015_kWh | kWh | double | R | 12944
1657 | Energy | Input Channel 15 active energy total | EP_TOTAL_015_kWh | kWh | double | R | 12948
1658 | Energy | Input Channel 15 reactive energy import | EQ_IMP_015_kvarh | kvarh | double | R | 12952
1659 | Energy | Input Channel 15 reactive energy export | EQ_EXP_015_kvarh | kvarh | double | R | 12956
1660 | Energy | Input Channel 15 reactive energy net | EQ_NET_015_kvarh | kvarh | double | R | 12960
1661 | Energy | Input Channel 15 reactive energy total | EQ_TOTAL_015_kvarh | kvarh | double | R | 12964
1662 | Energy | Input Channel 15 apparent energy | ES_015_kVAh | kVAh | double | R | 12968
1663 | Energy | Input Channel 16 active energy import | EP_IMP_016_kWh | kWh | double | R | 12972
1664 | Energy | Input Channel 16 active energy export | EP_EXP_016_kWh | kWh | double | R | 12976
1665 | Energy | Input Channel 16 active energy net | EP_NET_016_kWh | kWh | double | R | 12980
1666 | Energy | Input Channel 16 active energy total | EP_TOTAL_016_kWh | kWh | double | R | 12984
1667 | Energy | Input Channel 16 reactive energy import | EQ_IMP_016_kvarh | kvarh | double | R | 12988
1668 | Energy | Input Channel 16 reactive energy export | EQ_EXP_016_kvarh | kvarh | double | R | 12992
1669 | Energy | Input Channel 16 reactive energy net | EQ_NET_016_kvarh | kvarh | double | R | 12996
1670 | Energy | Input Channel 16 reactive energy total | EQ_TOTAL_016_kvarh | kvarh | double | R | 13000
1671 | Energy | Input Channel 16 apparent energy | ES_016_kVAh | kVAh | double | R | 13004
1672 | Energy | Input Channel 17 active energy import | EP_IMP_017_kWh | kWh | double | R | 13008
1673 | Energy | Input Channel 17 active energy export | EP_EXP_017_kWh | kWh | double | R | 13012
1674 | Energy | Input Channel 17 active energy net | EP_NET_017_kWh | kWh | double | R | 13016
1675 | Energy | Input Channel 17 active energy total | EP_TOTAL_017_kWh | kWh | double | R | 13020
1676 | Energy | Input Channel 17 reactive energy import | EQ_IMP_017_kvarh | kvarh | double | R | 13024
1677 | Energy | Input Channel 17 reactive energy export | EQ_EXP_017_kvarh | kvarh | double | R | 13028
1678 | Energy | Input Channel 17 reactive energy net | EQ_NET_017_kvarh | kvarh | double | R | 13032
1679 | Energy | Input Channel 17 reactive energy total | EQ_TOTAL_017_kvarh | kvarh | double | R | 13036
1680 | Energy | Input Channel 17 apparent energy | ES_017_kVAh | kVAh | double | R | 13040
1681 | Energy | Input Channel 18 active energy import | EP_IMP_018_kWh | kWh | double | R | 13044
1682 | Energy | Input Channel 18 active energy export | EP_EXP_018_kWh | kWh | double | R | 13048
1683 | Energy | Input Channel 18 active energy net | EP_NET_018_kWh | kWh | double | R | 13052
1684 | Energy | Input Channel 18 active energy total | EP_TOTAL_018_kWh | kWh | double | R | 13056
1685 | Energy | Input Channel 18 reactive energy import | EQ_IMP_018_kvarh | kvarh | double | R | 13060
1686 | Energy | Input Channel 18 reactive energy export | EQ_EXP_018_kvarh | kvarh | double | R | 13064
1687 | Energy | Input Channel 18 reactive energy net | EQ_NET_018_kvarh | kvarh | double | R | 13068
1688 | Energy | Input Channel 18 reactive energy total | EQ_TOTAL_018_kvarh | kvarh | double | R | 13072
1689 | Energy | Input Channel 18 apparent energy | ES_018_kVAh | kVAh | double | R | 13076
1690 | Energy | Input Channel 19 active energy import | EP_IMP_019_kWh | kWh | double | R | 13080
1691 | Energy | Input Channel 19 active energy export | EP_EXP_019_kWh | kWh | double | R | 13084
1692 | Energy | Input Channel 19 active energy net | EP_NET_019_kWh | kWh | double | R | 13088
1693 | Energy | Input Channel 19 active energy total | EP_TOTAL_019_kWh | kWh | double | R | 13092
1694 | Energy | Input Channel 19 reactive energy import | EQ_IMP_019_kvarh | kvarh | double | R | 13096
1695 | Energy | Input Channel 19 reactive energy export | EQ_EXP_019_kvarh | kvarh | double | R | 13100
1696 | Energy | Input Channel 19 reactive energy net | EQ_NET_019_kvarh | kvarh | double | R | 13104
1697 | Energy | Input Channel 19 reactive energy total | EQ_TOTAL_019_kvarh | kvarh | double | R | 13108
1698 | Energy | Input Channel 19 apparent energy | ES_019_kVAh | kVAh | double | R | 13112
1699 | Energy | Input Channel 20 active energy import | EP_IMP_020_kWh | kWh | double | R | 13116
1700 | Energy | Input Channel 20 active energy export | EP_EXP_020_kWh | kWh | double | R | 13120
1701 | Energy | Input Channel 20 active energy net | EP_NET_020_kWh | kWh | double | R | 13124
1702 | Energy | Input Channel 20 active energy total | EP_TOTAL_020_kWh | kWh | double | R | 13128
1703 | Energy | Input Channel 20 reactive energy import | EQ_IMP_020_kvarh | kvarh | double | R | 13132
1704 | Energy | Input Channel 20 reactive energy export | EQ_EXP_020_kvarh | kvarh | double | R | 13136
1705 | Energy | Input Channel 20 reactive energy net | EQ_NET_020_kvarh | kvarh | double | R | 13140
1706 | Energy | Input Channel 20 reactive energy total | EQ_TOTAL_020_kvarh | kvarh | double | R | 13144
1707 | Energy | Input Channel 20 apparent energy | ES_020_kVAh | kVAh | double | R | 13148
1708 | Energy | Input Channel 21 active energy import | EP_IMP_021_kWh | kWh | double | R | 13152
1709 | Energy | Input Channel 21 active energy export | EP_EXP_021_kWh | kWh | double | R | 13156
1710 | Energy | Input Channel 21 active energy net | EP_NET_021_kWh | kWh | double | R | 13160
1711 | Energy | Input Channel 21 active energy total | EP_TOTAL_021_kWh | kWh | double | R | 13164
1712 | Energy | Input Channel 21 reactive energy import | EQ_IMP_021_kvarh | kvarh | double | R | 13168
1713 | Energy | Input Channel 21 reactive energy export | EQ_EXP_021_kvarh | kvarh | double | R | 13172
1714 | Energy | Input Channel 21 reactive energy net | EQ_NET_021_kvarh | kvarh | double | R | 13176
1715 | Energy | Input Channel 21 reactive energy total | EQ_TOTAL_021_kvarh | kvarh | double | R | 13180
1716 | Energy | Input Channel 21 apparent energy | ES_021_kVAh | kVAh | double | R | 13184
1717 | Energy | Input Channel 22 active energy import | EP_IMP_022_kWh | kWh | double | R | 13188
1718 | Energy | Input Channel 22 active energy export | EP_EXP_022_kWh | kWh | double | R | 13192
1719 | Energy | Input Channel 22 active energy net | EP_NET_022_kWh | kWh | double | R | 13196
1720 | Energy | Input Channel 22 active energy total | EP_TOTAL_022_kWh | kWh | double | R | 13200
1721 | Energy | Input Channel 22 reactive energy import | EQ_IMP_022_kvarh | kvarh | double | R | 13204
1722 | Energy | Input Channel 22 reactive energy export | EQ_EXP_022_kvarh | kvarh | double | R | 13208
1723 | Energy | Input Channel 22 reactive energy net | EQ_NET_022_kvarh | kvarh | double | R | 13212
1724 | Energy | Input Channel 22 reactive energy total | EQ_TOTAL_022_kvarh | kvarh | double | R | 13216
1725 | Energy | Input Channel 22 apparent energy | ES_022_kVAh | kVAh | double | R | 13220
1726 | Energy | Input Channel 23 active energy import | EP_IMP_023_kWh | kWh | double | R | 13224
1727 | Energy | Input Channel 23 active energy export | EP_EXP_023_kWh | kWh | double | R | 13228
1728 | Energy | Input Channel 23 active energy net | EP_NET_023_kWh | kWh | double | R | 13232
1729 | Energy | Input Channel 23 active energy total | EP_TOTAL_023_kWh | kWh | double | R | 13236
1730 | Energy | Input Channel 23 reactive energy import | EQ_IMP_023_kvarh | kvarh | double | R | 13240
1731 | Energy | Input Channel 23 reactive energy export | EQ_EXP_023_kvarh | kvarh | double | R | 13244
1732 | Energy | Input Channel 23 reactive energy net | EQ_NET_023_kvarh | kvarh | double | R | 13248
1733 | Energy | Input Channel 23 reactive energy total | EQ_TOTAL_023_kvarh | kvarh | double | R | 13252
1734 | Energy | Input Channel 23 apparent energy | ES_023_kVAh | kVAh | double | R | 13256
1735 | Energy | Input Channel 24 active energy import | EP_IMP_024_kWh | kWh | double | R | 13260
1736 | Energy | Input Channel 24 active energy export | EP_EXP_024_kWh | kWh | double | R | 13264
1737 | Energy | Input Channel 24 active energy net | EP_NET_024_kWh | kWh | double | R | 13268
1738 | Energy | Input Channel 24 active energy total | EP_TOTAL_024_kWh | kWh | double | R | 13272
1739 | Energy | Input Channel 24 reactive energy import | EQ_IMP_024_kvarh | kvarh | double | R | 13276
1740 | Energy | Input Channel 24 reactive energy export | EQ_EXP_024_kvarh | kvarh | double | R | 13280
1741 | Energy | Input Channel 24 reactive energy net | EQ_NET_024_kvarh | kvarh | double | R | 13284
1742 | Energy | Input Channel 24 reactive energy total | EQ_TOTAL_024_kvarh | kvarh | double | R | 13288
1743 | Energy | Input Channel 24 apparent energy | ES_024_kVAh | kVAh | double | R | 13292
1744 | Energy | User Channel 1 active energy import | EP_IMP_s001_kWh | kWh | double | R | 13296
1745 | Energy | User Channel 1 active energy export | EP_EXP_s001_kWh | kWh | double | R | 13300
1746 | Energy | User Channel 1 active energy net | EP_NET_s001_kWh | kWh | double | R | 13304
1747 | Energy | User Channel 1 active energy total | EP_TOTAL_s001_kWh | kWh | double | R | 13308
1748 | Energy | User Channel 1 reactive energy import | EQ_IMP_s001_kvarh | kvarh | double | R | 13312
1749 | Energy | User Channel 1 reactive energy export | EQ_EXP_s001_kvarh | kvarh | double | R | 13316
1750 | Energy | User Channel 1 reactive energy net | EQ_NET_s001_kvarh | kvarh | double | R | 13320
1751 | Energy | User Channel 1 reactive energy total | EQ_TOTAL_s001_kvarh | kvarh | double | R | 13324
1752 | Energy | User Channel 1 apparent energy | ES_s001_kVAh | kVAh | double | R | 13328
1753 | Energy | User Channel 2 active energy import | EP_IMP_s002_kWh | kWh | double | R | 13332
1754 | Energy | User Channel 2 active energy export | EP_EXP_s002_kWh | kWh | double | R | 13336
1755 | Energy | User Channel 2 active energy net | EP_NET_s002_kWh | kWh | double | R | 13340
1756 | Energy | User Channel 2 active energy total | EP_TOTAL_s002_kWh | kWh | double | R | 13344
1757 | Energy | User Channel 2 reactive energy import | EQ_IMP_s002_kvarh | kvarh | double | R | 13348
1758 | Energy | User Channel 2 reactive energy export | EQ_EXP_s002_kvarh | kvarh | double | R | 13352
1759 | Energy | User Channel 2 reactive energy net | EQ_NET_s002_kvarh | kvarh | double | R | 13356
1760 | Energy | User Channel 2 reactive energy total | EQ_TOTAL_s002_kvarh | kvarh | double | R | 13360
1761 | Energy | User Channel 2 apparent energy | ES_s002_kVAh | kVAh | double | R | 13364
1762 | Energy | User Channel 3 active energy import | EP_IMP_s003_kWh | kWh | double | R | 13368
1763 | Energy | User Channel 3 active energy export | EP_EXP_s003_kWh | kWh | double | R | 13372
1764 | Energy | User Channel 3 active energy net | EP_NET_s003_kWh | kWh | double | R | 13376
1765 | Energy | User Channel 3 active energy total | EP_TOTAL_s003_kWh | kWh | double | R | 13380
1766 | Energy | User Channel 3 reactive energy import | EQ_IMP_s003_kvarh | kvarh | double | R | 13384
1767 | Energy | User Channel 3 reactive energy export | EQ_EXP_s003_kvarh | kvarh | double | R | 13388
1768 | Energy | User Channel 3 reactive energy net | EQ_NET_s003_kvarh | kvarh | double | R | 13392
1769 | Energy | User Channel 3 reactive energy total | EQ_TOTAL_s003_kvarh | kvarh | double | R | 13396
1770 | Energy | User Channel 3 apparent energy | ES_s003_kVAh | kVAh | double | R | 13400
1771 | Energy | User Channel 4 active energy import | EP_IMP_s004_kWh | kWh | double | R | 13404
1772 | Energy | User Channel 4 active energy export | EP_EXP_s004_kWh | kWh | double | R | 13408
1773 | Energy | User Channel 4 active energy net | EP_NET_s004_kWh | kWh | double | R | 13412
1774 | Energy | User Channel 4 active energy total | EP_TOTAL_s004_kWh | kWh | double | R | 13416
1775 | Energy | User Channel 4 reactive energy import | EQ_IMP_s004_kvarh | kvarh | double | R | 13420
1776 | Energy | User Channel 4 reactive energy export | EQ_EXP_s004_kvarh | kvarh | double | R | 13424
1777 | Energy | User Channel 4 reactive energy net | EQ_NET_s004_kvarh | kvarh | double | R | 13428
1778 | Energy | User Channel 4 reactive energy total | EQ_TOTAL_s004_kvarh | kvarh | double | R | 13432
1779 | Energy | User Channel 4 apparent energy | ES_s004_kVAh | kVAh | double | R | 13436
1780 | Energy | User Channel 5 active energy import | EP_IMP_s005_kWh | kWh | double | R | 13440
1781 | Energy | User Channel 5 active energy export | EP_EXP_s005_kWh | kWh | double | R | 13444
1782 | Energy | User Channel 5 active energy net | EP_NET_s005_kWh | kWh | double | R | 13448
1783 | Energy | User Channel 5 active energy total | EP_TOTAL_s005_kWh | kWh | double | R | 13452
1784 | Energy | User Channel 5 reactive energy import | EQ_IMP_s005_kvarh | kvarh | double | R | 13456
1785 | Energy | User Channel 5 reactive energy export | EQ_EXP_s005_kvarh | kvarh | double | R | 13460
1786 | Energy | User Channel 5 reactive energy net | EQ_NET_s005_kvarh | kvarh | double | R | 13464
1787 | Energy | User Channel 5 reactive energy total | EQ_TOTAL_s005_kvarh | kvarh | double | R | 13468
1788 | Energy | User Channel 5 apparent energy | ES_s005_kVAh | kVAh | double | R | 13472
1789 | Energy | User Channel 6 active energy import | EP_IMP_s006_kWh | kWh | double | R | 13476
1790 | Energy | User Channel 6 active energy export | EP_EXP_s006_kWh | kWh | double | R | 13480
1791 | Energy | User Channel 6 active energy net | EP_NET_s006_kWh | kWh | double | R | 13484
1792 | Energy | User Channel 6 active energy total | EP_TOTAL_s006_kWh | kWh | double | R | 13488
1793 | Energy | User Channel 6 reactive energy import | EQ_IMP_s006_kvarh | kvarh | double | R | 13492
1794 | Energy | User Channel 6 reactive energy export | EQ_EXP_s006_kvarh | kvarh | double | R | 13496
1795 | Energy | User Channel 6 reactive energy net | EQ_NET_s006_kvarh | kvarh | double | R | 13500
1796 | Energy | User Channel 6 reactive energy total | EQ_TOTAL_s006_kvarh | kvarh | double | R | 13504
1797 | Energy | User Channel 6 apparent energy | ES_s006_kVAh | kVAh | double | R | 13508
1798 | Energy | User Channel 7 active energy import | EP_IMP_s007_kWh | kWh | double | R | 13512
1799 | Energy | User Channel 7 active energy export | EP_EXP_s007_kWh | kWh | double | R | 13516
1800 | Energy | User Channel 7 active energy net | EP_NET_s007_kWh | kWh | double | R | 13520
1801 | Energy | User Channel 7 active energy total | EP_TOTAL_s007_kWh | kWh | double | R | 13524
1802 | Energy | User Channel 7 reactive energy import | EQ_IMP_s007_kvarh | kvarh | double | R | 13528
1803 | Energy | User Channel 7 reactive energy export | EQ_EXP_s007_kvarh | kvarh | double | R | 13532
1804 | Energy | User Channel 7 reactive energy net | EQ_NET_s007_kvarh | kvarh | double | R | 13536
1805 | Energy | User Channel 7 reactive energy total | EQ_TOTAL_s007_kvarh | kvarh | double | R | 13540
1806 | Energy | User Channel 7 apparent energy | ES_s007_kVAh | kVAh | double | R | 13544
1807 | Energy | User Channel 8 active energy import | EP_IMP_s008_kWh | kWh | double | R | 13548
1808 | Energy | User Channel 8 active energy export | EP_EXP_s008_kWh | kWh | double | R | 13552
1809 | Energy | User Channel 8 active energy net | EP_NET_s008_kWh | kWh | double | R | 13556
1810 | Energy | User Channel 8 active energy total | EP_TOTAL_s008_kWh | kWh | double | R | 13560
1811 | Energy | User Channel 8 reactive energy import | EQ_IMP_s008_kvarh | kvarh | double | R | 13564
1812 | Energy | User Channel 8 reactive energy export | EQ_EXP_s008_kvarh | kvarh | double | R | 13568
1813 | Energy | User Channel 8 reactive energy net | EQ_NET_s008_kvarh | kvarh | double | R | 13572
1814 | Energy | User Channel 8 reactive energy total | EQ_TOTAL_s008_kvarh | kvarh | double | R | 13576
1815 | Energy | User Channel 8 apparent energy | ES_s008_kVAh | kVAh | double | R | 13580
1816 | Energy | User Channel 9 active energy import | EP_IMP_s009_kWh | kWh | double | R | 13584
1817 | Energy | User Channel 9 active energy export | EP_EXP_s009_kWh | kWh | double | R | 13588
1818 | Energy | User Channel 9 active energy net | EP_NET_s009_kWh | kWh | double | R | 13592
1819 | Energy | User Channel 9 active energy total | EP_TOTAL_s009_kWh | kWh | double | R | 13596
1820 | Energy | User Channel 9 reactive energy import | EQ_IMP_s009_kvarh | kvarh | double | R | 13600
1821 | Energy | User Channel 9 reactive energy export | EQ_EXP_s009_kvarh | kvarh | double | R | 13604
1822 | Energy | User Channel 9 reactive energy net | EQ_NET_s009_kvarh | kvarh | double | R | 13608
1823 | Energy | User Channel 9 reactive energy total | EQ_TOTAL_s009_kvarh | kvarh | double | R | 13612
1824 | Energy | User Channel 9 apparent energy | ES_s009_kVAh | kVAh | double | R | 13616
1825 | Energy | User Channel 10 active energy import | EP_IMP_s010_kWh | kWh | double | R | 13620
1826 | Energy | User Channel 10 active energy export | EP_EXP_s010_kWh | kWh | double | R | 13624
1827 | Energy | User Channel 10 active energy net | EP_NET_s010_kWh | kWh | double | R | 13628
1828 | Energy | User Channel 10 active energy total | EP_TOTAL_s010_kWh | kWh | double | R | 13632
1829 | Energy | User Channel 10 reactive energy import | EQ_IMP_s010_kvarh | kvarh | double | R | 13636
1830 | Energy | User Channel 10 reactive energy export | EQ_EXP_s010_kvarh | kvarh | double | R | 13640
1831 | Energy | User Channel 10 reactive energy net | EQ_NET_s010_kvarh | kvarh | double | R | 13644
1832 | Energy | User Channel 10 reactive energy total | EQ_TOTAL_s010_kvarh | kvarh | double | R | 13648
1833 | Energy | User Channel 10 apparent energy | ES_s010_kVAh | kVAh | double | R | 13652
1834 | Energy | User Channel 11 active energy import | EP_IMP_s011_kWh | kWh | double | R | 13656
1835 | Energy | User Channel 11 active energy export | EP_EXP_s011_kWh | kWh | double | R | 13660
1836 | Energy | User Channel 11 active energy net | EP_NET_s011_kWh | kWh | double | R | 13664
1837 | Energy | User Channel 11 active energy total | EP_TOTAL_s011_kWh | kWh | double | R | 13668
1838 | Energy | User Channel 11 reactive energy import | EQ_IMP_s011_kvarh | kvarh | double | R | 13672
1839 | Energy | User Channel 11 reactive energy export | EQ_EXP_s011_kvarh | kvarh | double | R | 13676
1840 | Energy | User Channel 11 reactive energy net | EQ_NET_s011_kvarh | kvarh | double | R | 13680
1841 | Energy | User Channel 11 reactive energy total | EQ_TOTAL_s011_kvarh | kvarh | double | R | 13684
1842 | Energy | User Channel 11 apparent energy | ES_s011_kVAh | kVAh | double | R | 13688
1843 | Energy | User Channel 12 active energy import | EP_IMP_s012_kWh | kWh | double | R | 13692
1844 | Energy | User Channel 12 active energy export | EP_EXP_s012_kWh | kWh | double | R | 13696
1845 | Energy | User Channel 12 active energy net | EP_NET_s012_kWh | kWh | double | R | 13700
1846 | Energy | User Channel 12 active energy total | EP_TOTAL_s012_kWh | kWh | double | R | 13704
1847 | Energy | User Channel 12 reactive energy import | EQ_IMP_s012_kvarh | kvarh | double | R | 13708
1848 | Energy | User Channel 12 reactive energy export | EQ_EXP_s012_kvarh | kvarh | double | R | 13712
1849 | Energy | User Channel 12 reactive energy net | EQ_NET_s012_kvarh | kvarh | double | R | 13716
1850 | Energy | User Channel 12 reactive energy total | EQ_TOTAL_s012_kvarh | kvarh | double | R | 13720
1851 | Energy | User Channel 12 apparent energy | ES_s012_kVAh | kVAh | double | R | 13724
1852 | DI | DI1 pulse count | DI_PC_001 |  | uint32 | RW | 25600
1853 | DI | DI2 pulse count | DI_PC_002 |  | uint32 | RW | 25602
1854 | DI | DI3 pulse count | DI_PC_003 |  | uint32 | RW | 25604
1855 | DI | DI4 pulse count | DI_PC_004 |  | uint32 | RW | 25606
1856 | DI | DI1 status | DI_ST_001 |  | uint16 | R | 0
1857 | DI | DI2 status | DI_ST_002 |  | uint16 | R | 1
1858 | DI | DI3 status | DI_ST_003 |  | uint16 | R | 2
1859 | DI | DI4 status | DI_ST_004 |  | uint16 | R | 3
1860 | DO | DO1 status | DO_ST_001 |  | uint16 | RW | 0
1861 | DO | DO2 status | DO_ST_002 |  | uint16 | RW | 1
1862 | DO | DO3 status | DO_ST_003 |  | uint16 | RW | 2
1863 | DO | DO4 status | DO_ST_004 |  | uint16 | RW | 3
1864 | DO | DO5 status | DO_ST_005 |  | uint16 | RW | 4
1865 | DO | DO6 status | DO_ST_006 |  | uint16 | RW | 5
1866 | DO | DO7 status | DO_ST_007 |  | uint16 | RW | 6
1867 | DO | DO8 status | DO_ST_008 |  | uint16 | RW | 7
1868 | RO | RO1 status | RO_ST_001 |  | uint16 | RW | 32
1869 | RO | RO2 status | RO_ST_002 |  | uint16 | RW | 33

## AcuIOM-01
No. | Parameter Category | Parameter Name | Parameter Key | Unit | Data Type | R/W | Modbus Address (Dec)
1 | AI value | AI1 input original data | AI1_input_original_data |  | float32 | R | 13568
2 | AI value | AI2 input original data | AI2_input_original_data |  | float32 | R | 13570
3 | AI value | AI3 input original data | AI3_input_original_data |  | float32 | R | 13572
4 | AI value | AI4 input original data | AI4_input_original_data |  | float32 | R | 13574
5 | AI value | AI5 input original data | AI5_input_original_data |  | float32 | R | 13576
6 | AI value | AI6 input original data | AI6_input_original_data |  | float32 | R | 13578
7 | AI value | AI7 input original data | AI7_input_original_data |  | float32 | R | 13580
8 | AI value | AI8 input original data | AI8_input_original_data |  | float32 | R | 13582
9 | AI value | AI1 physical measurement reading | AI1_physical_measurement_reading |  | float32 | R | 14080
10 | AI value | AI2 physical measurement reading | AI2_physical_measurement_reading |  | float32 | R | 14082
11 | AI value | AI3 physical measurement reading | AI3_physical_measurement_reading |  | float32 | R | 14084
12 | AI value | AI4 physical measurement reading | AI4_physical_measurement_reading |  | float32 | R | 14086
13 | AI value | AI5 physical measurement reading | AI5_physical_measurement_reading |  | float32 | R | 14088
14 | AI value | AI6 physical measurement reading | AI6_physical_measurement_reading |  | float32 | R | 14090
15 | AI value | AI7 physical measurement reading | AI7_physical_measurement_reading |  | float32 | R | 14092
16 | AI value | AI8 physical measurement reading | AI8_physical_measurement_reading |  | float32 | R | 14094

## AcuIOM-02
No. | Parameter Category | Parameter Name | Parameter Key | Unit | Data Type | R/W | Modbus Address (Dec)
1 | AI value | AI1 input original data | AI1_input_original_data |  | float32 | R | 13568
2 | AI value | AI2 input original data | AI2_input_original_data |  | float32 | R | 13570
3 | AI value | AI3 input original data | AI3_input_original_data |  | float32 | R | 13572
4 | AI value | AI4 input original data | AI4_input_original_data |  | float32 | R | 13574
5 | AI value | AI5 input original data | AI5_input_original_data |  | float32 | R | 13576
6 | AI value | AI6 input original data | AI6_input_original_data |  | float32 | R | 13578
7 | AI value | AI7 input original data | AI7_input_original_data |  | float32 | R | 13580
8 | AI value | AI8 input original data | AI8_input_original_data |  | float32 | R | 13582
9 | AI value | AI9 input original data | AI9_input_original_data |  | float32 | R | 13584
10 | AI value | AI10 input original data | AI10_input_original_data |  | float32 | R | 13586
11 | AI value | AI11 input original data | AI11_input_original_data |  | float32 | R | 13588
12 | AI value | AI12 input original data | AI12_input_original_data |  | float32 | R | 13590
13 | AI value | AI13 input original data | AI13_input_original_data |  | float32 | R | 13592
14 | AI value | AI14 input original data | AI14_input_original_data |  | float32 | R | 13594
15 | AI value | AI15 input original data | AI15_input_original_data |  | float32 | R | 13596
16 | AI value | AI16 input original data | AI16_input_original_data |  | float32 | R | 13598
17 | AI value | AI1 physical measurement reading | AI1_physical_measurement_reading |  | float32 | R | 14080
18 | AI value | AI2 physical measurement reading | AI2_physical_measurement_reading |  | float32 | R | 14082
19 | AI value | AI3 physical measurement reading | AI3_physical_measurement_reading |  | float32 | R | 14084
20 | AI value | AI4 physical measurement reading | AI4_physical_measurement_reading |  | float32 | R | 14086
21 | AI value | AI5 physical measurement reading | AI5_physical_measurement_reading |  | float32 | R | 14088
22 | AI value | AI6 physical measurement reading | AI6_physical_measurement_reading |  | float32 | R | 14090
23 | AI value | AI7 physical measurement reading | AI7_physical_measurement_reading |  | float32 | R | 14092
24 | AI value | AI8 physical measurement reading | AI8_physical_measurement_reading |  | float32 | R | 14094
25 | AI value | AI9 physical measurement reading | AI9_physical_measurement_reading |  | float32 | R | 14096
26 | AI value | AI10 physical measurement reading | AI10_physical_measurement_reading |  | float32 | R | 14098
27 | AI value | AI11 physical measurement reading | AI11_physical_measurement_reading |  | float32 | R | 14100
28 | AI value | AI12 physical measurement reading | AI12_physical_measurement_reading |  | float32 | R | 14102
29 | AI value | AI13 physical measurement reading | AI13_physical_measurement_reading |  | float32 | R | 14104
30 | AI value | AI14 physical measurement reading | AI14_physical_measurement_reading |  | float32 | R | 14106
31 | AI value | AI15 physical measurement reading | AI15_physical_measurement_reading |  | float32 | R | 14108
32 | AI value | AI16 physical measurement reading | AI16_physical_measurement_reading |  | float32 | R | 14110

## AcuIOM-03
No. | Parameter Category | Parameter Name | Parameter Key | Unit | Data Type | R/W | Modbus Address (Dec)
1 | DI status | DI 1 Status | DI_1_Status |  | uint16 | R | 0
2 | DI status | DI 2 Status | DI_2_Status |  | uint16 | R | 1
3 | DI status | DI 3 Status | DI_3_Status |  | uint16 | R | 2
4 | DI status | DI 4 Status | DI_4_Status |  | uint16 | R | 3
5 | DI status | DI 5 Status | DI_5_Status |  | uint16 | R | 4
6 | DI status | DI 6 Status | DI_6_Status |  | uint16 | R | 5
7 | DI status | DI 7 Status | DI_7_Status |  | uint16 | R | 6
8 | DI status | DI 8 Status | DI_8_Status |  | uint16 | R | 7
9 | DI status | DI 9 Status | DI_9_Status |  | uint16 | R | 8
10 | DI status | DI 10 Status | DI_10_Status |  | uint16 | R | 9
11 | DI status | DI 11 Status | DI_11_Status |  | uint16 | R | 10
12 | DI status | DI 12 Status | DI_12_Status |  | uint16 | R | 11
13 | DI status | DI 13 Status | DI_13_Status |  | uint16 | R | 12
14 | DI status | DI 14 Status | DI_14_Status |  | uint16 | R | 13
15 | DI pulse count | DI1 pulse count | Conf_DI1_pulse_count |  | uint32 | RW | 8704
16 | DI pulse count | DI2 pulse count | Conf_DI2_pulse_count |  | uint32 | RW | 8706
17 | DI pulse count | DI3 pulse count | Conf_DI3_pulse_count |  | uint32 | RW | 8708
18 | DI pulse count | DI4 pulse count | Conf_DI4_pulse_count |  | uint32 | RW | 8710
19 | DI pulse count | DI5 pulse count | Conf_DI5_pulse_count |  | uint32 | RW | 8712
20 | DI pulse count | DI6 pulse count | Conf_DI6_pulse_count |  | uint32 | RW | 8714
21 | DI pulse count | DI7 pulse count | Conf_DI7_pulse_count |  | uint32 | RW | 8716
22 | DI pulse count | DI8 pulse count | Conf_DI8_pulse_count |  | uint32 | RW | 8718
23 | DI pulse count | DI9 pulse count | Conf_DI9_pulse_count |  | uint32 | RW | 8720
24 | DI pulse count | DI10 pulse count | Conf_DI10_pulse_count |  | uint32 | RW | 8722
25 | DI pulse count | DI11 pulse count | Conf_DI11_pulse_count |  | uint32 | RW | 8724
26 | DI pulse count | DI12 pulse count | Conf_DI12_pulse_count |  | uint32 | RW | 8726
27 | DI pulse count | DI13 pulse count | Conf_DI13_pulse_count |  | uint32 | RW | 8728
28 | DI pulse count | DI14 pulse count | Conf_DI14_pulse_count |  | uint32 | RW | 8730
29 | DO status | DO1 Status | DO1_Status |  | uint16 | RW | 0
30 | DO status | DO2 Status | DO2_Status |  | uint16 | RW | 1
31 | RO status | RO1 Status | RO1_Status |  | uint16 | RW | 32
32 | RO status | RO2 Status | RO2_Status |  | uint16 | RW | 33

## AcuIOM-04
No. | Parameter Category | Parameter Name | Parameter Key | Unit | Data Type | R/W | Modbus Address (Dec)
1 | DI status | DI 1 Status | DI_1_Status |  | uint16 | R | 0
2 | DI status | DI 2 Status | DI_2_Status |  | uint16 | R | 1
3 | DI status | DI 3 Status | DI_3_Status |  | uint16 | R | 2
4 | DI status | DI 4 Status | DI_4_Status |  | uint16 | R | 3
5 | DI status | DI 5 Status | DI_5_Status |  | uint16 | R | 4
6 | DI status | DI 6 Status | DI_6_Status |  | uint16 | R | 5
7 | DI status | DI 7 Status | DI_7_Status |  | uint16 | R | 6
8 | DI status | DI 8 Status | DI_8_Status |  | uint16 | R | 7
9 | DI status | DI 9 Status | DI_9_Status |  | uint16 | R | 8
10 | DI status | DI 10 Status | DI_10_Status |  | uint16 | R | 9
11 | DI status | DI 11 Status | DI_11_Status |  | uint16 | R | 10
12 | DI status | DI 12 Status | DI_12_Status |  | uint16 | R | 11
13 | DI status | DI 13 Status | DI_13_Status |  | uint16 | R | 12
14 | DI status | DI 14 Status | DI_14_Status |  | uint16 | R | 13
15 | DI status | DI 15 Status | DI_15_Status |  | uint16 | R | 14
16 | DI status | DI 16 Status | DI_16_Status |  | uint16 | R | 15
17 | DI status | DI 17 Status | DI_17_Status |  | uint16 | R | 16
18 | DI status | DI 18 Status | DI_18_Status |  | uint16 | R | 17
19 | DI status | DI 19 Status | DI_19_Status |  | uint16 | R | 18
20 | DI status | DI 20 Status | DI_20_Status |  | uint16 | R | 19
21 | DI status | DI 21 Status | DI_21_Status |  | uint16 | R | 20
22 | DI status | DI 22 Status | DI_22_Status |  | uint16 | R | 21
23 | DI status | DI 23 Status | DI_23_Status |  | uint16 | R | 22
24 | DI status | DI 24 Status | DI_24_Status |  | uint16 | R | 23
25 | DI status | DI 25 Status | DI_25_Status |  | uint16 | R | 24
26 | DI status | DI 26 Status | DI_26_Status |  | uint16 | R | 25
27 | DI status | DI 27 Status | DI_27_Status |  | uint16 | R | 26
28 | DI status | DI 28 Status | DI_28_Status |  | uint16 | R | 27
29 | DI pulse count | DI1 pulse count | Conf_DI1_pulse_count |  | uint32 | RW | 8704
30 | DI pulse count | DI2 pulse count | Conf_DI2_pulse_count |  | uint32 | RW | 8706
31 | DI pulse count | DI3 pulse count | Conf_DI3_pulse_count |  | uint32 | RW | 8708
32 | DI pulse count | DI4 pulse count | Conf_DI4_pulse_count |  | uint32 | RW | 8710
33 | DI pulse count | DI5 pulse count | Conf_DI5_pulse_count |  | uint32 | RW | 8712
34 | DI pulse count | DI6 pulse count | Conf_DI6_pulse_count |  | uint32 | RW | 8714
35 | DI pulse count | DI7 pulse count | Conf_DI7_pulse_count |  | uint32 | RW | 8716
36 | DI pulse count | DI8 pulse count | Conf_DI8_pulse_count |  | uint32 | RW | 8718
37 | DI pulse count | DI9 pulse count | Conf_DI9_pulse_count |  | uint32 | RW | 8720
38 | DI pulse count | DI10 pulse count | Conf_DI10_pulse_count |  | uint32 | RW | 8722
39 | DI pulse count | DI11 pulse count | Conf_DI11_pulse_count |  | uint32 | RW | 8724
40 | DI pulse count | DI12 pulse count | Conf_DI12_pulse_count |  | uint32 | RW | 8726
41 | DI pulse count | DI13 pulse count | Conf_DI13_pulse_count |  | uint32 | RW | 8728
42 | DI pulse count | DI14 pulse count | Conf_DI14_pulse_count |  | uint32 | RW | 8730
43 | DI pulse count | DI15 pulse count | Conf_DI15_pulse_count |  | uint32 | RW | 8732
44 | DI pulse count | DI16 pulse count | Conf_DI16_pulse_count |  | uint32 | RW | 8734
45 | DI pulse count | DI17 pulse count | Conf_DI17_pulse_count |  | uint32 | RW | 8736
46 | DI pulse count | DI18 pulse count | Conf_DI18_pulse_count |  | uint32 | RW | 8738
47 | DI pulse count | DI19 pulse count | Conf_DI19_pulse_count |  | uint32 | RW | 8740
48 | DI pulse count | DI20 pulse count | Conf_DI20_pulse_count |  | uint32 | RW | 8742
49 | DI pulse count | DI21 pulse count | Conf_DI21_pulse_count |  | uint32 | RW | 8744
50 | DI pulse count | DI22 pulse count | Conf_DI22_pulse_count |  | uint32 | RW | 8746
51 | DI pulse count | DI23 pulse count | Conf_DI23_pulse_count |  | uint32 | RW | 8748
52 | DI pulse count | DI24 pulse count | Conf_DI24_pulse_count |  | uint32 | RW | 8750
53 | DI pulse count | DI25 pulse count | Conf_DI25_pulse_count |  | uint32 | RW | 8752
54 | DI pulse count | DI26 pulse count | Conf_DI26_pulse_count |  | uint32 | RW | 8754
55 | DI pulse count | DI27 pulse count | Conf_DI27_pulse_count |  | uint32 | RW | 8756
56 | DI pulse count | DI28 pulse count | Conf_DI28_pulse_count |  | uint32 | RW | 8758
57 | DO status | DO1 Status | DO1_Status |  | uint16 | RW | 0
58 | DO status | DO2 Status | DO2_Status |  | uint16 | RW | 1
59 | DO status | DO3 Status | DO3_Status |  | uint16 | RW | 2
60 | DO status | DO4 Status | DO4_Status |  | uint16 | RW | 3
61 | RO status | RO1 Status | RO1_Status |  | uint16 | RW | 32
62 | RO status | RO2 Status | RO2_Status |  | uint16 | RW | 33

## Note
Notes:
Date: October 22, 2026
Product Name: AcuRev-4100-WEB2
Product Model Number: ACM-41-WEB2
Application Software Version: v1.00p01
Firmware Revision: v1.01p05
BACnet Protocol Version: 1
BACnet Protocol Revision: 1
Summary
Device | Description | Parameter Category | Number of Parameters
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Real-time | 236
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Demand | 240
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Sequence | 91
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | THD | 114
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Harmonics | 810
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Energy | 360
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | DI | 8
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | DO | 8
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | RO | 2
AcuRev 4100 (Basic Module) | AcuRev 4100 meter | Subtotal | 1869
AcuIOM-01 | AcuIOM-AIAO | AI value | 16
AcuIOM-01 | AcuIOM-AIAO | Subtotal | 16
AcuIOM-02 | AcuIOM-AIAO | AI value | 32
AcuIOM-02 | AcuIOM-AIAO | Subtotal | 32
AcuIOM-03 | AcuIOM-DIDO | DI status | 14
AcuIOM-03 | AcuIOM-DIDO | DI pulse count | 14
AcuIOM-03 | AcuIOM-DIDO | DO status | 2
AcuIOM-03 | AcuIOM-DIDO | RO status | 2
AcuIOM-03 | AcuIOM-DIDO | Subtotal | 32
AcuIOM-04 | AcuIOM-DIDO | DI status | 28
AcuIOM-04 | AcuIOM-DIDO | DI pulse count | 28
AcuIOM-04 | AcuIOM-DIDO | DO status | 4
AcuIOM-04 | AcuIOM-DIDO | RO status | 2
AcuIOM-04 | AcuIOM-DIDO | Subtotal | 62
Total |  |  | 2011