## AcuRev4100
BACnet Points List AcuRev4100
Firmware v1.03p06. List generated 2026-05-26 from firmware source. BACnet/IP and BACnet MS/TP expose the same objects.
ID | Name | Description | Object Type | Data type | RW | Unit
RealTime
1 | Freq_rms | Frequency | Object Analog Input | float | R | Hertz
2 | Ua_rms | Phase A Voltage | Object Analog Input | float | R | Volts
3 | Ub_rms | Phase B Voltage | Object Analog Input | float | R | Volts
4 | Uc_rms | Phase C Voltage | Object Analog Input | float | R | Volts
5 | Uavg_rms | Phase Average Voltage | Object Analog Input | float | R | Volts
6 | Uab_rms | Line Voltage AB | Object Analog Input | float | R | Volts
7 | Ubc_rms | Line Voltage BC | Object Analog Input | float | R | Volts
8 | Uca_rms | Line Voltage CA | Object Analog Input | float | R | Volts
9 | Ulavg_rms | Average Line Voltage | Object Analog Input | float | R | Volts
10 | UaAng_rms | Phase A Voltage Angle | Object Analog Input | float | R | Degrees Phase
11 | UbAng_rms | Phase B Voltage Angle | Object Analog Input | float | R | Degrees Phase
12 | UcAng_rms | Phase C Voltage Angle | Object Analog Input | float | R | Degrees Phase
13 | Ia_rms | Phase A Current | Object Analog Input | float | R | Amperes
14 | Pa_rms | Phase A Active Power | Object Analog Input | float | R | Kilowatts
15 | Qa_rms | Phase A Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
16 | Sa_rms | Phase A Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
17 | LNa_rms | Phase A Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
18 | PFa_rms | Phase A Power Factor | Object Analog Input | float | R | Power Factor
19 | Ib_rms | Phase B Current | Object Analog Input | float | R | Amperes
20 | Pb_rms | Phase B Active Power | Object Analog Input | float | R | Kilowatts
21 | Qb_rms | Phase B Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
22 | Sb_rms | Phase B Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
23 | LNb_rms | Phase B Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
24 | PFb_rms | Phase B Power Factor | Object Analog Input | float | R | Power Factor
25 | Ic_rms | Phase C Current | Object Analog Input | float | R | Amperes
26 | Pc_rms | Phase C Active Power | Object Analog Input | float | R | Kilowatts
27 | Qc_rms | Phase C Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
28 | Sc_rms | Phase C Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
29 | LNc_rms | Phase C Load Nature (0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
30 | PFc_rms | Phase C Power Factor | Object Analog Input | float | R | Power Factor
31 | Isys_rms | System Average Current | Object Analog Input | float | R | Amperes
32 | Psys_rms | System Active Power | Object Analog Input | float | R | Kilowatts
33 | Qsys_rms | System Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
34 | Ssys_rms | System Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
35 | LNsys_rms | System Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
36 | PFsys_rms | System Power Factor | Object Analog Input | float | R | Power Factor
37 | Ichn1_rms | Input Channel 1 Current | Object Analog Input | float | R | Amperes
38 | Pchn1_rms | Input Channel 1 Active Power | Object Analog Input | float | R | Kilowatts
39 | Qchn1_rms | Input Channel 1 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
40 | Schn1_rms | Input Channel 1 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
41 | LNchn1_rms | Input Channel 1 Load Nature (0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
42 | PFchn1_rms | Input Channel 1 Power Factor | Object Analog Input | float | R | Power Factor
43 | Angchn1_rms | Input Channel 1 Current Phase Angle | Object Analog Input | float | R | Degrees Phase
44-204 |  | Input Channel 2-24 basic parameters | Object Analog Input |  | R
205 | Iusr1_rms | User Channel 1 Current | Object Analog Input | float | R | Amperes
206 | Pusr1_rms | User Channel 1 Active Power | Object Analog Input | float | R | Kilowatts
207 | Qusr1_rms | User Channel 1 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
S | Susr1_rms | User Channel 1 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
209 | LNusr1_rms | User Channel 1 Load Nature (0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units
210 | PFusr1_rms | User Channel 1 Power Factor | Object Analog Input | float | R | Power Factor
205-276 |  | User Channel 2-12 basic parameters | Object Analog Input |  | R
Demand
277 | Ia_dema | Phase A Current Demand | Object Analog Input | float | R | Amperes
278 | PaImp_dema | Phase A Import Active Power Demand | Object Analog Input | float | R | Kilowatts
279 | PaExp_dema | Phase A Export Active Power Demand | Object Analog Input | float | R | Kilowatts
280 | QaImp_dema | Phase A Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
281 | QaExp_dema | Phase A Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
282 | Sa_dema | Phase A Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
283 | Ib_dema | Phase B Current Demand | Object Analog Input | float | R | Amperes
284 | PbImp_dema | Phase B Import Active Power Demand | Object Analog Input | float | R | Kilowatts
285 | PbExp_dema | Phase B Export Active Power Demand | Object Analog Input | float | R | Kilowatts
286 | QbImp_dema | Phase B Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
287 | QbExp_dema | Phase B Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
288 | Sb_dema | Phase B Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
289 | Ic_dema | Phase C Current Demand | Object Analog Input | float | R | Amperes
290 | PcImp_dema | Phase C Import Active Power Demand | Object Analog Input | float | R | Kilowatts
291 | PcExp_dema | Phase C Export Active Power Demand | Object Analog Input | float | R | Kilowatts
292 | QcImp_dema | Phase C Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
293 | QcExp_dema | Phase C Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
294 | Sc_dema | Phase C Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
295 | Isys_dema | System Average Current Demand | Object Analog Input | float | R | Amperes
296 | PsysImp_dema | System Import Active Power Demand | Object Analog Input | float | R | Kilowatts
297 | PsysExp_dema | System Export Active Power Demand | Object Analog Input | float | R | Kilowatts
298 | QsysImp_dema | System Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
299 | QsysExp_dema | System Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
300 | Ssys_dema | System Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
Input Demand Channel
301 | Ichn1_dema | Input Channel 1 Current Demand | Object Analog Input | float | R | Amperes
302 | Pchn1Imp_dema | Input Channel 1 Import Active Power Demand | Object Analog Input | float | R | Kilowatts
303 | Pchn1Exp_dema | Input Channel 1 Export Active Power Demand | Object Analog Input | float | R | Kilowatts
304 | Qchn1Imp_dema | Input Channel 1 Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
305 | Qchn1Exp_dema | Input Channel 1 Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
306 | Schn1_dema | Input Channel 1 Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
307-444 |  | Input Channel 2-24 Demands | Object Analog Input | float | R
User Channel Demand
445 | Iusr1_dema | User Channel 1 Current Demand | Object Analog Input | float | R | Amperes
446 | Pusr1Imp_dema | User Channel 1 Import Active Power Demand | Object Analog Input | float | R | Kilowatts
447 | Pusr1Exp_dema | User Channel 1 Export Active Power Demand | Object Analog Input | float | R | Kilowatts
448 | Qusr1Imp_dema | User Channel 1 Import Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
449 | Qusr1Exp_dema | User Channel 1 Export Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
450 | Susr1_dema | User Channel 1 Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
451-516 |  | User Channel 2-12 Demands | Object Analog Input | float | R
System Power Quality
517 | Vpsm_pq | Voltage Positive Sequence Magnitude | Object Analog Input | float | R | Volts
518 | Vzsm_pq | Voltage Zero Sequence Magnitude | Object Analog Input | float | R | Volts
519 | Vnsm_pq | Voltage Negative Sequence Magnitude | Object Analog Input | float | R | Volts
520 | Vpsa_pq | Voltage Positive Sequence Angle | Object Analog Input | float | R | Degrees Phase
521 | Vzsa_pq | Voltage Zero Sequence Angle | Object Analog Input | float | R | Degrees Phase
522 | Vnsa_pq | Voltage Negative Sequence Angle | Object Analog Input | float | R | Degrees Phase
523 | Vufm_pq | Voltage Unbalance Factor Magnitude | Object Analog Input | float | R | Percent
524 | VThd_A_pq | Phase A Voltage THD | Object Analog Input | float | R | Percent
525 | VThdO_A_pq | Phase A Voltage THD Odd | Object Analog Input | float | R | Percent
526 | VThdE_A_pq | Phase A Voltage THD Even | Object Analog Input | float | R | Percent
527 | VCF_A_pq | Phase A Voltage Crest Factor | Object Analog Input | float | R | No Units
528 | VThff_A_pq | Phase A Voltage THFF Factor | Object Analog Input | float | R | Percent
529 | VThd_B_pq | Phase B Voltage THD | Object Analog Input | float | R | Percent
530 | VThdO_B_pq | Phase B Voltage THD Odd | Object Analog Input | float | R | Percent
531 | VThdE_B_pq | Phase B Voltage THD Even | Object Analog Input | float | R | Percent
532 | VCF_B_pq | Phase B Voltage Crest Factor | Object Analog Input | float | R | No Units
533 | VThff_B_pq | Phase B Voltage THFF Factor | Object Analog Input | float | R | Percent
534 | VThd_C_pq | Phase C Voltage THD | Object Analog Input | float | R | Percent
535 | VThdO_C_pq | Phase C Voltage THD Odd | Object Analog Input | float | R | Percent
536 | VThdE_C_pq | Phase C Voltage THD Even | Object Analog Input | float | R | Percent
537 | VCF_C_pq | Phase C Voltage Crest Factor | Object Analog Input | float | R | No Units
538 | VThff_C_pq | Phase C Voltage THFF Factor | Object Analog Input | float | R | Percent
539 | VavgThd_pq | Average Voltage THD | Object Analog Input | float | R | Percent
540 | VavgThdO_pq | Average Voltage THD Odd | Object Analog Input | float | R | Percent
541 | VavgThdE_pq | Average Voltage THD Even | Object Analog Input | float | R | Percent
Input Channel Power Quality
542 | Ichn1Thd_pq | Input Channel 1 Current THD | Object Analog Input | float | R | Percent
543 | Ichn1ThdO_pq | Input Channel 1 Current THD Odd | Object Analog Input | float | R | Percent
544 | Ichn1ThdE_pq | Input Channel 1 Current THD Even | Object Analog Input | float | R | Percent
545 | Ichn1KF_pq | Input Channel 1 Current K Factor | Object Analog Input | float | R | No Units
546-637 |  | Input channel 2-24 power quality | Object Analog Input | float | R
User Channel Power Quality
638 | Iuser1psm_pq | User Channel 1 Current Positive Sequence Magnitude | Object Analog Input | float | R | Amperes
639 | Iuser1zsm_pq | User Channel 1 Current Zero Sequence Magnitude | Object Analog Input | float | R | Amperes
640 | Iuser1nsm_pq | User Channel 1 Current Negative Sequence Magnitude | Object Analog Input | float | R | Amperes
641 | Iuser1psa_pq | User Channel 1 Current Positive Sequence Angle | Object Analog Input | float | R | Degrees Phase
642 | Iuser1zsa_pq | User Channel 1 Current Zero Sequence Angle | Object Analog Input | float | R | Degrees Phase
643 | Iuser1nsa_pq | User Channel 1 Current Negative Sequence Angle | Object Analog Input | float | R | Degrees Phase
644 | Iuser1ufm_pq | User Channel 1 Current Unbalance Factor Magnitude | Object Analog Input | float | R | Percent
645-721 |  | User channel 2-12 power quality | Object Analog Input | float | R
System Energy
1 | PaImp_eng | Phase A active energy import | Object Large Analog Value | double | R | Kilowatt Hours
2 | PaExp_eng | Phase A active energy export | Object Large Analog Value | double | R | Kilowatt Hours
3 | PaNet_eng | Phase A active energy net | Object Large Analog Value | double | R | Kilowatt Hours
4 | PaTotal_eng | Phase A active energy total | Object Large Analog Value | double | R | Kilowatt Hours
5 | QaImp_eng | Phase A reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
6 | QaExp_eng | Phase A reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
7 | QaNet_eng | Phase A reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
8 | QaTotal_eng | Phase A reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
9 | Sa_eng | Phase A apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
10 | PbImp_eng | Phase B active energy import | Object Large Analog Value | double | R | Kilowatt Hours
11 | PbExp_eng | Phase B active energy export | Object Large Analog Value | double | R | Kilowatt Hours
12 | PbNet_eng | Phase B active energy net | Object Large Analog Value | double | R | Kilowatt Hours
13 | PbTotal_eng | Phase B active energy total | Object Large Analog Value | double | R | Kilowatt Hours
14 | QbImp_eng | Phase B reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
15 | QbExp_eng | Phase B reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
16 | QbNet_eng | Phase B reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
17 | QbTotal_eng | Phase B reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
18 | Sb_eng | Phase B apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
19 | PcImp_eng | Phase C active energy import | Object Large Analog Value | double | R | Kilowatt Hours
20 | PcExp_eng | Phase C active energy export | Object Large Analog Value | double | R | Kilowatt Hours
21 | PcNet_eng | Phase C active energy net | Object Large Analog Value | double | R | Kilowatt Hours
22 | PcTotal_eng | Phase C active energy total | Object Large Analog Value | double | R | Kilowatt Hours
23 | QcImp_eng | Phase C reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
24 | QcExp_eng | Phase C reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
25 | QcNet_eng | Phase C reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
26 | QcTotal_eng | Phase C reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
27 | Sc_eng | Phase C apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
28 | PsysImp_eng | System active energy import | Object Large Analog Value | double | R | Kilowatt Hours
29 | PsysExp_eng | System active energy export | Object Large Analog Value | double | R | Kilowatt Hours
30 | PsysNet_eng | System active energy net | Object Large Analog Value | double | R | Kilowatt Hours
31 | PsysTotal_eng | System active energy total | Object Large Analog Value | double | R | Kilowatt Hours
32 | QsysImp_eng | System reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
33 | QsysExp_eng | System reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
34 | QsysNet_eng | System reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
35 | QsysTotal_eng | System reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
36 | Ssys_eng | System apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
Input Channel Energy
37 | PChn1Imp_eng | Input Channel 1 active energy import | Object Large Analog Value | double | R | Kilowatt Hours
38 | PChn1Exp_eng | Input Channel 1 active energy export | Object Large Analog Value | double | R | Kilowatt Hours
39 | PChn1Net_eng | Input Channel 1 active energy net | Object Large Analog Value | double | R | Kilowatt Hours
40 | PChn1Total_eng | Input Channel 1 active energy total | Object Large Analog Value | double | R | Kilowatt Hours
41 | QChn1Imp_eng | Input Channel 1 reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
42 | QChn1Exp_eng | Input Channel 1 reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
43 | QChn1Net_eng | Input Channel 1 reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
44 | QChn1Total_eng | Input Channel 1 reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
45 | SChn1_eng | Input Channel 1 apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
46-252 |  | Input Channel 2-24 energy | Object Large Analog Value | double | R
User Channel Energy
253 | PUser1Imp_eng | User Channel 1 active energy import | Object Large Analog Value | double | R | Kilowatt Hours
254 | PUser1Exp_eng | User Channel 1 active energy export | Object Large Analog Value | double | R | Kilowatt Hours
255 | PUser1Net_eng | User Channel 1 active energy net | Object Large Analog Value | double | R | Kilowatt Hours
256 | PUser1Total_eng | User Channel 1 active energy total | Object Large Analog Value | double | R | Kilowatt Hours
257 | QUser1Imp_eng | User Channel 1 reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
258 | QUser1Exp_eng | User Channel 1 reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
259 | QUser1Net_eng | User Channel 1 reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
260 | QUser1Total_eng | User Channel 1 reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive
261 | SUser1_eng | User Channel 1 apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours
262 | 262-360 | User Channel 2-12 energy | Object Large Analog Value | double | R

## Note
Notes
Source:
AcuRev4100- firmware v1.03p06 Date :May 26, 2026 BACnet Protocol Version: 1 BACnet Protocol Revision: 26 Objects are defined by the parameter mapping and BACnet mapper tables in the firmware database (createParamDefault).
Object counts:
Analog Input: 721 objects (instances 1-721)
Large Analog Value: 360 objects (instances 1-360)
Availability:
RealTime Objects( Start 1 -End 276 ),Length :276
Demand Objects (Start 277;End 516), Length :240
Power Quality Objects (Start 517;End 721),Length :205
Energy Objects( Start 1 -End 360),Length :360