## Sheet1
BACnet Points List Acuvim-3
Firmware v1.04p13 (released 2026-09-22). List generated 2026-10-06 from firmware source. BACnet/IP and BACnet MS/TP expose the same objects.
Object ID | Object Name | Object Description | Object Type | Units
Real-Time Parameters (200 ms RMS)
1 | System Frequency | System Frequency | Analog Input | Hz
2 | Phase A Line-to-Neutral Voltage | Phase A Line-to-Neutral Voltage | Analog Input | V
3 | Phase B Line-to-Neutral Voltage | Phase B Line-to-Neutral Voltage | Analog Input | V
4 | Phase C Line-to-Neutral Voltage | Phase C Line-to-Neutral Voltage | Analog Input | V
5 | Average Line-to-Neutral Voltage | Average Line-to-Neutral Voltage | Analog Input | V
6 | Phase AB Line-to-Line Voltage | Phase AB Line-to-Line Voltage | Analog Input | V
7 | Phase BC Line-to-Line Voltage | Phase BC Line-to-Line Voltage | Analog Input | V
8 | Phase CA Line-to-Line Voltage | Phase CA Line-to-Line Voltage | Analog Input | V
9 | Average Line-to-Line Voltage | Average Line-to-Line Voltage | Analog Input | V
10 | Phase A Current | Phase A Current | Analog Input | A
11 | Phase B Current | Phase B Current | Analog Input | A
12 | Phase C Current | Phase C Current | Analog Input | A
13 | Phase N Current | Phase N Current | Analog Input | A
14 | Average Current | Average Current | Analog Input | A
15 | Phase A Active Power | Phase A Active Power | Analog Input | kW
16 | Phase B Active Power | Phase B Active Power | Analog Input | kW
17 | Phase C Active Power | Phase C Active Power | Analog Input | kW
18 | System Active Power | System Active Power | Analog Input | kW
19 | Phase A Reactive Power | Phase A Reactive Power | Analog Input | kvar
20 | Phase B Reactive Power | Phase B Reactive Power | Analog Input | kvar
21 | Phase C Reactive Power | Phase C Reactive Power | Analog Input | kvar
22 | System Reactive Power | System Reactive Power | Analog Input | kvar
23 | Phase A Apparent Power | Phase A Apparent Power | Analog Input | kVA
24 | Phase B Apparent Power | Phase B Apparent Power | Analog Input | kVA
25 | Phase C Apparent Power | Phase C Apparent Power | Analog Input | kVA
26 | System Apparent Power | System Apparent Power | Analog Input | kVA
27 | Phase A Load Nature | Phase A Load Nature | Analog Input | no units
28 | Phase B Load Nature | Phase B Load Nature | Analog Input | no units
29 | Phase C Load Nature | Phase C Load Nature | Analog Input | no units
30 | System Load Nature | System Load Nature | Analog Input | no units
31 | Phase A Power Factor | Phase A Power Factor | Analog Input | PF
32 | Phase B Power Factor | Phase B Power Factor | Analog Input | PF
33 | Phase C Power Factor | Phase C Power Factor | Analog Input | PF
34 | System Power Factor | System Power Factor | Analog Input | PF
35 | Phase A Leading Power Factor | Phase A Leading Power Factor | Analog Input | PF
36 | Phase B Leading Power Factor | Phase B Leading Power Factor | Analog Input | PF
37 | Phase C Leading Power Factor | Phase C Leading Power Factor | Analog Input | PF
38 | System Leading Power Factor | System Leading Power Factor | Analog Input | PF
39 | Phase A Lagging Power Factor | Phase A Lagging Power Factor | Analog Input | PF
40 | Phase B Lagging Power Factor | Phase B Lagging Power Factor | Analog Input | PF
41 | Phase C Lagging Power Factor | Phase C Lagging Power Factor | Analog Input | PF
42 | System Lagging Power Factor | System Lagging Power Factor | Analog Input | PF
43 | Phase A Line-to-Neutral Voltage Phase Angle | Phase A Line-to-Neutral Voltage Phase Angle | Analog Input | degrees
44 | Phase B Line-to-Neutral Voltage Phase Angle | Phase B Line-to-Neutral Voltage Phase Angle | Analog Input | degrees
45 | Phase C Line-to-Neutral Voltage Phase Angle | Phase C Line-to-Neutral Voltage Phase Angle | Analog Input | degrees
46 | Phase AB Line-to-Line Voltage Phase Angle | Phase AB Line-to-Line Voltage Phase Angle | Analog Input | degrees
47 | Phase BC Line-to-Line Voltage Phase Angle | Phase BC Line-to-Line Voltage Phase Angle | Analog Input | degrees
48 | Phase CA Line-to-Line Voltage Phase Angle | Phase CA Line-to-Line Voltage Phase Angle | Analog Input | degrees
49 | Phase A Current Phase Angle | Phase A Current Phase Angle | Analog Input | degrees
50 | Phase B Current Phase Angle | Phase B Current Phase Angle | Analog Input | degrees
51 | Phase C Current Phase Angle | Phase C Current Phase Angle | Analog Input | degrees
Sequence Components - Magnitude
52 | 200ms RMS Voltage Positive Sequence Magnitude | Voltage Positive Sequence Magnitude | Analog Input | V
53 | 200ms RMS Voltage Zero Sequence Magnitude | Voltage Zero Sequence Magnitude | Analog Input | V
54 | 200ms RMS Voltage Negative Sequence Magnitude | Voltage Negative Sequence Magnitude | Analog Input | V
55 | 200ms RMS Voltage Zero Sequence Ratio Magnitude | Voltage Zero Sequence Ratio Magnitude | Analog Input | %
56 | 200ms RMS Voltage Unbalance Factor Magnitude | Voltage Unbalance Factor Magnitude | Analog Input | %
57 | 200ms RMS Current Positive Sequence Magnitude | Current Positive Sequence Magnitude | Analog Input | A
58 | 200ms RMS Current Zero Sequence Magnitude | Current Zero Sequence Magnitude | Analog Input | A
59 | 200ms RMS Current Negative Sequence Magnitude | Current Negative Sequence Magnitude | Analog Input | A
60 | 200ms RMS Current Zero Sequence Ratio Magnitude | Current Zero Sequence Ratio Magnitude | Analog Input | %
61 | 200ms RMS Current Unbalance Factor Magnitude | Current Unbalance Factor Magnitude | Analog Input | %
Sequence Components - Angle
62 | 200ms RMS Voltage Positive Sequence Angle | Voltage Positive Sequence Angle | Analog Input | V
63 | 200ms RMS Voltage Zero Sequence Angle | Voltage Zero Sequence Angle | Analog Input | V
64 | 200ms RMS Voltage Negative Sequence Angle | Voltage Negative Sequence Angle | Analog Input | V
65 | 200ms RMS Current Positive Sequence Angle | Current Positive Sequence Angle | Analog Input | A
66 | 200ms RMS Current Zero Sequence Angle | Current Zero Sequence Angle | Analog Input | A
67 | 200ms RMS Current Negative Sequence Angle | Current Negative Sequence Angle | Analog Input | A
Real-Time Parameters (200 ms RMS) - Phase Angles, Unbalance, THD
68 | Phase A Voltage THD | Phase A Voltage THD | Analog Input | %
69 | Phase B Voltage THD | Phase B Voltage THD | Analog Input | %
70 | Phase C Voltage THD | Phase C Voltage THD | Analog Input | %
71 | Phase A Voltage THD Odd | Phase A Voltage THD Odd | Analog Input | %
72 | Phase B Voltage THD Odd | Phase B Voltage THD Odd | Analog Input | %
73 | Phase C Voltage THD Odd | Phase C Voltage THD Odd | Analog Input | %
74 | Phase A Voltage THD Even | Phase A Voltage THD Even | Analog Input | %
75 | Phase B Voltage THD Even | Phase B Voltage THD Even | Analog Input | %
76 | Phase C Voltage THD Even | Phase C Voltage THD Even | Analog Input | %
77 | Phase A Voltage Crest Factor | Phase A Voltage Crest Factor | Analog Input | %
78 | Phase B Voltage Crest Factor | Phase B Voltage Crest Factor | Analog Input | %
79 | Phase C Voltage Crest Factor | Phase C Voltage Crest Factor | Analog Input | %
80 | Phase A Current THD | Phase A Current THD | Analog Input | %
81 | Phase B Current THD | Phase B Current THD | Analog Input | %
82 | Phase C Current THD | Phase C Current THD | Analog Input | %
83 | Phase N Current THD | Phase N Current THD | Analog Input | %
84 | Phase A Current THD Odd | Phase A Current THD Odd | Analog Input | %
85 | Phase B Current THD Odd | Phase B Current THD Odd | Analog Input | %
86 | Phase C Current THD Odd | Phase C Current THD Odd | Analog Input | %
87 | Phase N Current THD Odd | Phase N Current THD Odd | Analog Input | %
88 | Phase A Current THD Even | Phase A Current THD Even | Analog Input | %
89 | Phase B Current THD Even | Phase B Current THD Even | Analog Input | %
90 | Phase C Current THD Even | Phase C Current THD Even | Analog Input | %
91 | Phase N Current THD Even | Phase N Current THD Even | Analog Input | %
92 | Phase A Current TDD | Phase A Current TDD | Analog Input | %
93 | Phase B Current TDD | Phase B Current TDD | Analog Input | %
94 | Phase C Current TDD | Phase C Current TDD | Analog Input | %
95 | Phase N Current TDD | Phase N Current TDD | Analog Input | %
96 | Phase A Current Crest-Factor | Phase A Current Crest-Factor | Analog Input | %
97 | Phase B Current Crest-Factor | Phase B Current Crest-Factor | Analog Input | %
98 | Phase C Current Crest-Factor | Phase C Current Crest-Factor | Analog Input | %
99 | Phase N Current Crest-Factor | Phase N Current Crest-Factor | Analog Input | %
100 | Phase A Current K-Factor | Phase A Current K-Factor | Analog Input | %
101 | Phase B Current K-Factor | Phase B Current K-Factor | Analog Input | %
102 | Phase C Current K-Factor | Phase C Current K-Factor | Analog Input | %
103 | Phase N Current K-Factor | Phase N Current K-Factor | Analog Input | %
Harmonics - Magnitude
104 | Phase A 1st Voltage Magnitude Harmonics | Phase A 1st Voltage Magnitude Harmonics | Analog Input | %
105 | Phase B 1st Voltage Magnitude Harmonics | Phase B 1st Voltage Magnitude Harmonics | Analog Input | %
106 | Phase C 1st Voltage Magnitude Harmonics | Phase C 1st Voltage Magnitude Harmonics | Analog Input | %
107 | Phase A 1st Current Magnitude Harmonics | Phase A 1st Current Magnitude Harmonics | Analog Input | %
108 | Phase B 1st Current Magnitude Harmonics | Phase B 1st Current Magnitude Harmonics | Analog Input | %
109 | Phase C 1st Current Magnitude Harmonics | Phase C 1st Current Magnitude Harmonics | Analog Input | %
110 | Phase N 1st Current Magnitude Harmonics | Phase N 1st Current Magnitude Harmonics | Analog Input | %
111 | Phase A 2nd Voltage Magnitude Harmonics | Phase A 2nd Voltage Magnitude Harmonics | Analog Input | %
112 | Phase B 2nd Voltage Magnitude Harmonics | Phase B 2nd Voltage Magnitude Harmonics | Analog Input | %
113 | Phase C 2nd Voltage Magnitude Harmonics | Phase C 2nd Voltage Magnitude Harmonics | Analog Input | %
114 | Phase A 2nd Current Magnitude Harmonics | Phase A 2nd Current Magnitude Harmonics | Analog Input | %
115 | Phase B 2nd Current Magnitude Harmonics | Phase B 2nd Current Magnitude Harmonics | Analog Input | %
116 | Phase C 2nd Current Magnitude Harmonics | Phase C 2nd Current Magnitude Harmonics | Analog Input | %
117 | Phase N 2nd Current Magnitude Harmonics | Phase N 2nd Current Magnitude Harmonics | Analog Input | %
118 | Phase A 3rd Voltage Magnitude Harmonics | Phase A 3rd Voltage Magnitude Harmonics | Analog Input | %
119 | Phase B 3rd Voltage Magnitude Harmonics | Phase B 3rd Voltage Magnitude Harmonics | Analog Input | %
120 | Phase C 3rd Voltage Magnitude Harmonics | Phase C 3rd Voltage Magnitude Harmonics | Analog Input | %
121 | Phase A 3rd Current Magnitude Harmonics | Phase A 3rd Current Magnitude Harmonics | Analog Input | %
122 | Phase B 3rd Current Magnitude Harmonics | Phase B 3rd Current Magnitude Harmonics | Analog Input | %
123 | Phase C 3rd Current Magnitude Harmonics | Phase C 3rd Current Magnitude Harmonics | Analog Input | %
124 | Phase N 3rd Current Magnitude Harmonics | Phase N 3rd Current Magnitude Harmonics | Analog Input | %
125 | Phase A 4th Voltage Magnitude Harmonics | Phase A 4th Voltage Magnitude Harmonics | Analog Input | %
126 | Phase B 4th Voltage Magnitude Harmonics | Phase B 4th Voltage Magnitude Harmonics | Analog Input | %
127 | Phase C 4th Voltage Magnitude Harmonics | Phase C 4th Voltage Magnitude Harmonics | Analog Input | %
128 | Phase A 4th Current Magnitude Harmonics | Phase A 4th Current Magnitude Harmonics | Analog Input | %
129 | Phase B 4th Current Magnitude Harmonics | Phase B 4th Current Magnitude Harmonics | Analog Input | %
130 | Phase C 4th Current Magnitude Harmonics | Phase C 4th Current Magnitude Harmonics | Analog Input | %
131 | Phase N 4th Current Magnitude Harmonics | Phase N 4th Current Magnitude Harmonics | Analog Input | %
132 | Phase A 5th Voltage Magnitude Harmonics | Phase A 5th Voltage Magnitude Harmonics | Analog Input | %
133 | Phase B 5th Voltage Magnitude Harmonics | Phase B 5th Voltage Magnitude Harmonics | Analog Input | %
134 | Phase C 5th Voltage Magnitude Harmonics | Phase C 5th Voltage Magnitude Harmonics | Analog Input | %
135 | Phase A 5th Current Magnitude Harmonics | Phase A 5th Current Magnitude Harmonics | Analog Input | %
136 | Phase B 5th Current Magnitude Harmonics | Phase B 5th Current Magnitude Harmonics | Analog Input | %
137 | Phase C 5th Current Magnitude Harmonics | Phase C 5th Current Magnitude Harmonics | Analog Input | %
138 | Phase N 5th Current Magnitude Harmonics | Phase N 5th Current Magnitude Harmonics | Analog Input | %
139 | Phase A 6th Voltage Magnitude Harmonics | Phase A 6th Voltage Magnitude Harmonics | Analog Input | %
140 | Phase B 6th Voltage Magnitude Harmonics | Phase B 6th Voltage Magnitude Harmonics | Analog Input | %
141 | Phase C 6th Voltage Magnitude Harmonics | Phase C 6th Voltage Magnitude Harmonics | Analog Input | %
142 | Phase A 6th Current Magnitude Harmonics | Phase A 6th Current Magnitude Harmonics | Analog Input | %
143 | Phase B 6th Current Magnitude Harmonics | Phase B 6th Current Magnitude Harmonics | Analog Input | %
144 | Phase C 6th Current Magnitude Harmonics | Phase C 6th Current Magnitude Harmonics | Analog Input | %
145 | Phase N 6th Current Magnitude Harmonics | Phase N 6th Current Magnitude Harmonics | Analog Input | %
146 | Phase A 7th Voltage Magnitude Harmonics | Phase A 7th Voltage Magnitude Harmonics | Analog Input | %
147 | Phase B 7th Voltage Magnitude Harmonics | Phase B 7th Voltage Magnitude Harmonics | Analog Input | %
148 | Phase C 7th Voltage Magnitude Harmonics | Phase C 7th Voltage Magnitude Harmonics | Analog Input | %
149 | Phase A 7th Current Magnitude Harmonics | Phase A 7th Current Magnitude Harmonics | Analog Input | %
150 | Phase B 7th Current Magnitude Harmonics | Phase B 7th Current Magnitude Harmonics | Analog Input | %
151 | Phase C 7th Current Magnitude Harmonics | Phase C 7th Current Magnitude Harmonics | Analog Input | %
152 | Phase N 7th Current Magnitude Harmonics | Phase N 7th Current Magnitude Harmonics | Analog Input | %
153 | Phase A 8th Voltage Magnitude Harmonics | Phase A 8th Voltage Magnitude Harmonics | Analog Input | %
154 | Phase B 8th Voltage Magnitude Harmonics | Phase B 8th Voltage Magnitude Harmonics | Analog Input | %
155 | Phase C 8th Voltage Magnitude Harmonics | Phase C 8th Voltage Magnitude Harmonics | Analog Input | %
156 | Phase A 8th Current Magnitude Harmonics | Phase A 8th Current Magnitude Harmonics | Analog Input | %
157 | Phase B 8th Current Magnitude Harmonics | Phase B 8th Current Magnitude Harmonics | Analog Input | %
158 | Phase C 8th Current Magnitude Harmonics | Phase C 8th Current Magnitude Harmonics | Analog Input | %
159 | Phase N 8th Current Magnitude Harmonics | Phase N 8th Current Magnitude Harmonics | Analog Input | %
160 | Phase A 9th Voltage Magnitude Harmonics | Phase A 9th Voltage Magnitude Harmonics | Analog Input | %
161 | Phase B 9th Voltage Magnitude Harmonics | Phase B 9th Voltage Magnitude Harmonics | Analog Input | %
162 | Phase C 9th Voltage Magnitude Harmonics | Phase C 9th Voltage Magnitude Harmonics | Analog Input | %
163 | Phase A 9th Current Magnitude Harmonics | Phase A 9th Current Magnitude Harmonics | Analog Input | %
164 | Phase B 9th Current Magnitude Harmonics | Phase B 9th Current Magnitude Harmonics | Analog Input | %
165 | Phase C 9th Current Magnitude Harmonics | Phase C 9th Current Magnitude Harmonics | Analog Input | %
166 | Phase N 9th Current Magnitude Harmonics | Phase N 9th Current Magnitude Harmonics | Analog Input | %
167 | Phase A 10th Voltage Magnitude Harmonics | Phase A 10th Voltage Magnitude Harmonics | Analog Input | %
168 | Phase B 10th Voltage Magnitude Harmonics | Phase B 10th Voltage Magnitude Harmonics | Analog Input | %
169 | Phase C 10th Voltage Magnitude Harmonics | Phase C 10th Voltage Magnitude Harmonics | Analog Input | %
170 | Phase A 10th Current Magnitude Harmonics | Phase A 10th Current Magnitude Harmonics | Analog Input | %
171 | Phase B 10th Current Magnitude Harmonics | Phase B 10th Current Magnitude Harmonics | Analog Input | %
172 | Phase C 10th Current Magnitude Harmonics | Phase C 10th Current Magnitude Harmonics | Analog Input | %
173 | Phase N 10th Current Magnitude Harmonics | Phase N 10th Current Magnitude Harmonics | Analog Input | %
174 | Phase A 11st Voltage Magnitude Harmonics | Phase A 11st Voltage Magnitude Harmonics | Analog Input | %
175 | Phase B 11st Voltage Magnitude Harmonics | Phase B 11st Voltage Magnitude Harmonics | Analog Input | %
176 | Phase C 11st Voltage Magnitude Harmonics | Phase C 11st Voltage Magnitude Harmonics | Analog Input | %
177 | Phase A 11st Current Magnitude Harmonics | Phase A 11st Current Magnitude Harmonics | Analog Input | %
178 | Phase B 11st Current Magnitude Harmonics | Phase B 11st Current Magnitude Harmonics | Analog Input | %
179 | Phase C 11st Current Magnitude Harmonics | Phase C 11st Current Magnitude Harmonics | Analog Input | %
180 | Phase N 11st Current Magnitude Harmonics | Phase N 11st Current Magnitude Harmonics | Analog Input | %
181 | Phase A 12nd Voltage Magnitude Harmonics | Phase A 12nd Voltage Magnitude Harmonics | Analog Input | %
182 | Phase B 12nd Voltage Magnitude Harmonics | Phase B 12nd Voltage Magnitude Harmonics | Analog Input | %
183 | Phase C 12nd Voltage Magnitude Harmonics | Phase C 12nd Voltage Magnitude Harmonics | Analog Input | %
184 | Phase A 12nd Current Magnitude Harmonics | Phase A 12nd Current Magnitude Harmonics | Analog Input | %
185 | Phase B 12nd Current Magnitude Harmonics | Phase B 12nd Current Magnitude Harmonics | Analog Input | %
186 | Phase C 12nd Current Magnitude Harmonics | Phase C 12nd Current Magnitude Harmonics | Analog Input | %
187 | Phase N 12nd Current Magnitude Harmonics | Phase N 12nd Current Magnitude Harmonics | Analog Input | %
188 | Phase A 13rd Voltage Magnitude Harmonics | Phase A 13rd Voltage Magnitude Harmonics | Analog Input | %
189 | Phase B 13rd Voltage Magnitude Harmonics | Phase B 13rd Voltage Magnitude Harmonics | Analog Input | %
190 | Phase C 13rd Voltage Magnitude Harmonics | Phase C 13rd Voltage Magnitude Harmonics | Analog Input | %
191 | Phase A 13rd Current Magnitude Harmonics | Phase A 13rd Current Magnitude Harmonics | Analog Input | %
192 | Phase B 13rd Current Magnitude Harmonics | Phase B 13rd Current Magnitude Harmonics | Analog Input | %
193 | Phase C 13rd Current Magnitude Harmonics | Phase C 13rd Current Magnitude Harmonics | Analog Input | %
194 | Phase N 13rd Current Magnitude Harmonics | Phase N 13rd Current Magnitude Harmonics | Analog Input | %
195 | Phase A 14th Voltage Magnitude Harmonics | Phase A 14th Voltage Magnitude Harmonics | Analog Input | %
196 | Phase B 14th Voltage Magnitude Harmonics | Phase B 14th Voltage Magnitude Harmonics | Analog Input | %
197 | Phase C 14th Voltage Magnitude Harmonics | Phase C 14th Voltage Magnitude Harmonics | Analog Input | %
198 | Phase A 14th Current Magnitude Harmonics | Phase A 14th Current Magnitude Harmonics | Analog Input | %
199 | Phase B 14th Current Magnitude Harmonics | Phase B 14th Current Magnitude Harmonics | Analog Input | %
200 | Phase C 14th Current Magnitude Harmonics | Phase C 14th Current Magnitude Harmonics | Analog Input | %
201 | Phase N 14th Current Magnitude Harmonics | Phase N 14th Current Magnitude Harmonics | Analog Input | %
202 | Phase A 15th Voltage Magnitude Harmonics | Phase A 15th Voltage Magnitude Harmonics | Analog Input | %
203 | Phase B 15th Voltage Magnitude Harmonics | Phase B 15th Voltage Magnitude Harmonics | Analog Input | %
204 | Phase C 15th Voltage Magnitude Harmonics | Phase C 15th Voltage Magnitude Harmonics | Analog Input | %
205 | Phase A 15th Current Magnitude Harmonics | Phase A 15th Current Magnitude Harmonics | Analog Input | %
206 | Phase B 15th Current Magnitude Harmonics | Phase B 15th Current Magnitude Harmonics | Analog Input | %
207 | Phase C 15th Current Magnitude Harmonics | Phase C 15th Current Magnitude Harmonics | Analog Input | %
208 | Phase N 15th Current Magnitude Harmonics | Phase N 15th Current Magnitude Harmonics | Analog Input | %
209 | Phase A 16th Voltage Magnitude Harmonics | Phase A 16th Voltage Magnitude Harmonics | Analog Input | %
210 | Phase B 16th Voltage Magnitude Harmonics | Phase B 16th Voltage Magnitude Harmonics | Analog Input | %
211 | Phase C 16th Voltage Magnitude Harmonics | Phase C 16th Voltage Magnitude Harmonics | Analog Input | %
212 | Phase A 16th Current Magnitude Harmonics | Phase A 16th Current Magnitude Harmonics | Analog Input | %
213 | Phase B 16th Current Magnitude Harmonics | Phase B 16th Current Magnitude Harmonics | Analog Input | %
214 | Phase C 16th Current Magnitude Harmonics | Phase C 16th Current Magnitude Harmonics | Analog Input | %
215 | Phase N 16th Current Magnitude Harmonics | Phase N 16th Current Magnitude Harmonics | Analog Input | %
216 | Phase A 17th Voltage Magnitude Harmonics | Phase A 17th Voltage Magnitude Harmonics | Analog Input | %
217 | Phase B 17th Voltage Magnitude Harmonics | Phase B 17th Voltage Magnitude Harmonics | Analog Input | %
218 | Phase C 17th Voltage Magnitude Harmonics | Phase C 17th Voltage Magnitude Harmonics | Analog Input | %
219 | Phase A 17th Current Magnitude Harmonics | Phase A 17th Current Magnitude Harmonics | Analog Input | %
220 | Phase B 17th Current Magnitude Harmonics | Phase B 17th Current Magnitude Harmonics | Analog Input | %
221 | Phase C 17th Current Magnitude Harmonics | Phase C 17th Current Magnitude Harmonics | Analog Input | %
222 | Phase N 17th Current Magnitude Harmonics | Phase N 17th Current Magnitude Harmonics | Analog Input | %
223 | Phase A 18th Voltage Magnitude Harmonics | Phase A 18th Voltage Magnitude Harmonics | Analog Input | %
224 | Phase B 18th Voltage Magnitude Harmonics | Phase B 18th Voltage Magnitude Harmonics | Analog Input | %
225 | Phase C 18th Voltage Magnitude Harmonics | Phase C 18th Voltage Magnitude Harmonics | Analog Input | %
226 | Phase A 18th Current Magnitude Harmonics | Phase A 18th Current Magnitude Harmonics | Analog Input | %
227 | Phase B 18th Current Magnitude Harmonics | Phase B 18th Current Magnitude Harmonics | Analog Input | %
228 | Phase C 18th Current Magnitude Harmonics | Phase C 18th Current Magnitude Harmonics | Analog Input | %
229 | Phase N 18th Current Magnitude Harmonics | Phase N 18th Current Magnitude Harmonics | Analog Input | %
230 | Phase A 19th Voltage Magnitude Harmonics | Phase A 19th Voltage Magnitude Harmonics | Analog Input | %
231 | Phase B 19th Voltage Magnitude Harmonics | Phase B 19th Voltage Magnitude Harmonics | Analog Input | %
232 | Phase C 19th Voltage Magnitude Harmonics | Phase C 19th Voltage Magnitude Harmonics | Analog Input | %
233 | Phase A 19th Current Magnitude Harmonics | Phase A 19th Current Magnitude Harmonics | Analog Input | %
234 | Phase B 19th Current Magnitude Harmonics | Phase B 19th Current Magnitude Harmonics | Analog Input | %
235 | Phase C 19th Current Magnitude Harmonics | Phase C 19th Current Magnitude Harmonics | Analog Input | %
236 | Phase N 19th Current Magnitude Harmonics | Phase N 19th Current Magnitude Harmonics | Analog Input | %
237 | Phase A 20th Voltage Magnitude Harmonics | Phase A 20th Voltage Magnitude Harmonics | Analog Input | %
238 | Phase B 20th Voltage Magnitude Harmonics | Phase B 20th Voltage Magnitude Harmonics | Analog Input | %
239 | Phase C 20th Voltage Magnitude Harmonics | Phase C 20th Voltage Magnitude Harmonics | Analog Input | %
240 | Phase A 20th Current Magnitude Harmonics | Phase A 20th Current Magnitude Harmonics | Analog Input | %
241 | Phase B 20th Current Magnitude Harmonics | Phase B 20th Current Magnitude Harmonics | Analog Input | %
242 | Phase C 20th Current Magnitude Harmonics | Phase C 20th Current Magnitude Harmonics | Analog Input | %
243 | Phase N 20th Current Magnitude Harmonics | Phase N 20th Current Magnitude Harmonics | Analog Input | %
244 | Phase A 21st Voltage Magnitude Harmonics | Phase A 21st Voltage Magnitude Harmonics | Analog Input | %
245 | Phase B 21st Voltage Magnitude Harmonics | Phase B 21st Voltage Magnitude Harmonics | Analog Input | %
246 | Phase C 21st Voltage Magnitude Harmonics | Phase C 21st Voltage Magnitude Harmonics | Analog Input | %
247 | Phase A 21st Current Magnitude Harmonics | Phase A 21st Current Magnitude Harmonics | Analog Input | %
248 | Phase B 21st Current Magnitude Harmonics | Phase B 21st Current Magnitude Harmonics | Analog Input | %
249 | Phase C 21st Current Magnitude Harmonics | Phase C 21st Current Magnitude Harmonics | Analog Input | %
250 | Phase N 21st Current Magnitude Harmonics | Phase N 21st Current Magnitude Harmonics | Analog Input | %
251 | Phase A 22nd Voltage Magnitude Harmonics | Phase A 22nd Voltage Magnitude Harmonics | Analog Input | %
252 | Phase B 22nd Voltage Magnitude Harmonics | Phase B 22nd Voltage Magnitude Harmonics | Analog Input | %
253 | Phase C 22nd Voltage Magnitude Harmonics | Phase C 22nd Voltage Magnitude Harmonics | Analog Input | %
254 | Phase A 22nd Current Magnitude Harmonics | Phase A 22nd Current Magnitude Harmonics | Analog Input | %
255 | Phase B 22nd Current Magnitude Harmonics | Phase B 22nd Current Magnitude Harmonics | Analog Input | %
256 | Phase C 22nd Current Magnitude Harmonics | Phase C 22nd Current Magnitude Harmonics | Analog Input | %
257 | Phase N 22nd Current Magnitude Harmonics | Phase N 22nd Current Magnitude Harmonics | Analog Input | %
258 | Phase A 23rd Voltage Magnitude Harmonics | Phase A 23rd Voltage Magnitude Harmonics | Analog Input | %
259 | Phase B 23rd Voltage Magnitude Harmonics | Phase B 23rd Voltage Magnitude Harmonics | Analog Input | %
260 | Phase C 23rd Voltage Magnitude Harmonics | Phase C 23rd Voltage Magnitude Harmonics | Analog Input | %
261 | Phase A 23rd Current Magnitude Harmonics | Phase A 23rd Current Magnitude Harmonics | Analog Input | %
262 | Phase B 23rd Current Magnitude Harmonics | Phase B 23rd Current Magnitude Harmonics | Analog Input | %
263 | Phase C 23rd Current Magnitude Harmonics | Phase C 23rd Current Magnitude Harmonics | Analog Input | %
264 | Phase N 23rd Current Magnitude Harmonics | Phase N 23rd Current Magnitude Harmonics | Analog Input | %
265 | Phase A 24th Voltage Magnitude Harmonics | Phase A 24th Voltage Magnitude Harmonics | Analog Input | %
266 | Phase B 24th Voltage Magnitude Harmonics | Phase B 24th Voltage Magnitude Harmonics | Analog Input | %
267 | Phase C 24th Voltage Magnitude Harmonics | Phase C 24th Voltage Magnitude Harmonics | Analog Input | %
268 | Phase A 24th Current Magnitude Harmonics | Phase A 24th Current Magnitude Harmonics | Analog Input | %
269 | Phase B 24th Current Magnitude Harmonics | Phase B 24th Current Magnitude Harmonics | Analog Input | %
270 | Phase C 24th Current Magnitude Harmonics | Phase C 24th Current Magnitude Harmonics | Analog Input | %
271 | Phase N 24th Current Magnitude Harmonics | Phase N 24th Current Magnitude Harmonics | Analog Input | %
272 | Phase A 25th Voltage Magnitude Harmonics | Phase A 25th Voltage Magnitude Harmonics | Analog Input | %
273 | Phase B 25th Voltage Magnitude Harmonics | Phase B 25th Voltage Magnitude Harmonics | Analog Input | %
274 | Phase C 25th Voltage Magnitude Harmonics | Phase C 25th Voltage Magnitude Harmonics | Analog Input | %
275 | Phase A 25th Current Magnitude Harmonics | Phase A 25th Current Magnitude Harmonics | Analog Input | %
276 | Phase B 25th Current Magnitude Harmonics | Phase B 25th Current Magnitude Harmonics | Analog Input | %
277 | Phase C 25th Current Magnitude Harmonics | Phase C 25th Current Magnitude Harmonics | Analog Input | %
278 | Phase N 25th Current Magnitude Harmonics | Phase N 25th Current Magnitude Harmonics | Analog Input | %
279 | Phase A 26th Voltage Magnitude Harmonics | Phase A 26th Voltage Magnitude Harmonics | Analog Input | %
280 | Phase B 26th Voltage Magnitude Harmonics | Phase B 26th Voltage Magnitude Harmonics | Analog Input | %
281 | Phase C 26th Voltage Magnitude Harmonics | Phase C 26th Voltage Magnitude Harmonics | Analog Input | %
282 | Phase A 26th Current Magnitude Harmonics | Phase A 26th Current Magnitude Harmonics | Analog Input | %
283 | Phase B 26th Current Magnitude Harmonics | Phase B 26th Current Magnitude Harmonics | Analog Input | %
284 | Phase C 26th Current Magnitude Harmonics | Phase C 26th Current Magnitude Harmonics | Analog Input | %
285 | Phase N 26th Current Magnitude Harmonics | Phase N 26th Current Magnitude Harmonics | Analog Input | %
286 | Phase A 27th Voltage Magnitude Harmonics | Phase A 27th Voltage Magnitude Harmonics | Analog Input | %
287 | Phase B 27th Voltage Magnitude Harmonics | Phase B 27th Voltage Magnitude Harmonics | Analog Input | %
288 | Phase C 27th Voltage Magnitude Harmonics | Phase C 27th Voltage Magnitude Harmonics | Analog Input | %
289 | Phase A 27th Current Magnitude Harmonics | Phase A 27th Current Magnitude Harmonics | Analog Input | %
290 | Phase B 27th Current Magnitude Harmonics | Phase B 27th Current Magnitude Harmonics | Analog Input | %
291 | Phase C 27th Current Magnitude Harmonics | Phase C 27th Current Magnitude Harmonics | Analog Input | %
292 | Phase N 27th Current Magnitude Harmonics | Phase N 27th Current Magnitude Harmonics | Analog Input | %
293 | Phase A 28th Voltage Magnitude Harmonics | Phase A 28th Voltage Magnitude Harmonics | Analog Input | %
294 | Phase B 28th Voltage Magnitude Harmonics | Phase B 28th Voltage Magnitude Harmonics | Analog Input | %
295 | Phase C 28th Voltage Magnitude Harmonics | Phase C 28th Voltage Magnitude Harmonics | Analog Input | %
296 | Phase A 28th Current Magnitude Harmonics | Phase A 28th Current Magnitude Harmonics | Analog Input | %
297 | Phase B 28th Current Magnitude Harmonics | Phase B 28th Current Magnitude Harmonics | Analog Input | %
298 | Phase C 28th Current Magnitude Harmonics | Phase C 28th Current Magnitude Harmonics | Analog Input | %
299 | Phase N 28th Current Magnitude Harmonics | Phase N 28th Current Magnitude Harmonics | Analog Input | %
300 | Phase A 29th Voltage Magnitude Harmonics | Phase A 29th Voltage Magnitude Harmonics | Analog Input | %
301 | Phase B 29th Voltage Magnitude Harmonics | Phase B 29th Voltage Magnitude Harmonics | Analog Input | %
302 | Phase C 29th Voltage Magnitude Harmonics | Phase C 29th Voltage Magnitude Harmonics | Analog Input | %
303 | Phase A 29th Current Magnitude Harmonics | Phase A 29th Current Magnitude Harmonics | Analog Input | %
304 | Phase B 29th Current Magnitude Harmonics | Phase B 29th Current Magnitude Harmonics | Analog Input | %
305 | Phase C 29th Current Magnitude Harmonics | Phase C 29th Current Magnitude Harmonics | Analog Input | %
306 | Phase N 29th Current Magnitude Harmonics | Phase N 29th Current Magnitude Harmonics | Analog Input | %
307 | Phase A 30th Voltage Magnitude Harmonics | Phase A 30th Voltage Magnitude Harmonics | Analog Input | %
308 | Phase B 30th Voltage Magnitude Harmonics | Phase B 30th Voltage Magnitude Harmonics | Analog Input | %
309 | Phase C 30th Voltage Magnitude Harmonics | Phase C 30th Voltage Magnitude Harmonics | Analog Input | %
310 | Phase A 30th Current Magnitude Harmonics | Phase A 30th Current Magnitude Harmonics | Analog Input | %
311 | Phase B 30th Current Magnitude Harmonics | Phase B 30th Current Magnitude Harmonics | Analog Input | %
312 | Phase C 30th Current Magnitude Harmonics | Phase C 30th Current Magnitude Harmonics | Analog Input | %
313 | Phase N 30th Current Magnitude Harmonics | Phase N 30th Current Magnitude Harmonics | Analog Input | %
314 | Phase A 31st Voltage Magnitude Harmonics | Phase A 31st Voltage Magnitude Harmonics | Analog Input | %
315 | Phase B 31st Voltage Magnitude Harmonics | Phase B 31st Voltage Magnitude Harmonics | Analog Input | %
316 | Phase C 31st Voltage Magnitude Harmonics | Phase C 31st Voltage Magnitude Harmonics | Analog Input | %
317 | Phase A 31st Current Magnitude Harmonics | Phase A 31st Current Magnitude Harmonics | Analog Input | %
318 | Phase B 31st Current Magnitude Harmonics | Phase B 31st Current Magnitude Harmonics | Analog Input | %
319 | Phase C 31st Current Magnitude Harmonics | Phase C 31st Current Magnitude Harmonics | Analog Input | %
320 | Phase N 31st Current Magnitude Harmonics | Phase N 31st Current Magnitude Harmonics | Analog Input | %
321 | Phase A 32nd Voltage Magnitude Harmonics | Phase A 32nd Voltage Magnitude Harmonics | Analog Input | %
322 | Phase B 32nd Voltage Magnitude Harmonics | Phase B 32nd Voltage Magnitude Harmonics | Analog Input | %
323 | Phase C 32nd Voltage Magnitude Harmonics | Phase C 32nd Voltage Magnitude Harmonics | Analog Input | %
324 | Phase A 32nd Current Magnitude Harmonics | Phase A 32nd Current Magnitude Harmonics | Analog Input | %
325 | Phase B 32nd Current Magnitude Harmonics | Phase B 32nd Current Magnitude Harmonics | Analog Input | %
326 | Phase C 32nd Current Magnitude Harmonics | Phase C 32nd Current Magnitude Harmonics | Analog Input | %
327 | Phase N 32nd Current Magnitude Harmonics | Phase N 32nd Current Magnitude Harmonics | Analog Input | %
328 | Phase A 33rd Voltage Magnitude Harmonics | Phase A 33rd Voltage Magnitude Harmonics | Analog Input | %
329 | Phase B 33rd Voltage Magnitude Harmonics | Phase B 33rd Voltage Magnitude Harmonics | Analog Input | %
330 | Phase C 33rd Voltage Magnitude Harmonics | Phase C 33rd Voltage Magnitude Harmonics | Analog Input | %
331 | Phase A 33rd Current Magnitude Harmonics | Phase A 33rd Current Magnitude Harmonics | Analog Input | %
332 | Phase B 33rd Current Magnitude Harmonics | Phase B 33rd Current Magnitude Harmonics | Analog Input | %
333 | Phase C 33rd Current Magnitude Harmonics | Phase C 33rd Current Magnitude Harmonics | Analog Input | %
334 | Phase N 33rd Current Magnitude Harmonics | Phase N 33rd Current Magnitude Harmonics | Analog Input | %
335 | Phase A 34th Voltage Magnitude Harmonics | Phase A 34th Voltage Magnitude Harmonics | Analog Input | %
336 | Phase B 34th Voltage Magnitude Harmonics | Phase B 34th Voltage Magnitude Harmonics | Analog Input | %
337 | Phase C 34th Voltage Magnitude Harmonics | Phase C 34th Voltage Magnitude Harmonics | Analog Input | %
338 | Phase A 34th Current Magnitude Harmonics | Phase A 34th Current Magnitude Harmonics | Analog Input | %
339 | Phase B 34th Current Magnitude Harmonics | Phase B 34th Current Magnitude Harmonics | Analog Input | %
340 | Phase C 34th Current Magnitude Harmonics | Phase C 34th Current Magnitude Harmonics | Analog Input | %
341 | Phase N 34th Current Magnitude Harmonics | Phase N 34th Current Magnitude Harmonics | Analog Input | %
342 | Phase A 35th Voltage Magnitude Harmonics | Phase A 35th Voltage Magnitude Harmonics | Analog Input | %
343 | Phase B 35th Voltage Magnitude Harmonics | Phase B 35th Voltage Magnitude Harmonics | Analog Input | %
344 | Phase C 35th Voltage Magnitude Harmonics | Phase C 35th Voltage Magnitude Harmonics | Analog Input | %
345 | Phase A 35th Current Magnitude Harmonics | Phase A 35th Current Magnitude Harmonics | Analog Input | %
346 | Phase B 35th Current Magnitude Harmonics | Phase B 35th Current Magnitude Harmonics | Analog Input | %
347 | Phase C 35th Current Magnitude Harmonics | Phase C 35th Current Magnitude Harmonics | Analog Input | %
348 | Phase N 35th Current Magnitude Harmonics | Phase N 35th Current Magnitude Harmonics | Analog Input | %
349 | Phase A 36th Voltage Magnitude Harmonics | Phase A 36th Voltage Magnitude Harmonics | Analog Input | %
350 | Phase B 36th Voltage Magnitude Harmonics | Phase B 36th Voltage Magnitude Harmonics | Analog Input | %
351 | Phase C 36th Voltage Magnitude Harmonics | Phase C 36th Voltage Magnitude Harmonics | Analog Input | %
352 | Phase A 36th Current Magnitude Harmonics | Phase A 36th Current Magnitude Harmonics | Analog Input | %
353 | Phase B 36th Current Magnitude Harmonics | Phase B 36th Current Magnitude Harmonics | Analog Input | %
354 | Phase C 36th Current Magnitude Harmonics | Phase C 36th Current Magnitude Harmonics | Analog Input | %
355 | Phase N 36th Current Magnitude Harmonics | Phase N 36th Current Magnitude Harmonics | Analog Input | %
356 | Phase A 37th Voltage Magnitude Harmonics | Phase A 37th Voltage Magnitude Harmonics | Analog Input | %
357 | Phase B 37th Voltage Magnitude Harmonics | Phase B 37th Voltage Magnitude Harmonics | Analog Input | %
358 | Phase C 37th Voltage Magnitude Harmonics | Phase C 37th Voltage Magnitude Harmonics | Analog Input | %
359 | Phase A 37th Current Magnitude Harmonics | Phase A 37th Current Magnitude Harmonics | Analog Input | %
360 | Phase B 37th Current Magnitude Harmonics | Phase B 37th Current Magnitude Harmonics | Analog Input | %
361 | Phase C 37th Current Magnitude Harmonics | Phase C 37th Current Magnitude Harmonics | Analog Input | %
362 | Phase N 37th Current Magnitude Harmonics | Phase N 37th Current Magnitude Harmonics | Analog Input | %
363 | Phase A 38th Voltage Magnitude Harmonics | Phase A 38th Voltage Magnitude Harmonics | Analog Input | %
364 | Phase B 38th Voltage Magnitude Harmonics | Phase B 38th Voltage Magnitude Harmonics | Analog Input | %
365 | Phase C 38th Voltage Magnitude Harmonics | Phase C 38th Voltage Magnitude Harmonics | Analog Input | %
366 | Phase A 38th Current Magnitude Harmonics | Phase A 38th Current Magnitude Harmonics | Analog Input | %
367 | Phase B 38th Current Magnitude Harmonics | Phase B 38th Current Magnitude Harmonics | Analog Input | %
368 | Phase C 38th Current Magnitude Harmonics | Phase C 38th Current Magnitude Harmonics | Analog Input | %
369 | Phase N 38th Current Magnitude Harmonics | Phase N 38th Current Magnitude Harmonics | Analog Input | %
370 | Phase A 39th Voltage Magnitude Harmonics | Phase A 39th Voltage Magnitude Harmonics | Analog Input | %
371 | Phase B 39th Voltage Magnitude Harmonics | Phase B 39th Voltage Magnitude Harmonics | Analog Input | %
372 | Phase C 39th Voltage Magnitude Harmonics | Phase C 39th Voltage Magnitude Harmonics | Analog Input | %
373 | Phase A 39th Current Magnitude Harmonics | Phase A 39th Current Magnitude Harmonics | Analog Input | %
374 | Phase B 39th Current Magnitude Harmonics | Phase B 39th Current Magnitude Harmonics | Analog Input | %
375 | Phase C 39th Current Magnitude Harmonics | Phase C 39th Current Magnitude Harmonics | Analog Input | %
376 | Phase N 39th Current Magnitude Harmonics | Phase N 39th Current Magnitude Harmonics | Analog Input | %
377 | Phase A 40th Voltage Magnitude Harmonics | Phase A 40th Voltage Magnitude Harmonics | Analog Input | %
378 | Phase B 40th Voltage Magnitude Harmonics | Phase B 40th Voltage Magnitude Harmonics | Analog Input | %
379 | Phase C 40th Voltage Magnitude Harmonics | Phase C 40th Voltage Magnitude Harmonics | Analog Input | %
380 | Phase A 40th Current Magnitude Harmonics | Phase A 40th Current Magnitude Harmonics | Analog Input | %
381 | Phase B 40th Current Magnitude Harmonics | Phase B 40th Current Magnitude Harmonics | Analog Input | %
382 | Phase C 40th Current Magnitude Harmonics | Phase C 40th Current Magnitude Harmonics | Analog Input | %
383 | Phase N 40th Current Magnitude Harmonics | Phase N 40th Current Magnitude Harmonics | Analog Input | %
384 | Phase A 41st Voltage Magnitude Harmonics | Phase A 41st Voltage Magnitude Harmonics | Analog Input | %
385 | Phase B 41st Voltage Magnitude Harmonics | Phase B 41st Voltage Magnitude Harmonics | Analog Input | %
386 | Phase C 41st Voltage Magnitude Harmonics | Phase C 41st Voltage Magnitude Harmonics | Analog Input | %
387 | Phase A 41st Current Magnitude Harmonics | Phase A 41st Current Magnitude Harmonics | Analog Input | %
388 | Phase B 41st Current Magnitude Harmonics | Phase B 41st Current Magnitude Harmonics | Analog Input | %
389 | Phase C 41st Current Magnitude Harmonics | Phase C 41st Current Magnitude Harmonics | Analog Input | %
390 | Phase N 41st Current Magnitude Harmonics | Phase N 41st Current Magnitude Harmonics | Analog Input | %
391 | Phase A 42nd Voltage Magnitude Harmonics | Phase A 42nd Voltage Magnitude Harmonics | Analog Input | %
392 | Phase B 42nd Voltage Magnitude Harmonics | Phase B 42nd Voltage Magnitude Harmonics | Analog Input | %
393 | Phase C 42nd Voltage Magnitude Harmonics | Phase C 42nd Voltage Magnitude Harmonics | Analog Input | %
394 | Phase A 42nd Current Magnitude Harmonics | Phase A 42nd Current Magnitude Harmonics | Analog Input | %
395 | Phase B 42nd Current Magnitude Harmonics | Phase B 42nd Current Magnitude Harmonics | Analog Input | %
396 | Phase C 42nd Current Magnitude Harmonics | Phase C 42nd Current Magnitude Harmonics | Analog Input | %
397 | Phase N 42nd Current Magnitude Harmonics | Phase N 42nd Current Magnitude Harmonics | Analog Input | %
398 | Phase A 43rd Voltage Magnitude Harmonics | Phase A 43rd Voltage Magnitude Harmonics | Analog Input | %
399 | Phase B 43rd Voltage Magnitude Harmonics | Phase B 43rd Voltage Magnitude Harmonics | Analog Input | %
400 | Phase C 43rd Voltage Magnitude Harmonics | Phase C 43rd Voltage Magnitude Harmonics | Analog Input | %
401 | Phase A 43rd Current Magnitude Harmonics | Phase A 43rd Current Magnitude Harmonics | Analog Input | %
402 | Phase B 43rd Current Magnitude Harmonics | Phase B 43rd Current Magnitude Harmonics | Analog Input | %
403 | Phase C 43rd Current Magnitude Harmonics | Phase C 43rd Current Magnitude Harmonics | Analog Input | %
404 | Phase N 43rd Current Magnitude Harmonics | Phase N 43rd Current Magnitude Harmonics | Analog Input | %
405 | Phase A 44th Voltage Magnitude Harmonics | Phase A 44th Voltage Magnitude Harmonics | Analog Input | %
406 | Phase B 44th Voltage Magnitude Harmonics | Phase B 44th Voltage Magnitude Harmonics | Analog Input | %
407 | Phase C 44th Voltage Magnitude Harmonics | Phase C 44th Voltage Magnitude Harmonics | Analog Input | %
408 | Phase A 44th Current Magnitude Harmonics | Phase A 44th Current Magnitude Harmonics | Analog Input | %
409 | Phase B 44th Current Magnitude Harmonics | Phase B 44th Current Magnitude Harmonics | Analog Input | %
410 | Phase C 44th Current Magnitude Harmonics | Phase C 44th Current Magnitude Harmonics | Analog Input | %
411 | Phase N 44th Current Magnitude Harmonics | Phase N 44th Current Magnitude Harmonics | Analog Input | %
412 | Phase A 45th Voltage Magnitude Harmonics | Phase A 45th Voltage Magnitude Harmonics | Analog Input | %
413 | Phase B 45th Voltage Magnitude Harmonics | Phase B 45th Voltage Magnitude Harmonics | Analog Input | %
414 | Phase C 45th Voltage Magnitude Harmonics | Phase C 45th Voltage Magnitude Harmonics | Analog Input | %
415 | Phase A 45th Current Magnitude Harmonics | Phase A 45th Current Magnitude Harmonics | Analog Input | %
416 | Phase B 45th Current Magnitude Harmonics | Phase B 45th Current Magnitude Harmonics | Analog Input | %
417 | Phase C 45th Current Magnitude Harmonics | Phase C 45th Current Magnitude Harmonics | Analog Input | %
418 | Phase N 45th Current Magnitude Harmonics | Phase N 45th Current Magnitude Harmonics | Analog Input | %
419 | Phase A 46th Voltage Magnitude Harmonics | Phase A 46th Voltage Magnitude Harmonics | Analog Input | %
420 | Phase B 46th Voltage Magnitude Harmonics | Phase B 46th Voltage Magnitude Harmonics | Analog Input | %
421 | Phase C 46th Voltage Magnitude Harmonics | Phase C 46th Voltage Magnitude Harmonics | Analog Input | %
422 | Phase A 46th Current Magnitude Harmonics | Phase A 46th Current Magnitude Harmonics | Analog Input | %
423 | Phase B 46th Current Magnitude Harmonics | Phase B 46th Current Magnitude Harmonics | Analog Input | %
424 | Phase C 46th Current Magnitude Harmonics | Phase C 46th Current Magnitude Harmonics | Analog Input | %
425 | Phase N 46th Current Magnitude Harmonics | Phase N 46th Current Magnitude Harmonics | Analog Input | %
426 | Phase A 47th Voltage Magnitude Harmonics | Phase A 47th Voltage Magnitude Harmonics | Analog Input | %
427 | Phase B 47th Voltage Magnitude Harmonics | Phase B 47th Voltage Magnitude Harmonics | Analog Input | %
428 | Phase C 47th Voltage Magnitude Harmonics | Phase C 47th Voltage Magnitude Harmonics | Analog Input | %
429 | Phase A 47th Current Magnitude Harmonics | Phase A 47th Current Magnitude Harmonics | Analog Input | %
430 | Phase B 47th Current Magnitude Harmonics | Phase B 47th Current Magnitude Harmonics | Analog Input | %
431 | Phase C 47th Current Magnitude Harmonics | Phase C 47th Current Magnitude Harmonics | Analog Input | %
432 | Phase N 47th Current Magnitude Harmonics | Phase N 47th Current Magnitude Harmonics | Analog Input | %
433 | Phase A 48th Voltage Magnitude Harmonics | Phase A 48th Voltage Magnitude Harmonics | Analog Input | %
434 | Phase B 48th Voltage Magnitude Harmonics | Phase B 48th Voltage Magnitude Harmonics | Analog Input | %
435 | Phase C 48th Voltage Magnitude Harmonics | Phase C 48th Voltage Magnitude Harmonics | Analog Input | %
436 | Phase A 48th Current Magnitude Harmonics | Phase A 48th Current Magnitude Harmonics | Analog Input | %
437 | Phase B 48th Current Magnitude Harmonics | Phase B 48th Current Magnitude Harmonics | Analog Input | %
438 | Phase C 48th Current Magnitude Harmonics | Phase C 48th Current Magnitude Harmonics | Analog Input | %
439 | Phase N 48th Current Magnitude Harmonics | Phase N 48th Current Magnitude Harmonics | Analog Input | %
440 | Phase A 49th Voltage Magnitude Harmonics | Phase A 49th Voltage Magnitude Harmonics | Analog Input | %
441 | Phase B 49th Voltage Magnitude Harmonics | Phase B 49th Voltage Magnitude Harmonics | Analog Input | %
442 | Phase C 49th Voltage Magnitude Harmonics | Phase C 49th Voltage Magnitude Harmonics | Analog Input | %
443 | Phase A 49th Current Magnitude Harmonics | Phase A 49th Current Magnitude Harmonics | Analog Input | %
444 | Phase B 49th Current Magnitude Harmonics | Phase B 49th Current Magnitude Harmonics | Analog Input | %
445 | Phase C 49th Current Magnitude Harmonics | Phase C 49th Current Magnitude Harmonics | Analog Input | %
446 | Phase N 49th Current Magnitude Harmonics | Phase N 49th Current Magnitude Harmonics | Analog Input | %
447 | Phase A 50th Voltage Magnitude Harmonics | Phase A 50th Voltage Magnitude Harmonics | Analog Input | %
448 | Phase B 50th Voltage Magnitude Harmonics | Phase B 50th Voltage Magnitude Harmonics | Analog Input | %
449 | Phase C 50th Voltage Magnitude Harmonics | Phase C 50th Voltage Magnitude Harmonics | Analog Input | %
450 | Phase A 50th Current Magnitude Harmonics | Phase A 50th Current Magnitude Harmonics | Analog Input | %
451 | Phase B 50th Current Magnitude Harmonics | Phase B 50th Current Magnitude Harmonics | Analog Input | %
452 | Phase C 50th Current Magnitude Harmonics | Phase C 50th Current Magnitude Harmonics | Analog Input | %
453 | Phase N 50th Current Magnitude Harmonics | Phase N 50th Current Magnitude Harmonics | Analog Input | %
454 | Phase A 51st Voltage Magnitude Harmonics | Phase A 51st Voltage Magnitude Harmonics | Analog Input | %
455 | Phase B 51st Voltage Magnitude Harmonics | Phase B 51st Voltage Magnitude Harmonics | Analog Input | %
456 | Phase C 51st Voltage Magnitude Harmonics | Phase C 51st Voltage Magnitude Harmonics | Analog Input | %
457 | Phase A 51st Current Magnitude Harmonics | Phase A 51st Current Magnitude Harmonics | Analog Input | %
458 | Phase B 51st Current Magnitude Harmonics | Phase B 51st Current Magnitude Harmonics | Analog Input | %
459 | Phase C 51st Current Magnitude Harmonics | Phase C 51st Current Magnitude Harmonics | Analog Input | %
460 | Phase N 51st Current Magnitude Harmonics | Phase N 51st Current Magnitude Harmonics | Analog Input | %
461 | Phase A 52nd Voltage Magnitude Harmonics | Phase A 52nd Voltage Magnitude Harmonics | Analog Input | %
462 | Phase B 52nd Voltage Magnitude Harmonics | Phase B 52nd Voltage Magnitude Harmonics | Analog Input | %
463 | Phase C 52nd Voltage Magnitude Harmonics | Phase C 52nd Voltage Magnitude Harmonics | Analog Input | %
464 | Phase A 52nd Current Magnitude Harmonics | Phase A 52nd Current Magnitude Harmonics | Analog Input | %
465 | Phase B 52nd Current Magnitude Harmonics | Phase B 52nd Current Magnitude Harmonics | Analog Input | %
466 | Phase C 52nd Current Magnitude Harmonics | Phase C 52nd Current Magnitude Harmonics | Analog Input | %
467 | Phase N 52nd Current Magnitude Harmonics | Phase N 52nd Current Magnitude Harmonics | Analog Input | %
468 | Phase A 53rd Voltage Magnitude Harmonics | Phase A 53rd Voltage Magnitude Harmonics | Analog Input | %
469 | Phase B 53rd Voltage Magnitude Harmonics | Phase B 53rd Voltage Magnitude Harmonics | Analog Input | %
470 | Phase C 53rd Voltage Magnitude Harmonics | Phase C 53rd Voltage Magnitude Harmonics | Analog Input | %
471 | Phase A 53rd Current Magnitude Harmonics | Phase A 53rd Current Magnitude Harmonics | Analog Input | %
472 | Phase B 53rd Current Magnitude Harmonics | Phase B 53rd Current Magnitude Harmonics | Analog Input | %
473 | Phase C 53rd Current Magnitude Harmonics | Phase C 53rd Current Magnitude Harmonics | Analog Input | %
474 | Phase N 53rd Current Magnitude Harmonics | Phase N 53rd Current Magnitude Harmonics | Analog Input | %
475 | Phase A 54th Voltage Magnitude Harmonics | Phase A 54th Voltage Magnitude Harmonics | Analog Input | %
476 | Phase B 54th Voltage Magnitude Harmonics | Phase B 54th Voltage Magnitude Harmonics | Analog Input | %
477 | Phase C 54th Voltage Magnitude Harmonics | Phase C 54th Voltage Magnitude Harmonics | Analog Input | %
478 | Phase A 54th Current Magnitude Harmonics | Phase A 54th Current Magnitude Harmonics | Analog Input | %
479 | Phase B 54th Current Magnitude Harmonics | Phase B 54th Current Magnitude Harmonics | Analog Input | %
480 | Phase C 54th Current Magnitude Harmonics | Phase C 54th Current Magnitude Harmonics | Analog Input | %
481 | Phase N 54th Current Magnitude Harmonics | Phase N 54th Current Magnitude Harmonics | Analog Input | %
482 | Phase A 55th Voltage Magnitude Harmonics | Phase A 55th Voltage Magnitude Harmonics | Analog Input | %
483 | Phase B 55th Voltage Magnitude Harmonics | Phase B 55th Voltage Magnitude Harmonics | Analog Input | %
484 | Phase C 55th Voltage Magnitude Harmonics | Phase C 55th Voltage Magnitude Harmonics | Analog Input | %
485 | Phase A 55th Current Magnitude Harmonics | Phase A 55th Current Magnitude Harmonics | Analog Input | %
486 | Phase B 55th Current Magnitude Harmonics | Phase B 55th Current Magnitude Harmonics | Analog Input | %
487 | Phase C 55th Current Magnitude Harmonics | Phase C 55th Current Magnitude Harmonics | Analog Input | %
488 | Phase N 55th Current Magnitude Harmonics | Phase N 55th Current Magnitude Harmonics | Analog Input | %
489 | Phase A 56th Voltage Magnitude Harmonics | Phase A 56th Voltage Magnitude Harmonics | Analog Input | %
490 | Phase B 56th Voltage Magnitude Harmonics | Phase B 56th Voltage Magnitude Harmonics | Analog Input | %
491 | Phase C 56th Voltage Magnitude Harmonics | Phase C 56th Voltage Magnitude Harmonics | Analog Input | %
492 | Phase A 56th Current Magnitude Harmonics | Phase A 56th Current Magnitude Harmonics | Analog Input | %
493 | Phase B 56th Current Magnitude Harmonics | Phase B 56th Current Magnitude Harmonics | Analog Input | %
494 | Phase C 56th Current Magnitude Harmonics | Phase C 56th Current Magnitude Harmonics | Analog Input | %
495 | Phase N 56th Current Magnitude Harmonics | Phase N 56th Current Magnitude Harmonics | Analog Input | %
496 | Phase A 57th Voltage Magnitude Harmonics | Phase A 57th Voltage Magnitude Harmonics | Analog Input | %
497 | Phase B 57th Voltage Magnitude Harmonics | Phase B 57th Voltage Magnitude Harmonics | Analog Input | %
498 | Phase C 57th Voltage Magnitude Harmonics | Phase C 57th Voltage Magnitude Harmonics | Analog Input | %
499 | Phase A 57th Current Magnitude Harmonics | Phase A 57th Current Magnitude Harmonics | Analog Input | %
500 | Phase B 57th Current Magnitude Harmonics | Phase B 57th Current Magnitude Harmonics | Analog Input | %
501 | Phase C 57th Current Magnitude Harmonics | Phase C 57th Current Magnitude Harmonics | Analog Input | %
502 | Phase N 57th Current Magnitude Harmonics | Phase N 57th Current Magnitude Harmonics | Analog Input | %
503 | Phase A 58th Voltage Magnitude Harmonics | Phase A 58th Voltage Magnitude Harmonics | Analog Input | %
504 | Phase B 58th Voltage Magnitude Harmonics | Phase B 58th Voltage Magnitude Harmonics | Analog Input | %
505 | Phase C 58th Voltage Magnitude Harmonics | Phase C 58th Voltage Magnitude Harmonics | Analog Input | %
506 | Phase A 58th Current Magnitude Harmonics | Phase A 58th Current Magnitude Harmonics | Analog Input | %
507 | Phase B 58th Current Magnitude Harmonics | Phase B 58th Current Magnitude Harmonics | Analog Input | %
508 | Phase C 58th Current Magnitude Harmonics | Phase C 58th Current Magnitude Harmonics | Analog Input | %
509 | Phase N 58th Current Magnitude Harmonics | Phase N 58th Current Magnitude Harmonics | Analog Input | %
510 | Phase A 59th Voltage Magnitude Harmonics | Phase A 59th Voltage Magnitude Harmonics | Analog Input | %
511 | Phase B 59th Voltage Magnitude Harmonics | Phase B 59th Voltage Magnitude Harmonics | Analog Input | %
512 | Phase C 59th Voltage Magnitude Harmonics | Phase C 59th Voltage Magnitude Harmonics | Analog Input | %
513 | Phase A 59th Current Magnitude Harmonics | Phase A 59th Current Magnitude Harmonics | Analog Input | %
514 | Phase B 59th Current Magnitude Harmonics | Phase B 59th Current Magnitude Harmonics | Analog Input | %
515 | Phase C 59th Current Magnitude Harmonics | Phase C 59th Current Magnitude Harmonics | Analog Input | %
516 | Phase N 59th Current Magnitude Harmonics | Phase N 59th Current Magnitude Harmonics | Analog Input | %
517 | Phase A 60th Voltage Magnitude Harmonics | Phase A 60th Voltage Magnitude Harmonics | Analog Input | %
518 | Phase B 60th Voltage Magnitude Harmonics | Phase B 60th Voltage Magnitude Harmonics | Analog Input | %
519 | Phase C 60th Voltage Magnitude Harmonics | Phase C 60th Voltage Magnitude Harmonics | Analog Input | %
520 | Phase A 60th Current Magnitude Harmonics | Phase A 60th Current Magnitude Harmonics | Analog Input | %
521 | Phase B 60th Current Magnitude Harmonics | Phase B 60th Current Magnitude Harmonics | Analog Input | %
522 | Phase C 60th Current Magnitude Harmonics | Phase C 60th Current Magnitude Harmonics | Analog Input | %
523 | Phase N 60th Current Magnitude Harmonics | Phase N 60th Current Magnitude Harmonics | Analog Input | %
524 | Phase A 61st Voltage Magnitude Harmonics | Phase A 61st Voltage Magnitude Harmonics | Analog Input | %
525 | Phase B 61st Voltage Magnitude Harmonics | Phase B 61st Voltage Magnitude Harmonics | Analog Input | %
526 | Phase C 61st Voltage Magnitude Harmonics | Phase C 61st Voltage Magnitude Harmonics | Analog Input | %
527 | Phase A 61st Current Magnitude Harmonics | Phase A 61st Current Magnitude Harmonics | Analog Input | %
528 | Phase B 61st Current Magnitude Harmonics | Phase B 61st Current Magnitude Harmonics | Analog Input | %
529 | Phase C 61st Current Magnitude Harmonics | Phase C 61st Current Magnitude Harmonics | Analog Input | %
530 | Phase N 61st Current Magnitude Harmonics | Phase N 61st Current Magnitude Harmonics | Analog Input | %
531 | Phase A 62nd Voltage Magnitude Harmonics | Phase A 62nd Voltage Magnitude Harmonics | Analog Input | %
532 | Phase B 62nd Voltage Magnitude Harmonics | Phase B 62nd Voltage Magnitude Harmonics | Analog Input | %
533 | Phase C 62nd Voltage Magnitude Harmonics | Phase C 62nd Voltage Magnitude Harmonics | Analog Input | %
534 | Phase A 62nd Current Magnitude Harmonics | Phase A 62nd Current Magnitude Harmonics | Analog Input | %
535 | Phase B 62nd Current Magnitude Harmonics | Phase B 62nd Current Magnitude Harmonics | Analog Input | %
536 | Phase C 62nd Current Magnitude Harmonics | Phase C 62nd Current Magnitude Harmonics | Analog Input | %
537 | Phase N 62nd Current Magnitude Harmonics | Phase N 62nd Current Magnitude Harmonics | Analog Input | %
538 | Phase A 63rd Voltage Magnitude Harmonics | Phase A 63rd Voltage Magnitude Harmonics | Analog Input | %
539 | Phase B 63rd Voltage Magnitude Harmonics | Phase B 63rd Voltage Magnitude Harmonics | Analog Input | %
540 | Phase C 63rd Voltage Magnitude Harmonics | Phase C 63rd Voltage Magnitude Harmonics | Analog Input | %
541 | Phase A 63rd Current Magnitude Harmonics | Phase A 63rd Current Magnitude Harmonics | Analog Input | %
542 | Phase B 63rd Current Magnitude Harmonics | Phase B 63rd Current Magnitude Harmonics | Analog Input | %
543 | Phase C 63rd Current Magnitude Harmonics | Phase C 63rd Current Magnitude Harmonics | Analog Input | %
544 | Phase N 63rd Current Magnitude Harmonics | Phase N 63rd Current Magnitude Harmonics | Analog Input | %
545 | Phase A 64th Voltage Magnitude Harmonics | Phase A 64th Voltage Magnitude Harmonics | Analog Input | %
546 | Phase B 64th Voltage Magnitude Harmonics | Phase B 64th Voltage Magnitude Harmonics | Analog Input | %
547 | Phase C 64th Voltage Magnitude Harmonics | Phase C 64th Voltage Magnitude Harmonics | Analog Input | %
548 | Phase A 64th Current Magnitude Harmonics | Phase A 64th Current Magnitude Harmonics | Analog Input | %
549 | Phase B 64th Current Magnitude Harmonics | Phase B 64th Current Magnitude Harmonics | Analog Input | %
550 | Phase C 64th Current Magnitude Harmonics | Phase C 64th Current Magnitude Harmonics | Analog Input | %
551 | Phase N 64th Current Magnitude Harmonics | Phase N 64th Current Magnitude Harmonics | Analog Input | %
552 | Phase A 65th Voltage Magnitude Harmonics | Phase A 65th Voltage Magnitude Harmonics | Analog Input | %
553 | Phase B 65th Voltage Magnitude Harmonics | Phase B 65th Voltage Magnitude Harmonics | Analog Input | %
554 | Phase C 65th Voltage Magnitude Harmonics | Phase C 65th Voltage Magnitude Harmonics | Analog Input | %
555 | Phase A 65th Current Magnitude Harmonics | Phase A 65th Current Magnitude Harmonics | Analog Input | %
556 | Phase B 65th Current Magnitude Harmonics | Phase B 65th Current Magnitude Harmonics | Analog Input | %
557 | Phase C 65th Current Magnitude Harmonics | Phase C 65th Current Magnitude Harmonics | Analog Input | %
558 | Phase N 65th Current Magnitude Harmonics | Phase N 65th Current Magnitude Harmonics | Analog Input | %
559 | Phase A 66th Voltage Magnitude Harmonics | Phase A 66th Voltage Magnitude Harmonics | Analog Input | %
560 | Phase B 66th Voltage Magnitude Harmonics | Phase B 66th Voltage Magnitude Harmonics | Analog Input | %
561 | Phase C 66th Voltage Magnitude Harmonics | Phase C 66th Voltage Magnitude Harmonics | Analog Input | %
562 | Phase A 66th Current Magnitude Harmonics | Phase A 66th Current Magnitude Harmonics | Analog Input | %
563 | Phase B 66th Current Magnitude Harmonics | Phase B 66th Current Magnitude Harmonics | Analog Input | %
564 | Phase C 66th Current Magnitude Harmonics | Phase C 66th Current Magnitude Harmonics | Analog Input | %
565 | Phase N 66th Current Magnitude Harmonics | Phase N 66th Current Magnitude Harmonics | Analog Input | %
566 | Phase A 67th Voltage Magnitude Harmonics | Phase A 67th Voltage Magnitude Harmonics | Analog Input | %
567 | Phase B 67th Voltage Magnitude Harmonics | Phase B 67th Voltage Magnitude Harmonics | Analog Input | %
568 | Phase C 67th Voltage Magnitude Harmonics | Phase C 67th Voltage Magnitude Harmonics | Analog Input | %
569 | Phase A 67th Current Magnitude Harmonics | Phase A 67th Current Magnitude Harmonics | Analog Input | %
570 | Phase B 67th Current Magnitude Harmonics | Phase B 67th Current Magnitude Harmonics | Analog Input | %
571 | Phase C 67th Current Magnitude Harmonics | Phase C 67th Current Magnitude Harmonics | Analog Input | %
572 | Phase N 67th Current Magnitude Harmonics | Phase N 67th Current Magnitude Harmonics | Analog Input | %
573 | Phase A 68th Voltage Magnitude Harmonics | Phase A 68th Voltage Magnitude Harmonics | Analog Input | %
574 | Phase B 68th Voltage Magnitude Harmonics | Phase B 68th Voltage Magnitude Harmonics | Analog Input | %
575 | Phase C 68th Voltage Magnitude Harmonics | Phase C 68th Voltage Magnitude Harmonics | Analog Input | %
576 | Phase A 68th Current Magnitude Harmonics | Phase A 68th Current Magnitude Harmonics | Analog Input | %
577 | Phase B 68th Current Magnitude Harmonics | Phase B 68th Current Magnitude Harmonics | Analog Input | %
578 | Phase C 68th Current Magnitude Harmonics | Phase C 68th Current Magnitude Harmonics | Analog Input | %
579 | Phase N 68th Current Magnitude Harmonics | Phase N 68th Current Magnitude Harmonics | Analog Input | %
580 | Phase A 69th Voltage Magnitude Harmonics | Phase A 69th Voltage Magnitude Harmonics | Analog Input | %
581 | Phase B 69th Voltage Magnitude Harmonics | Phase B 69th Voltage Magnitude Harmonics | Analog Input | %
582 | Phase C 69th Voltage Magnitude Harmonics | Phase C 69th Voltage Magnitude Harmonics | Analog Input | %
583 | Phase A 69th Current Magnitude Harmonics | Phase A 69th Current Magnitude Harmonics | Analog Input | %
584 | Phase B 69th Current Magnitude Harmonics | Phase B 69th Current Magnitude Harmonics | Analog Input | %
585 | Phase C 69th Current Magnitude Harmonics | Phase C 69th Current Magnitude Harmonics | Analog Input | %
586 | Phase N 69th Current Magnitude Harmonics | Phase N 69th Current Magnitude Harmonics | Analog Input | %
587 | Phase A 70th Voltage Magnitude Harmonics | Phase A 70th Voltage Magnitude Harmonics | Analog Input | %
588 | Phase B 70th Voltage Magnitude Harmonics | Phase B 70th Voltage Magnitude Harmonics | Analog Input | %
589 | Phase C 70th Voltage Magnitude Harmonics | Phase C 70th Voltage Magnitude Harmonics | Analog Input | %
590 | Phase A 70th Current Magnitude Harmonics | Phase A 70th Current Magnitude Harmonics | Analog Input | %
591 | Phase B 70th Current Magnitude Harmonics | Phase B 70th Current Magnitude Harmonics | Analog Input | %
592 | Phase C 70th Current Magnitude Harmonics | Phase C 70th Current Magnitude Harmonics | Analog Input | %
593 | Phase N 70th Current Magnitude Harmonics | Phase N 70th Current Magnitude Harmonics | Analog Input | %
594 | Phase A 71st Voltage Magnitude Harmonics | Phase A 71st Voltage Magnitude Harmonics | Analog Input | %
595 | Phase B 71st Voltage Magnitude Harmonics | Phase B 71st Voltage Magnitude Harmonics | Analog Input | %
596 | Phase C 71st Voltage Magnitude Harmonics | Phase C 71st Voltage Magnitude Harmonics | Analog Input | %
597 | Phase A 71st Current Magnitude Harmonics | Phase A 71st Current Magnitude Harmonics | Analog Input | %
598 | Phase B 71st Current Magnitude Harmonics | Phase B 71st Current Magnitude Harmonics | Analog Input | %
599 | Phase C 71st Current Magnitude Harmonics | Phase C 71st Current Magnitude Harmonics | Analog Input | %
600 | Phase N 71st Current Magnitude Harmonics | Phase N 71st Current Magnitude Harmonics | Analog Input | %
601 | Phase A 72nd Voltage Magnitude Harmonics | Phase A 72nd Voltage Magnitude Harmonics | Analog Input | %
602 | Phase B 72nd Voltage Magnitude Harmonics | Phase B 72nd Voltage Magnitude Harmonics | Analog Input | %
603 | Phase C 72nd Voltage Magnitude Harmonics | Phase C 72nd Voltage Magnitude Harmonics | Analog Input | %
604 | Phase A 72nd Current Magnitude Harmonics | Phase A 72nd Current Magnitude Harmonics | Analog Input | %
605 | Phase B 72nd Current Magnitude Harmonics | Phase B 72nd Current Magnitude Harmonics | Analog Input | %
606 | Phase C 72nd Current Magnitude Harmonics | Phase C 72nd Current Magnitude Harmonics | Analog Input | %
607 | Phase N 72nd Current Magnitude Harmonics | Phase N 72nd Current Magnitude Harmonics | Analog Input | %
608 | Phase A 73rd Voltage Magnitude Harmonics | Phase A 73rd Voltage Magnitude Harmonics | Analog Input | %
609 | Phase B 73rd Voltage Magnitude Harmonics | Phase B 73rd Voltage Magnitude Harmonics | Analog Input | %
610 | Phase C 73rd Voltage Magnitude Harmonics | Phase C 73rd Voltage Magnitude Harmonics | Analog Input | %
611 | Phase A 73rd Current Magnitude Harmonics | Phase A 73rd Current Magnitude Harmonics | Analog Input | %
612 | Phase B 73rd Current Magnitude Harmonics | Phase B 73rd Current Magnitude Harmonics | Analog Input | %
613 | Phase C 73rd Current Magnitude Harmonics | Phase C 73rd Current Magnitude Harmonics | Analog Input | %
614 | Phase N 73rd Current Magnitude Harmonics | Phase N 73rd Current Magnitude Harmonics | Analog Input | %
615 | Phase A 74th Voltage Magnitude Harmonics | Phase A 74th Voltage Magnitude Harmonics | Analog Input | %
616 | Phase B 74th Voltage Magnitude Harmonics | Phase B 74th Voltage Magnitude Harmonics | Analog Input | %
617 | Phase C 74th Voltage Magnitude Harmonics | Phase C 74th Voltage Magnitude Harmonics | Analog Input | %
618 | Phase A 74th Current Magnitude Harmonics | Phase A 74th Current Magnitude Harmonics | Analog Input | %
619 | Phase B 74th Current Magnitude Harmonics | Phase B 74th Current Magnitude Harmonics | Analog Input | %
620 | Phase C 74th Current Magnitude Harmonics | Phase C 74th Current Magnitude Harmonics | Analog Input | %
621 | Phase N 74th Current Magnitude Harmonics | Phase N 74th Current Magnitude Harmonics | Analog Input | %
622 | Phase A 75th Voltage Magnitude Harmonics | Phase A 75th Voltage Magnitude Harmonics | Analog Input | %
623 | Phase B 75th Voltage Magnitude Harmonics | Phase B 75th Voltage Magnitude Harmonics | Analog Input | %
624 | Phase C 75th Voltage Magnitude Harmonics | Phase C 75th Voltage Magnitude Harmonics | Analog Input | %
625 | Phase A 75th Current Magnitude Harmonics | Phase A 75th Current Magnitude Harmonics | Analog Input | %
626 | Phase B 75th Current Magnitude Harmonics | Phase B 75th Current Magnitude Harmonics | Analog Input | %
627 | Phase C 75th Current Magnitude Harmonics | Phase C 75th Current Magnitude Harmonics | Analog Input | %
628 | Phase N 75th Current Magnitude Harmonics | Phase N 75th Current Magnitude Harmonics | Analog Input | %
629 | Phase A 76th Voltage Magnitude Harmonics | Phase A 76th Voltage Magnitude Harmonics | Analog Input | %
630 | Phase B 76th Voltage Magnitude Harmonics | Phase B 76th Voltage Magnitude Harmonics | Analog Input | %
631 | Phase C 76th Voltage Magnitude Harmonics | Phase C 76th Voltage Magnitude Harmonics | Analog Input | %
632 | Phase A 76th Current Magnitude Harmonics | Phase A 76th Current Magnitude Harmonics | Analog Input | %
633 | Phase B 76th Current Magnitude Harmonics | Phase B 76th Current Magnitude Harmonics | Analog Input | %
634 | Phase C 76th Current Magnitude Harmonics | Phase C 76th Current Magnitude Harmonics | Analog Input | %
635 | Phase N 76th Current Magnitude Harmonics | Phase N 76th Current Magnitude Harmonics | Analog Input | %
636 | Phase A 77th Voltage Magnitude Harmonics | Phase A 77th Voltage Magnitude Harmonics | Analog Input | %
637 | Phase B 77th Voltage Magnitude Harmonics | Phase B 77th Voltage Magnitude Harmonics | Analog Input | %
638 | Phase C 77th Voltage Magnitude Harmonics | Phase C 77th Voltage Magnitude Harmonics | Analog Input | %
639 | Phase A 77th Current Magnitude Harmonics | Phase A 77th Current Magnitude Harmonics | Analog Input | %
640 | Phase B 77th Current Magnitude Harmonics | Phase B 77th Current Magnitude Harmonics | Analog Input | %
641 | Phase C 77th Current Magnitude Harmonics | Phase C 77th Current Magnitude Harmonics | Analog Input | %
642 | Phase N 77th Current Magnitude Harmonics | Phase N 77th Current Magnitude Harmonics | Analog Input | %
643 | Phase A 78th Voltage Magnitude Harmonics | Phase A 78th Voltage Magnitude Harmonics | Analog Input | %
644 | Phase B 78th Voltage Magnitude Harmonics | Phase B 78th Voltage Magnitude Harmonics | Analog Input | %
645 | Phase C 78th Voltage Magnitude Harmonics | Phase C 78th Voltage Magnitude Harmonics | Analog Input | %
646 | Phase A 78th Current Magnitude Harmonics | Phase A 78th Current Magnitude Harmonics | Analog Input | %
647 | Phase B 78th Current Magnitude Harmonics | Phase B 78th Current Magnitude Harmonics | Analog Input | %
648 | Phase C 78th Current Magnitude Harmonics | Phase C 78th Current Magnitude Harmonics | Analog Input | %
649 | Phase N 78th Current Magnitude Harmonics | Phase N 78th Current Magnitude Harmonics | Analog Input | %
650 | Phase A 79th Voltage Magnitude Harmonics | Phase A 79th Voltage Magnitude Harmonics | Analog Input | %
651 | Phase B 79th Voltage Magnitude Harmonics | Phase B 79th Voltage Magnitude Harmonics | Analog Input | %
652 | Phase C 79th Voltage Magnitude Harmonics | Phase C 79th Voltage Magnitude Harmonics | Analog Input | %
653 | Phase A 79th Current Magnitude Harmonics | Phase A 79th Current Magnitude Harmonics | Analog Input | %
654 | Phase B 79th Current Magnitude Harmonics | Phase B 79th Current Magnitude Harmonics | Analog Input | %
655 | Phase C 79th Current Magnitude Harmonics | Phase C 79th Current Magnitude Harmonics | Analog Input | %
656 | Phase N 79th Current Magnitude Harmonics | Phase N 79th Current Magnitude Harmonics | Analog Input | %
657 | Phase A 80th Voltage Magnitude Harmonics | Phase A 80th Voltage Magnitude Harmonics | Analog Input | %
658 | Phase B 80th Voltage Magnitude Harmonics | Phase B 80th Voltage Magnitude Harmonics | Analog Input | %
659 | Phase C 80th Voltage Magnitude Harmonics | Phase C 80th Voltage Magnitude Harmonics | Analog Input | %
660 | Phase A 80th Current Magnitude Harmonics | Phase A 80th Current Magnitude Harmonics | Analog Input | %
661 | Phase B 80th Current Magnitude Harmonics | Phase B 80th Current Magnitude Harmonics | Analog Input | %
662 | Phase C 80th Current Magnitude Harmonics | Phase C 80th Current Magnitude Harmonics | Analog Input | %
663 | Phase N 80th Current Magnitude Harmonics | Phase N 80th Current Magnitude Harmonics | Analog Input | %
664 | Phase A 81st Voltage Magnitude Harmonics | Phase A 81st Voltage Magnitude Harmonics | Analog Input | %
665 | Phase B 81st Voltage Magnitude Harmonics | Phase B 81st Voltage Magnitude Harmonics | Analog Input | %
666 | Phase C 81st Voltage Magnitude Harmonics | Phase C 81st Voltage Magnitude Harmonics | Analog Input | %
667 | Phase A 81st Current Magnitude Harmonics | Phase A 81st Current Magnitude Harmonics | Analog Input | %
668 | Phase B 81st Current Magnitude Harmonics | Phase B 81st Current Magnitude Harmonics | Analog Input | %
669 | Phase C 81st Current Magnitude Harmonics | Phase C 81st Current Magnitude Harmonics | Analog Input | %
670 | Phase N 81st Current Magnitude Harmonics | Phase N 81st Current Magnitude Harmonics | Analog Input | %
671 | Phase A 82nd Voltage Magnitude Harmonics | Phase A 82nd Voltage Magnitude Harmonics | Analog Input | %
672 | Phase B 82nd Voltage Magnitude Harmonics | Phase B 82nd Voltage Magnitude Harmonics | Analog Input | %
673 | Phase C 82nd Voltage Magnitude Harmonics | Phase C 82nd Voltage Magnitude Harmonics | Analog Input | %
674 | Phase A 82nd Current Magnitude Harmonics | Phase A 82nd Current Magnitude Harmonics | Analog Input | %
675 | Phase B 82nd Current Magnitude Harmonics | Phase B 82nd Current Magnitude Harmonics | Analog Input | %
676 | Phase C 82nd Current Magnitude Harmonics | Phase C 82nd Current Magnitude Harmonics | Analog Input | %
677 | Phase N 82nd Current Magnitude Harmonics | Phase N 82nd Current Magnitude Harmonics | Analog Input | %
678 | Phase A 83rd Voltage Magnitude Harmonics | Phase A 83rd Voltage Magnitude Harmonics | Analog Input | %
679 | Phase B 83rd Voltage Magnitude Harmonics | Phase B 83rd Voltage Magnitude Harmonics | Analog Input | %
680 | Phase C 83rd Voltage Magnitude Harmonics | Phase C 83rd Voltage Magnitude Harmonics | Analog Input | %
681 | Phase A 83rd Current Magnitude Harmonics | Phase A 83rd Current Magnitude Harmonics | Analog Input | %
682 | Phase B 83rd Current Magnitude Harmonics | Phase B 83rd Current Magnitude Harmonics | Analog Input | %
683 | Phase C 83rd Current Magnitude Harmonics | Phase C 83rd Current Magnitude Harmonics | Analog Input | %
684 | Phase N 83rd Current Magnitude Harmonics | Phase N 83rd Current Magnitude Harmonics | Analog Input | %
685 | Phase A 84th Voltage Magnitude Harmonics | Phase A 84th Voltage Magnitude Harmonics | Analog Input | %
686 | Phase B 84th Voltage Magnitude Harmonics | Phase B 84th Voltage Magnitude Harmonics | Analog Input | %
687 | Phase C 84th Voltage Magnitude Harmonics | Phase C 84th Voltage Magnitude Harmonics | Analog Input | %
688 | Phase A 84th Current Magnitude Harmonics | Phase A 84th Current Magnitude Harmonics | Analog Input | %
689 | Phase B 84th Current Magnitude Harmonics | Phase B 84th Current Magnitude Harmonics | Analog Input | %
690 | Phase C 84th Current Magnitude Harmonics | Phase C 84th Current Magnitude Harmonics | Analog Input | %
691 | Phase N 84th Current Magnitude Harmonics | Phase N 84th Current Magnitude Harmonics | Analog Input | %
692 | Phase A 85th Voltage Magnitude Harmonics | Phase A 85th Voltage Magnitude Harmonics | Analog Input | %
693 | Phase B 85th Voltage Magnitude Harmonics | Phase B 85th Voltage Magnitude Harmonics | Analog Input | %
694 | Phase C 85th Voltage Magnitude Harmonics | Phase C 85th Voltage Magnitude Harmonics | Analog Input | %
695 | Phase A 85th Current Magnitude Harmonics | Phase A 85th Current Magnitude Harmonics | Analog Input | %
696 | Phase B 85th Current Magnitude Harmonics | Phase B 85th Current Magnitude Harmonics | Analog Input | %
697 | Phase C 85th Current Magnitude Harmonics | Phase C 85th Current Magnitude Harmonics | Analog Input | %
698 | Phase N 85th Current Magnitude Harmonics | Phase N 85th Current Magnitude Harmonics | Analog Input | %
699 | Phase A 86th Voltage Magnitude Harmonics | Phase A 86th Voltage Magnitude Harmonics | Analog Input | %
700 | Phase B 86th Voltage Magnitude Harmonics | Phase B 86th Voltage Magnitude Harmonics | Analog Input | %
701 | Phase C 86th Voltage Magnitude Harmonics | Phase C 86th Voltage Magnitude Harmonics | Analog Input | %
702 | Phase A 86th Current Magnitude Harmonics | Phase A 86th Current Magnitude Harmonics | Analog Input | %
703 | Phase B 86th Current Magnitude Harmonics | Phase B 86th Current Magnitude Harmonics | Analog Input | %
704 | Phase C 86th Current Magnitude Harmonics | Phase C 86th Current Magnitude Harmonics | Analog Input | %
705 | Phase N 86th Current Magnitude Harmonics | Phase N 86th Current Magnitude Harmonics | Analog Input | %
706 | Phase A 87th Voltage Magnitude Harmonics | Phase A 87th Voltage Magnitude Harmonics | Analog Input | %
707 | Phase B 87th Voltage Magnitude Harmonics | Phase B 87th Voltage Magnitude Harmonics | Analog Input | %
708 | Phase C 87th Voltage Magnitude Harmonics | Phase C 87th Voltage Magnitude Harmonics | Analog Input | %
709 | Phase A 87th Current Magnitude Harmonics | Phase A 87th Current Magnitude Harmonics | Analog Input | %
710 | Phase B 87th Current Magnitude Harmonics | Phase B 87th Current Magnitude Harmonics | Analog Input | %
711 | Phase C 87th Current Magnitude Harmonics | Phase C 87th Current Magnitude Harmonics | Analog Input | %
712 | Phase N 87th Current Magnitude Harmonics | Phase N 87th Current Magnitude Harmonics | Analog Input | %
713 | Phase A 88th Voltage Magnitude Harmonics | Phase A 88th Voltage Magnitude Harmonics | Analog Input | %
714 | Phase B 88th Voltage Magnitude Harmonics | Phase B 88th Voltage Magnitude Harmonics | Analog Input | %
715 | Phase C 88th Voltage Magnitude Harmonics | Phase C 88th Voltage Magnitude Harmonics | Analog Input | %
716 | Phase A 88th Current Magnitude Harmonics | Phase A 88th Current Magnitude Harmonics | Analog Input | %
717 | Phase B 88th Current Magnitude Harmonics | Phase B 88th Current Magnitude Harmonics | Analog Input | %
718 | Phase C 88th Current Magnitude Harmonics | Phase C 88th Current Magnitude Harmonics | Analog Input | %
719 | Phase N 88th Current Magnitude Harmonics | Phase N 88th Current Magnitude Harmonics | Analog Input | %
720 | Phase A 89th Voltage Magnitude Harmonics | Phase A 89th Voltage Magnitude Harmonics | Analog Input | %
721 | Phase B 89th Voltage Magnitude Harmonics | Phase B 89th Voltage Magnitude Harmonics | Analog Input | %
722 | Phase C 89th Voltage Magnitude Harmonics | Phase C 89th Voltage Magnitude Harmonics | Analog Input | %
723 | Phase A 89th Current Magnitude Harmonics | Phase A 89th Current Magnitude Harmonics | Analog Input | %
724 | Phase B 89th Current Magnitude Harmonics | Phase B 89th Current Magnitude Harmonics | Analog Input | %
725 | Phase C 89th Current Magnitude Harmonics | Phase C 89th Current Magnitude Harmonics | Analog Input | %
726 | Phase N 89th Current Magnitude Harmonics | Phase N 89th Current Magnitude Harmonics | Analog Input | %
727 | Phase A 90th Voltage Magnitude Harmonics | Phase A 90th Voltage Magnitude Harmonics | Analog Input | %
728 | Phase B 90th Voltage Magnitude Harmonics | Phase B 90th Voltage Magnitude Harmonics | Analog Input | %
729 | Phase C 90th Voltage Magnitude Harmonics | Phase C 90th Voltage Magnitude Harmonics | Analog Input | %
730 | Phase A 90th Current Magnitude Harmonics | Phase A 90th Current Magnitude Harmonics | Analog Input | %
731 | Phase B 90th Current Magnitude Harmonics | Phase B 90th Current Magnitude Harmonics | Analog Input | %
732 | Phase C 90th Current Magnitude Harmonics | Phase C 90th Current Magnitude Harmonics | Analog Input | %
733 | Phase N 90th Current Magnitude Harmonics | Phase N 90th Current Magnitude Harmonics | Analog Input | %
734 | Phase A 91st Voltage Magnitude Harmonics | Phase A 91st Voltage Magnitude Harmonics | Analog Input | %
735 | Phase B 91st Voltage Magnitude Harmonics | Phase B 91st Voltage Magnitude Harmonics | Analog Input | %
736 | Phase C 91st Voltage Magnitude Harmonics | Phase C 91st Voltage Magnitude Harmonics | Analog Input | %
737 | Phase A 91st Current Magnitude Harmonics | Phase A 91st Current Magnitude Harmonics | Analog Input | %
738 | Phase B 91st Current Magnitude Harmonics | Phase B 91st Current Magnitude Harmonics | Analog Input | %
739 | Phase C 91st Current Magnitude Harmonics | Phase C 91st Current Magnitude Harmonics | Analog Input | %
740 | Phase N 91st Current Magnitude Harmonics | Phase N 91st Current Magnitude Harmonics | Analog Input | %
741 | Phase A 92nd Voltage Magnitude Harmonics | Phase A 92nd Voltage Magnitude Harmonics | Analog Input | %
742 | Phase B 92nd Voltage Magnitude Harmonics | Phase B 92nd Voltage Magnitude Harmonics | Analog Input | %
743 | Phase C 92nd Voltage Magnitude Harmonics | Phase C 92nd Voltage Magnitude Harmonics | Analog Input | %
744 | Phase A 92nd Current Magnitude Harmonics | Phase A 92nd Current Magnitude Harmonics | Analog Input | %
745 | Phase B 92nd Current Magnitude Harmonics | Phase B 92nd Current Magnitude Harmonics | Analog Input | %
746 | Phase C 92nd Current Magnitude Harmonics | Phase C 92nd Current Magnitude Harmonics | Analog Input | %
747 | Phase N 92nd Current Magnitude Harmonics | Phase N 92nd Current Magnitude Harmonics | Analog Input | %
748 | Phase A 93rd Voltage Magnitude Harmonics | Phase A 93rd Voltage Magnitude Harmonics | Analog Input | %
749 | Phase B 93rd Voltage Magnitude Harmonics | Phase B 93rd Voltage Magnitude Harmonics | Analog Input | %
750 | Phase C 93rd Voltage Magnitude Harmonics | Phase C 93rd Voltage Magnitude Harmonics | Analog Input | %
751 | Phase A 93rd Current Magnitude Harmonics | Phase A 93rd Current Magnitude Harmonics | Analog Input | %
752 | Phase B 93rd Current Magnitude Harmonics | Phase B 93rd Current Magnitude Harmonics | Analog Input | %
753 | Phase C 93rd Current Magnitude Harmonics | Phase C 93rd Current Magnitude Harmonics | Analog Input | %
754 | Phase N 93rd Current Magnitude Harmonics | Phase N 93rd Current Magnitude Harmonics | Analog Input | %
755 | Phase A 94th Voltage Magnitude Harmonics | Phase A 94th Voltage Magnitude Harmonics | Analog Input | %
756 | Phase B 94th Voltage Magnitude Harmonics | Phase B 94th Voltage Magnitude Harmonics | Analog Input | %
757 | Phase C 94th Voltage Magnitude Harmonics | Phase C 94th Voltage Magnitude Harmonics | Analog Input | %
758 | Phase A 94th Current Magnitude Harmonics | Phase A 94th Current Magnitude Harmonics | Analog Input | %
759 | Phase B 94th Current Magnitude Harmonics | Phase B 94th Current Magnitude Harmonics | Analog Input | %
760 | Phase C 94th Current Magnitude Harmonics | Phase C 94th Current Magnitude Harmonics | Analog Input | %
761 | Phase N 94th Current Magnitude Harmonics | Phase N 94th Current Magnitude Harmonics | Analog Input | %
762 | Phase A 95th Voltage Magnitude Harmonics | Phase A 95th Voltage Magnitude Harmonics | Analog Input | %
763 | Phase B 95th Voltage Magnitude Harmonics | Phase B 95th Voltage Magnitude Harmonics | Analog Input | %
764 | Phase C 95th Voltage Magnitude Harmonics | Phase C 95th Voltage Magnitude Harmonics | Analog Input | %
765 | Phase A 95th Current Magnitude Harmonics | Phase A 95th Current Magnitude Harmonics | Analog Input | %
766 | Phase B 95th Current Magnitude Harmonics | Phase B 95th Current Magnitude Harmonics | Analog Input | %
767 | Phase C 95th Current Magnitude Harmonics | Phase C 95th Current Magnitude Harmonics | Analog Input | %
768 | Phase N 95th Current Magnitude Harmonics | Phase N 95th Current Magnitude Harmonics | Analog Input | %
769 | Phase A 96th Voltage Magnitude Harmonics | Phase A 96th Voltage Magnitude Harmonics | Analog Input | %
770 | Phase B 96th Voltage Magnitude Harmonics | Phase B 96th Voltage Magnitude Harmonics | Analog Input | %
771 | Phase C 96th Voltage Magnitude Harmonics | Phase C 96th Voltage Magnitude Harmonics | Analog Input | %
772 | Phase A 96th Current Magnitude Harmonics | Phase A 96th Current Magnitude Harmonics | Analog Input | %
773 | Phase B 96th Current Magnitude Harmonics | Phase B 96th Current Magnitude Harmonics | Analog Input | %
774 | Phase C 96th Current Magnitude Harmonics | Phase C 96th Current Magnitude Harmonics | Analog Input | %
775 | Phase N 96th Current Magnitude Harmonics | Phase N 96th Current Magnitude Harmonics | Analog Input | %
776 | Phase A 97th Voltage Magnitude Harmonics | Phase A 97th Voltage Magnitude Harmonics | Analog Input | %
777 | Phase B 97th Voltage Magnitude Harmonics | Phase B 97th Voltage Magnitude Harmonics | Analog Input | %
778 | Phase C 97th Voltage Magnitude Harmonics | Phase C 97th Voltage Magnitude Harmonics | Analog Input | %
779 | Phase A 97th Current Magnitude Harmonics | Phase A 97th Current Magnitude Harmonics | Analog Input | %
780 | Phase B 97th Current Magnitude Harmonics | Phase B 97th Current Magnitude Harmonics | Analog Input | %
781 | Phase C 97th Current Magnitude Harmonics | Phase C 97th Current Magnitude Harmonics | Analog Input | %
782 | Phase N 97th Current Magnitude Harmonics | Phase N 97th Current Magnitude Harmonics | Analog Input | %
783 | Phase A 98th Voltage Magnitude Harmonics | Phase A 98th Voltage Magnitude Harmonics | Analog Input | %
784 | Phase B 98th Voltage Magnitude Harmonics | Phase B 98th Voltage Magnitude Harmonics | Analog Input | %
785 | Phase C 98th Voltage Magnitude Harmonics | Phase C 98th Voltage Magnitude Harmonics | Analog Input | %
786 | Phase A 98th Current Magnitude Harmonics | Phase A 98th Current Magnitude Harmonics | Analog Input | %
787 | Phase B 98th Current Magnitude Harmonics | Phase B 98th Current Magnitude Harmonics | Analog Input | %
788 | Phase C 98th Current Magnitude Harmonics | Phase C 98th Current Magnitude Harmonics | Analog Input | %
789 | Phase N 98th Current Magnitude Harmonics | Phase N 98th Current Magnitude Harmonics | Analog Input | %
790 | Phase A 99th Voltage Magnitude Harmonics | Phase A 99th Voltage Magnitude Harmonics | Analog Input | %
791 | Phase B 99th Voltage Magnitude Harmonics | Phase B 99th Voltage Magnitude Harmonics | Analog Input | %
792 | Phase C 99th Voltage Magnitude Harmonics | Phase C 99th Voltage Magnitude Harmonics | Analog Input | %
793 | Phase A 99th Current Magnitude Harmonics | Phase A 99th Current Magnitude Harmonics | Analog Input | %
794 | Phase B 99th Current Magnitude Harmonics | Phase B 99th Current Magnitude Harmonics | Analog Input | %
795 | Phase C 99th Current Magnitude Harmonics | Phase C 99th Current Magnitude Harmonics | Analog Input | %
796 | Phase N 99th Current Magnitude Harmonics | Phase N 99th Current Magnitude Harmonics | Analog Input | %
797 | Phase A 100th Voltage Magnitude Harmonics | Phase A 100th Voltage Magnitude Harmonics | Analog Input | %
798 | Phase B 100th Voltage Magnitude Harmonics | Phase B 100th Voltage Magnitude Harmonics | Analog Input | %
799 | Phase C 100th Voltage Magnitude Harmonics | Phase C 100th Voltage Magnitude Harmonics | Analog Input | %
800 | Phase A 100th Current Magnitude Harmonics | Phase A 100th Current Magnitude Harmonics | Analog Input | %
801 | Phase B 100th Current Magnitude Harmonics | Phase B 100th Current Magnitude Harmonics | Analog Input | %
802 | Phase C 100th Current Magnitude Harmonics | Phase C 100th Current Magnitude Harmonics | Analog Input | %
803 | Phase N 100th Current Magnitude Harmonics | Phase N 100th Current Magnitude Harmonics | Analog Input | %
804 | Phase A 101st Voltage Magnitude Harmonics | Phase A 101st Voltage Magnitude Harmonics | Analog Input | %
805 | Phase B 101st Voltage Magnitude Harmonics | Phase B 101st Voltage Magnitude Harmonics | Analog Input | %
806 | Phase C 101st Voltage Magnitude Harmonics | Phase C 101st Voltage Magnitude Harmonics | Analog Input | %
807 | Phase A 101st Current Magnitude Harmonics | Phase A 101st Current Magnitude Harmonics | Analog Input | %
808 | Phase B 101st Current Magnitude Harmonics | Phase B 101st Current Magnitude Harmonics | Analog Input | %
809 | Phase C 101st Current Magnitude Harmonics | Phase C 101st Current Magnitude Harmonics | Analog Input | %
810 | Phase N 101st Current Magnitude Harmonics | Phase N 101st Current Magnitude Harmonics | Analog Input | %
811 | Phase A 102nd Voltage Magnitude Harmonics | Phase A 102nd Voltage Magnitude Harmonics | Analog Input | %
812 | Phase B 102nd Voltage Magnitude Harmonics | Phase B 102nd Voltage Magnitude Harmonics | Analog Input | %
813 | Phase C 102nd Voltage Magnitude Harmonics | Phase C 102nd Voltage Magnitude Harmonics | Analog Input | %
814 | Phase A 102nd Current Magnitude Harmonics | Phase A 102nd Current Magnitude Harmonics | Analog Input | %
815 | Phase B 102nd Current Magnitude Harmonics | Phase B 102nd Current Magnitude Harmonics | Analog Input | %
816 | Phase C 102nd Current Magnitude Harmonics | Phase C 102nd Current Magnitude Harmonics | Analog Input | %
817 | Phase N 102nd Current Magnitude Harmonics | Phase N 102nd Current Magnitude Harmonics | Analog Input | %
818 | Phase A 103rd Voltage Magnitude Harmonics | Phase A 103rd Voltage Magnitude Harmonics | Analog Input | %
819 | Phase B 103rd Voltage Magnitude Harmonics | Phase B 103rd Voltage Magnitude Harmonics | Analog Input | %
820 | Phase C 103rd Voltage Magnitude Harmonics | Phase C 103rd Voltage Magnitude Harmonics | Analog Input | %
821 | Phase A 103rd Current Magnitude Harmonics | Phase A 103rd Current Magnitude Harmonics | Analog Input | %
822 | Phase B 103rd Current Magnitude Harmonics | Phase B 103rd Current Magnitude Harmonics | Analog Input | %
823 | Phase C 103rd Current Magnitude Harmonics | Phase C 103rd Current Magnitude Harmonics | Analog Input | %
824 | Phase N 103rd Current Magnitude Harmonics | Phase N 103rd Current Magnitude Harmonics | Analog Input | %
825 | Phase A 104th Voltage Magnitude Harmonics | Phase A 104th Voltage Magnitude Harmonics | Analog Input | %
826 | Phase B 104th Voltage Magnitude Harmonics | Phase B 104th Voltage Magnitude Harmonics | Analog Input | %
827 | Phase C 104th Voltage Magnitude Harmonics | Phase C 104th Voltage Magnitude Harmonics | Analog Input | %
828 | Phase A 104th Current Magnitude Harmonics | Phase A 104th Current Magnitude Harmonics | Analog Input | %
829 | Phase B 104th Current Magnitude Harmonics | Phase B 104th Current Magnitude Harmonics | Analog Input | %
830 | Phase C 104th Current Magnitude Harmonics | Phase C 104th Current Magnitude Harmonics | Analog Input | %
831 | Phase N 104th Current Magnitude Harmonics | Phase N 104th Current Magnitude Harmonics | Analog Input | %
832 | Phase A 105th Voltage Magnitude Harmonics | Phase A 105th Voltage Magnitude Harmonics | Analog Input | %
833 | Phase B 105th Voltage Magnitude Harmonics | Phase B 105th Voltage Magnitude Harmonics | Analog Input | %
834 | Phase C 105th Voltage Magnitude Harmonics | Phase C 105th Voltage Magnitude Harmonics | Analog Input | %
835 | Phase A 105th Current Magnitude Harmonics | Phase A 105th Current Magnitude Harmonics | Analog Input | %
836 | Phase B 105th Current Magnitude Harmonics | Phase B 105th Current Magnitude Harmonics | Analog Input | %
837 | Phase C 105th Current Magnitude Harmonics | Phase C 105th Current Magnitude Harmonics | Analog Input | %
838 | Phase N 105th Current Magnitude Harmonics | Phase N 105th Current Magnitude Harmonics | Analog Input | %
839 | Phase A 106th Voltage Magnitude Harmonics | Phase A 106th Voltage Magnitude Harmonics | Analog Input | %
840 | Phase B 106th Voltage Magnitude Harmonics | Phase B 106th Voltage Magnitude Harmonics | Analog Input | %
841 | Phase C 106th Voltage Magnitude Harmonics | Phase C 106th Voltage Magnitude Harmonics | Analog Input | %
842 | Phase A 106th Current Magnitude Harmonics | Phase A 106th Current Magnitude Harmonics | Analog Input | %
843 | Phase B 106th Current Magnitude Harmonics | Phase B 106th Current Magnitude Harmonics | Analog Input | %
844 | Phase C 106th Current Magnitude Harmonics | Phase C 106th Current Magnitude Harmonics | Analog Input | %
845 | Phase N 106th Current Magnitude Harmonics | Phase N 106th Current Magnitude Harmonics | Analog Input | %
846 | Phase A 107th Voltage Magnitude Harmonics | Phase A 107th Voltage Magnitude Harmonics | Analog Input | %
847 | Phase B 107th Voltage Magnitude Harmonics | Phase B 107th Voltage Magnitude Harmonics | Analog Input | %
848 | Phase C 107th Voltage Magnitude Harmonics | Phase C 107th Voltage Magnitude Harmonics | Analog Input | %
849 | Phase A 107th Current Magnitude Harmonics | Phase A 107th Current Magnitude Harmonics | Analog Input | %
850 | Phase B 107th Current Magnitude Harmonics | Phase B 107th Current Magnitude Harmonics | Analog Input | %
851 | Phase C 107th Current Magnitude Harmonics | Phase C 107th Current Magnitude Harmonics | Analog Input | %
852 | Phase N 107th Current Magnitude Harmonics | Phase N 107th Current Magnitude Harmonics | Analog Input | %
853 | Phase A 108th Voltage Magnitude Harmonics | Phase A 108th Voltage Magnitude Harmonics | Analog Input | %
854 | Phase B 108th Voltage Magnitude Harmonics | Phase B 108th Voltage Magnitude Harmonics | Analog Input | %
855 | Phase C 108th Voltage Magnitude Harmonics | Phase C 108th Voltage Magnitude Harmonics | Analog Input | %
856 | Phase A 108th Current Magnitude Harmonics | Phase A 108th Current Magnitude Harmonics | Analog Input | %
857 | Phase B 108th Current Magnitude Harmonics | Phase B 108th Current Magnitude Harmonics | Analog Input | %
858 | Phase C 108th Current Magnitude Harmonics | Phase C 108th Current Magnitude Harmonics | Analog Input | %
859 | Phase N 108th Current Magnitude Harmonics | Phase N 108th Current Magnitude Harmonics | Analog Input | %
860 | Phase A 109th Voltage Magnitude Harmonics | Phase A 109th Voltage Magnitude Harmonics | Analog Input | %
861 | Phase B 109th Voltage Magnitude Harmonics | Phase B 109th Voltage Magnitude Harmonics | Analog Input | %
862 | Phase C 109th Voltage Magnitude Harmonics | Phase C 109th Voltage Magnitude Harmonics | Analog Input | %
863 | Phase A 109th Current Magnitude Harmonics | Phase A 109th Current Magnitude Harmonics | Analog Input | %
864 | Phase B 109th Current Magnitude Harmonics | Phase B 109th Current Magnitude Harmonics | Analog Input | %
865 | Phase C 109th Current Magnitude Harmonics | Phase C 109th Current Magnitude Harmonics | Analog Input | %
866 | Phase N 109th Current Magnitude Harmonics | Phase N 109th Current Magnitude Harmonics | Analog Input | %
867 | Phase A 110th Voltage Magnitude Harmonics | Phase A 110th Voltage Magnitude Harmonics | Analog Input | %
868 | Phase B 110th Voltage Magnitude Harmonics | Phase B 110th Voltage Magnitude Harmonics | Analog Input | %
869 | Phase C 110th Voltage Magnitude Harmonics | Phase C 110th Voltage Magnitude Harmonics | Analog Input | %
870 | Phase A 110th Current Magnitude Harmonics | Phase A 110th Current Magnitude Harmonics | Analog Input | %
871 | Phase B 110th Current Magnitude Harmonics | Phase B 110th Current Magnitude Harmonics | Analog Input | %
872 | Phase C 110th Current Magnitude Harmonics | Phase C 110th Current Magnitude Harmonics | Analog Input | %
873 | Phase N 110th Current Magnitude Harmonics | Phase N 110th Current Magnitude Harmonics | Analog Input | %
874 | Phase A 111st Voltage Magnitude Harmonics | Phase A 111st Voltage Magnitude Harmonics | Analog Input | %
875 | Phase B 111st Voltage Magnitude Harmonics | Phase B 111st Voltage Magnitude Harmonics | Analog Input | %
876 | Phase C 111st Voltage Magnitude Harmonics | Phase C 111st Voltage Magnitude Harmonics | Analog Input | %
877 | Phase A 111st Current Magnitude Harmonics | Phase A 111st Current Magnitude Harmonics | Analog Input | %
878 | Phase B 111st Current Magnitude Harmonics | Phase B 111st Current Magnitude Harmonics | Analog Input | %
879 | Phase C 111st Current Magnitude Harmonics | Phase C 111st Current Magnitude Harmonics | Analog Input | %
880 | Phase N 111st Current Magnitude Harmonics | Phase N 111st Current Magnitude Harmonics | Analog Input | %
881 | Phase A 112nd Voltage Magnitude Harmonics | Phase A 112nd Voltage Magnitude Harmonics | Analog Input | %
882 | Phase B 112nd Voltage Magnitude Harmonics | Phase B 112nd Voltage Magnitude Harmonics | Analog Input | %
883 | Phase C 112nd Voltage Magnitude Harmonics | Phase C 112nd Voltage Magnitude Harmonics | Analog Input | %
884 | Phase A 112nd Current Magnitude Harmonics | Phase A 112nd Current Magnitude Harmonics | Analog Input | %
885 | Phase B 112nd Current Magnitude Harmonics | Phase B 112nd Current Magnitude Harmonics | Analog Input | %
886 | Phase C 112nd Current Magnitude Harmonics | Phase C 112nd Current Magnitude Harmonics | Analog Input | %
887 | Phase N 112nd Current Magnitude Harmonics | Phase N 112nd Current Magnitude Harmonics | Analog Input | %
888 | Phase A 113rd Voltage Magnitude Harmonics | Phase A 113rd Voltage Magnitude Harmonics | Analog Input | %
889 | Phase B 113rd Voltage Magnitude Harmonics | Phase B 113rd Voltage Magnitude Harmonics | Analog Input | %
890 | Phase C 113rd Voltage Magnitude Harmonics | Phase C 113rd Voltage Magnitude Harmonics | Analog Input | %
891 | Phase A 113rd Current Magnitude Harmonics | Phase A 113rd Current Magnitude Harmonics | Analog Input | %
892 | Phase B 113rd Current Magnitude Harmonics | Phase B 113rd Current Magnitude Harmonics | Analog Input | %
893 | Phase C 113rd Current Magnitude Harmonics | Phase C 113rd Current Magnitude Harmonics | Analog Input | %
894 | Phase N 113rd Current Magnitude Harmonics | Phase N 113rd Current Magnitude Harmonics | Analog Input | %
895 | Phase A 114th Voltage Magnitude Harmonics | Phase A 114th Voltage Magnitude Harmonics | Analog Input | %
896 | Phase B 114th Voltage Magnitude Harmonics | Phase B 114th Voltage Magnitude Harmonics | Analog Input | %
897 | Phase C 114th Voltage Magnitude Harmonics | Phase C 114th Voltage Magnitude Harmonics | Analog Input | %
898 | Phase A 114th Current Magnitude Harmonics | Phase A 114th Current Magnitude Harmonics | Analog Input | %
899 | Phase B 114th Current Magnitude Harmonics | Phase B 114th Current Magnitude Harmonics | Analog Input | %
900 | Phase C 114th Current Magnitude Harmonics | Phase C 114th Current Magnitude Harmonics | Analog Input | %
901 | Phase N 114th Current Magnitude Harmonics | Phase N 114th Current Magnitude Harmonics | Analog Input | %
902 | Phase A 115th Voltage Magnitude Harmonics | Phase A 115th Voltage Magnitude Harmonics | Analog Input | %
903 | Phase B 115th Voltage Magnitude Harmonics | Phase B 115th Voltage Magnitude Harmonics | Analog Input | %
904 | Phase C 115th Voltage Magnitude Harmonics | Phase C 115th Voltage Magnitude Harmonics | Analog Input | %
905 | Phase A 115th Current Magnitude Harmonics | Phase A 115th Current Magnitude Harmonics | Analog Input | %
906 | Phase B 115th Current Magnitude Harmonics | Phase B 115th Current Magnitude Harmonics | Analog Input | %
907 | Phase C 115th Current Magnitude Harmonics | Phase C 115th Current Magnitude Harmonics | Analog Input | %
908 | Phase N 115th Current Magnitude Harmonics | Phase N 115th Current Magnitude Harmonics | Analog Input | %
909 | Phase A 116th Voltage Magnitude Harmonics | Phase A 116th Voltage Magnitude Harmonics | Analog Input | %
910 | Phase B 116th Voltage Magnitude Harmonics | Phase B 116th Voltage Magnitude Harmonics | Analog Input | %
911 | Phase C 116th Voltage Magnitude Harmonics | Phase C 116th Voltage Magnitude Harmonics | Analog Input | %
912 | Phase A 116th Current Magnitude Harmonics | Phase A 116th Current Magnitude Harmonics | Analog Input | %
913 | Phase B 116th Current Magnitude Harmonics | Phase B 116th Current Magnitude Harmonics | Analog Input | %
914 | Phase C 116th Current Magnitude Harmonics | Phase C 116th Current Magnitude Harmonics | Analog Input | %
915 | Phase N 116th Current Magnitude Harmonics | Phase N 116th Current Magnitude Harmonics | Analog Input | %
916 | Phase A 117th Voltage Magnitude Harmonics | Phase A 117th Voltage Magnitude Harmonics | Analog Input | %
917 | Phase B 117th Voltage Magnitude Harmonics | Phase B 117th Voltage Magnitude Harmonics | Analog Input | %
918 | Phase C 117th Voltage Magnitude Harmonics | Phase C 117th Voltage Magnitude Harmonics | Analog Input | %
919 | Phase A 117th Current Magnitude Harmonics | Phase A 117th Current Magnitude Harmonics | Analog Input | %
920 | Phase B 117th Current Magnitude Harmonics | Phase B 117th Current Magnitude Harmonics | Analog Input | %
921 | Phase C 117th Current Magnitude Harmonics | Phase C 117th Current Magnitude Harmonics | Analog Input | %
922 | Phase N 117th Current Magnitude Harmonics | Phase N 117th Current Magnitude Harmonics | Analog Input | %
923 | Phase A 118th Voltage Magnitude Harmonics | Phase A 118th Voltage Magnitude Harmonics | Analog Input | %
924 | Phase B 118th Voltage Magnitude Harmonics | Phase B 118th Voltage Magnitude Harmonics | Analog Input | %
925 | Phase C 118th Voltage Magnitude Harmonics | Phase C 118th Voltage Magnitude Harmonics | Analog Input | %
926 | Phase A 118th Current Magnitude Harmonics | Phase A 118th Current Magnitude Harmonics | Analog Input | %
927 | Phase B 118th Current Magnitude Harmonics | Phase B 118th Current Magnitude Harmonics | Analog Input | %
928 | Phase C 118th Current Magnitude Harmonics | Phase C 118th Current Magnitude Harmonics | Analog Input | %
929 | Phase N 118th Current Magnitude Harmonics | Phase N 118th Current Magnitude Harmonics | Analog Input | %
930 | Phase A 119th Voltage Magnitude Harmonics | Phase A 119th Voltage Magnitude Harmonics | Analog Input | %
931 | Phase B 119th Voltage Magnitude Harmonics | Phase B 119th Voltage Magnitude Harmonics | Analog Input | %
932 | Phase C 119th Voltage Magnitude Harmonics | Phase C 119th Voltage Magnitude Harmonics | Analog Input | %
933 | Phase A 119th Current Magnitude Harmonics | Phase A 119th Current Magnitude Harmonics | Analog Input | %
934 | Phase B 119th Current Magnitude Harmonics | Phase B 119th Current Magnitude Harmonics | Analog Input | %
935 | Phase C 119th Current Magnitude Harmonics | Phase C 119th Current Magnitude Harmonics | Analog Input | %
936 | Phase N 119th Current Magnitude Harmonics | Phase N 119th Current Magnitude Harmonics | Analog Input | %
937 | Phase A 120th Voltage Magnitude Harmonics | Phase A 120th Voltage Magnitude Harmonics | Analog Input | %
938 | Phase B 120th Voltage Magnitude Harmonics | Phase B 120th Voltage Magnitude Harmonics | Analog Input | %
939 | Phase C 120th Voltage Magnitude Harmonics | Phase C 120th Voltage Magnitude Harmonics | Analog Input | %
940 | Phase A 120th Current Magnitude Harmonics | Phase A 120th Current Magnitude Harmonics | Analog Input | %
941 | Phase B 120th Current Magnitude Harmonics | Phase B 120th Current Magnitude Harmonics | Analog Input | %
942 | Phase C 120th Current Magnitude Harmonics | Phase C 120th Current Magnitude Harmonics | Analog Input | %
943 | Phase N 120th Current Magnitude Harmonics | Phase N 120th Current Magnitude Harmonics | Analog Input | %
944 | Phase A 121st Voltage Magnitude Harmonics | Phase A 121st Voltage Magnitude Harmonics | Analog Input | %
945 | Phase B 121st Voltage Magnitude Harmonics | Phase B 121st Voltage Magnitude Harmonics | Analog Input | %
946 | Phase C 121st Voltage Magnitude Harmonics | Phase C 121st Voltage Magnitude Harmonics | Analog Input | %
947 | Phase A 121st Current Magnitude Harmonics | Phase A 121st Current Magnitude Harmonics | Analog Input | %
948 | Phase B 121st Current Magnitude Harmonics | Phase B 121st Current Magnitude Harmonics | Analog Input | %
949 | Phase C 121st Current Magnitude Harmonics | Phase C 121st Current Magnitude Harmonics | Analog Input | %
950 | Phase N 121st Current Magnitude Harmonics | Phase N 121st Current Magnitude Harmonics | Analog Input | %
951 | Phase A 122nd Voltage Magnitude Harmonics | Phase A 122nd Voltage Magnitude Harmonics | Analog Input | %
952 | Phase B 122nd Voltage Magnitude Harmonics | Phase B 122nd Voltage Magnitude Harmonics | Analog Input | %
953 | Phase C 122nd Voltage Magnitude Harmonics | Phase C 122nd Voltage Magnitude Harmonics | Analog Input | %
954 | Phase A 122nd Current Magnitude Harmonics | Phase A 122nd Current Magnitude Harmonics | Analog Input | %
955 | Phase B 122nd Current Magnitude Harmonics | Phase B 122nd Current Magnitude Harmonics | Analog Input | %
956 | Phase C 122nd Current Magnitude Harmonics | Phase C 122nd Current Magnitude Harmonics | Analog Input | %
957 | Phase N 122nd Current Magnitude Harmonics | Phase N 122nd Current Magnitude Harmonics | Analog Input | %
958 | Phase A 123rd Voltage Magnitude Harmonics | Phase A 123rd Voltage Magnitude Harmonics | Analog Input | %
959 | Phase B 123rd Voltage Magnitude Harmonics | Phase B 123rd Voltage Magnitude Harmonics | Analog Input | %
960 | Phase C 123rd Voltage Magnitude Harmonics | Phase C 123rd Voltage Magnitude Harmonics | Analog Input | %
961 | Phase A 123rd Current Magnitude Harmonics | Phase A 123rd Current Magnitude Harmonics | Analog Input | %
962 | Phase B 123rd Current Magnitude Harmonics | Phase B 123rd Current Magnitude Harmonics | Analog Input | %
963 | Phase C 123rd Current Magnitude Harmonics | Phase C 123rd Current Magnitude Harmonics | Analog Input | %
964 | Phase N 123rd Current Magnitude Harmonics | Phase N 123rd Current Magnitude Harmonics | Analog Input | %
965 | Phase A 124th Voltage Magnitude Harmonics | Phase A 124th Voltage Magnitude Harmonics | Analog Input | %
966 | Phase B 124th Voltage Magnitude Harmonics | Phase B 124th Voltage Magnitude Harmonics | Analog Input | %
967 | Phase C 124th Voltage Magnitude Harmonics | Phase C 124th Voltage Magnitude Harmonics | Analog Input | %
968 | Phase A 124th Current Magnitude Harmonics | Phase A 124th Current Magnitude Harmonics | Analog Input | %
969 | Phase B 124th Current Magnitude Harmonics | Phase B 124th Current Magnitude Harmonics | Analog Input | %
970 | Phase C 124th Current Magnitude Harmonics | Phase C 124th Current Magnitude Harmonics | Analog Input | %
971 | Phase N 124th Current Magnitude Harmonics | Phase N 124th Current Magnitude Harmonics | Analog Input | %
972 | Phase A 125th Voltage Magnitude Harmonics | Phase A 125th Voltage Magnitude Harmonics | Analog Input | %
973 | Phase B 125th Voltage Magnitude Harmonics | Phase B 125th Voltage Magnitude Harmonics | Analog Input | %
974 | Phase C 125th Voltage Magnitude Harmonics | Phase C 125th Voltage Magnitude Harmonics | Analog Input | %
975 | Phase A 125th Current Magnitude Harmonics | Phase A 125th Current Magnitude Harmonics | Analog Input | %
976 | Phase B 125th Current Magnitude Harmonics | Phase B 125th Current Magnitude Harmonics | Analog Input | %
977 | Phase C 125th Current Magnitude Harmonics | Phase C 125th Current Magnitude Harmonics | Analog Input | %
978 | Phase N 125th Current Magnitude Harmonics | Phase N 125th Current Magnitude Harmonics | Analog Input | %
979 | Phase A 126th Voltage Magnitude Harmonics | Phase A 126th Voltage Magnitude Harmonics | Analog Input | %
980 | Phase B 126th Voltage Magnitude Harmonics | Phase B 126th Voltage Magnitude Harmonics | Analog Input | %
981 | Phase C 126th Voltage Magnitude Harmonics | Phase C 126th Voltage Magnitude Harmonics | Analog Input | %
982 | Phase A 126th Current Magnitude Harmonics | Phase A 126th Current Magnitude Harmonics | Analog Input | %
983 | Phase B 126th Current Magnitude Harmonics | Phase B 126th Current Magnitude Harmonics | Analog Input | %
984 | Phase C 126th Current Magnitude Harmonics | Phase C 126th Current Magnitude Harmonics | Analog Input | %
985 | Phase N 126th Current Magnitude Harmonics | Phase N 126th Current Magnitude Harmonics | Analog Input | %
986 | Phase A 127th Voltage Magnitude Harmonics | Phase A 127th Voltage Magnitude Harmonics | Analog Input | %
987 | Phase B 127th Voltage Magnitude Harmonics | Phase B 127th Voltage Magnitude Harmonics | Analog Input | %
988 | Phase C 127th Voltage Magnitude Harmonics | Phase C 127th Voltage Magnitude Harmonics | Analog Input | %
989 | Phase A 127th Current Magnitude Harmonics | Phase A 127th Current Magnitude Harmonics | Analog Input | %
990 | Phase B 127th Current Magnitude Harmonics | Phase B 127th Current Magnitude Harmonics | Analog Input | %
991 | Phase C 127th Current Magnitude Harmonics | Phase C 127th Current Magnitude Harmonics | Analog Input | %
992 | Phase N 127th Current Magnitude Harmonics | Phase N 127th Current Magnitude Harmonics | Analog Input | %
Harmonics - Angle
993 | Phase A 1st Voltage Angle Harmonics | Phase A 1st Voltage Angle Harmonics | Analog Input | %
994 | Phase B 1st Voltage Angle Harmonics | Phase B 1st Voltage Angle Harmonics | Analog Input | %
995 | Phase C 1st Voltage Angle Harmonics | Phase C 1st Voltage Angle Harmonics | Analog Input | %
996 | Phase A 1st Current Angle Harmonics | Phase A 1st Current Angle Harmonics | Analog Input | %
997 | Phase B 1st Current Angle Harmonics | Phase B 1st Current Angle Harmonics | Analog Input | %
998 | Phase C 1st Current Angle Harmonics | Phase C 1st Current Angle Harmonics | Analog Input | %
999 | Phase N 1st Current Angle Harmonics | Phase N 1st Current Angle Harmonics | Analog Input | %
1000 | Phase A 2nd Voltage Angle Harmonics | Phase A 2nd Voltage Angle Harmonics | Analog Input | %
1001 | Phase B 2nd Voltage Angle Harmonics | Phase B 2nd Voltage Angle Harmonics | Analog Input | %
1002 | Phase C 2nd Voltage Angle Harmonics | Phase C 2nd Voltage Angle Harmonics | Analog Input | %
1003 | Phase A 2nd Current Angle Harmonics | Phase A 2nd Current Angle Harmonics | Analog Input | %
1004 | Phase B 2nd Current Angle Harmonics | Phase B 2nd Current Angle Harmonics | Analog Input | %
1005 | Phase C 2nd Current Angle Harmonics | Phase C 2nd Current Angle Harmonics | Analog Input | %
1006 | Phase N 2nd Current Angle Harmonics | Phase N 2nd Current Angle Harmonics | Analog Input | %
1007 | Phase A 3rd Voltage Angle Harmonics | Phase A 3rd Voltage Angle Harmonics | Analog Input | %
1008 | Phase B 3rd Voltage Angle Harmonics | Phase B 3rd Voltage Angle Harmonics | Analog Input | %
1009 | Phase C 3rd Voltage Angle Harmonics | Phase C 3rd Voltage Angle Harmonics | Analog Input | %
1010 | Phase A 3rd Current Angle Harmonics | Phase A 3rd Current Angle Harmonics | Analog Input | %
1011 | Phase B 3rd Current Angle Harmonics | Phase B 3rd Current Angle Harmonics | Analog Input | %
1012 | Phase C 3rd Current Angle Harmonics | Phase C 3rd Current Angle Harmonics | Analog Input | %
1013 | Phase N 3rd Current Angle Harmonics | Phase N 3rd Current Angle Harmonics | Analog Input | %
1014 | Phase A 4th Voltage Angle Harmonics | Phase A 4th Voltage Angle Harmonics | Analog Input | %
1015 | Phase B 4th Voltage Angle Harmonics | Phase B 4th Voltage Angle Harmonics | Analog Input | %
1016 | Phase C 4th Voltage Angle Harmonics | Phase C 4th Voltage Angle Harmonics | Analog Input | %
1017 | Phase A 4th Current Angle Harmonics | Phase A 4th Current Angle Harmonics | Analog Input | %
1018 | Phase B 4th Current Angle Harmonics | Phase B 4th Current Angle Harmonics | Analog Input | %
1019 | Phase C 4th Current Angle Harmonics | Phase C 4th Current Angle Harmonics | Analog Input | %
1020 | Phase N 4th Current Angle Harmonics | Phase N 4th Current Angle Harmonics | Analog Input | %
1021 | Phase A 5th Voltage Angle Harmonics | Phase A 5th Voltage Angle Harmonics | Analog Input | %
1022 | Phase B 5th Voltage Angle Harmonics | Phase B 5th Voltage Angle Harmonics | Analog Input | %
1023 | Phase C 5th Voltage Angle Harmonics | Phase C 5th Voltage Angle Harmonics | Analog Input | %
1024 | Phase A 5th Current Angle Harmonics | Phase A 5th Current Angle Harmonics | Analog Input | %
1025 | Phase B 5th Current Angle Harmonics | Phase B 5th Current Angle Harmonics | Analog Input | %
1026 | Phase C 5th Current Angle Harmonics | Phase C 5th Current Angle Harmonics | Analog Input | %
1027 | Phase N 5th Current Angle Harmonics | Phase N 5th Current Angle Harmonics | Analog Input | %
1028 | Phase A 6th Voltage Angle Harmonics | Phase A 6th Voltage Angle Harmonics | Analog Input | %
1029 | Phase B 6th Voltage Angle Harmonics | Phase B 6th Voltage Angle Harmonics | Analog Input | %
1030 | Phase C 6th Voltage Angle Harmonics | Phase C 6th Voltage Angle Harmonics | Analog Input | %
1031 | Phase A 6th Current Angle Harmonics | Phase A 6th Current Angle Harmonics | Analog Input | %
1032 | Phase B 6th Current Angle Harmonics | Phase B 6th Current Angle Harmonics | Analog Input | %
1033 | Phase C 6th Current Angle Harmonics | Phase C 6th Current Angle Harmonics | Analog Input | %
1034 | Phase N 6th Current Angle Harmonics | Phase N 6th Current Angle Harmonics | Analog Input | %
1035 | Phase A 7th Voltage Angle Harmonics | Phase A 7th Voltage Angle Harmonics | Analog Input | %
1036 | Phase B 7th Voltage Angle Harmonics | Phase B 7th Voltage Angle Harmonics | Analog Input | %
1037 | Phase C 7th Voltage Angle Harmonics | Phase C 7th Voltage Angle Harmonics | Analog Input | %
1038 | Phase A 7th Current Angle Harmonics | Phase A 7th Current Angle Harmonics | Analog Input | %
1039 | Phase B 7th Current Angle Harmonics | Phase B 7th Current Angle Harmonics | Analog Input | %
1040 | Phase C 7th Current Angle Harmonics | Phase C 7th Current Angle Harmonics | Analog Input | %
1041 | Phase N 7th Current Angle Harmonics | Phase N 7th Current Angle Harmonics | Analog Input | %
1042 | Phase A 8th Voltage Angle Harmonics | Phase A 8th Voltage Angle Harmonics | Analog Input | %
1043 | Phase B 8th Voltage Angle Harmonics | Phase B 8th Voltage Angle Harmonics | Analog Input | %
1044 | Phase C 8th Voltage Angle Harmonics | Phase C 8th Voltage Angle Harmonics | Analog Input | %
1045 | Phase A 8th Current Angle Harmonics | Phase A 8th Current Angle Harmonics | Analog Input | %
1046 | Phase B 8th Current Angle Harmonics | Phase B 8th Current Angle Harmonics | Analog Input | %
1047 | Phase C 8th Current Angle Harmonics | Phase C 8th Current Angle Harmonics | Analog Input | %
1048 | Phase N 8th Current Angle Harmonics | Phase N 8th Current Angle Harmonics | Analog Input | %
1049 | Phase A 9th Voltage Angle Harmonics | Phase A 9th Voltage Angle Harmonics | Analog Input | %
1050 | Phase B 9th Voltage Angle Harmonics | Phase B 9th Voltage Angle Harmonics | Analog Input | %
1051 | Phase C 9th Voltage Angle Harmonics | Phase C 9th Voltage Angle Harmonics | Analog Input | %
1052 | Phase A 9th Current Angle Harmonics | Phase A 9th Current Angle Harmonics | Analog Input | %
1053 | Phase B 9th Current Angle Harmonics | Phase B 9th Current Angle Harmonics | Analog Input | %
1054 | Phase C 9th Current Angle Harmonics | Phase C 9th Current Angle Harmonics | Analog Input | %
1055 | Phase N 9th Current Angle Harmonics | Phase N 9th Current Angle Harmonics | Analog Input | %
1056 | Phase A 10th Voltage Angle Harmonics | Phase A 10th Voltage Angle Harmonics | Analog Input | %
1057 | Phase B 10th Voltage Angle Harmonics | Phase B 10th Voltage Angle Harmonics | Analog Input | %
1058 | Phase C 10th Voltage Angle Harmonics | Phase C 10th Voltage Angle Harmonics | Analog Input | %
1059 | Phase A 10th Current Angle Harmonics | Phase A 10th Current Angle Harmonics | Analog Input | %
1060 | Phase B 10th Current Angle Harmonics | Phase B 10th Current Angle Harmonics | Analog Input | %
1061 | Phase C 10th Current Angle Harmonics | Phase C 10th Current Angle Harmonics | Analog Input | %
1062 | Phase N 10th Current Angle Harmonics | Phase N 10th Current Angle Harmonics | Analog Input | %
1063 | Phase A 11st Voltage Angle Harmonics | Phase A 11st Voltage Angle Harmonics | Analog Input | %
1064 | Phase B 11st Voltage Angle Harmonics | Phase B 11st Voltage Angle Harmonics | Analog Input | %
1065 | Phase C 11st Voltage Angle Harmonics | Phase C 11st Voltage Angle Harmonics | Analog Input | %
1066 | Phase A 11st Current Angle Harmonics | Phase A 11st Current Angle Harmonics | Analog Input | %
1067 | Phase B 11st Current Angle Harmonics | Phase B 11st Current Angle Harmonics | Analog Input | %
1068 | Phase C 11st Current Angle Harmonics | Phase C 11st Current Angle Harmonics | Analog Input | %
1069 | Phase N 11st Current Angle Harmonics | Phase N 11st Current Angle Harmonics | Analog Input | %
1070 | Phase A 12nd Voltage Angle Harmonics | Phase A 12nd Voltage Angle Harmonics | Analog Input | %
1071 | Phase B 12nd Voltage Angle Harmonics | Phase B 12nd Voltage Angle Harmonics | Analog Input | %
1072 | Phase C 12nd Voltage Angle Harmonics | Phase C 12nd Voltage Angle Harmonics | Analog Input | %
1073 | Phase A 12nd Current Angle Harmonics | Phase A 12nd Current Angle Harmonics | Analog Input | %
1074 | Phase B 12nd Current Angle Harmonics | Phase B 12nd Current Angle Harmonics | Analog Input | %
1075 | Phase C 12nd Current Angle Harmonics | Phase C 12nd Current Angle Harmonics | Analog Input | %
1076 | Phase N 12nd Current Angle Harmonics | Phase N 12nd Current Angle Harmonics | Analog Input | %
1077 | Phase A 13rd Voltage Angle Harmonics | Phase A 13rd Voltage Angle Harmonics | Analog Input | %
1078 | Phase B 13rd Voltage Angle Harmonics | Phase B 13rd Voltage Angle Harmonics | Analog Input | %
1079 | Phase C 13rd Voltage Angle Harmonics | Phase C 13rd Voltage Angle Harmonics | Analog Input | %
1080 | Phase A 13rd Current Angle Harmonics | Phase A 13rd Current Angle Harmonics | Analog Input | %
1081 | Phase B 13rd Current Angle Harmonics | Phase B 13rd Current Angle Harmonics | Analog Input | %
1082 | Phase C 13rd Current Angle Harmonics | Phase C 13rd Current Angle Harmonics | Analog Input | %
1083 | Phase N 13rd Current Angle Harmonics | Phase N 13rd Current Angle Harmonics | Analog Input | %
1084 | Phase A 14th Voltage Angle Harmonics | Phase A 14th Voltage Angle Harmonics | Analog Input | %
1085 | Phase B 14th Voltage Angle Harmonics | Phase B 14th Voltage Angle Harmonics | Analog Input | %
1086 | Phase C 14th Voltage Angle Harmonics | Phase C 14th Voltage Angle Harmonics | Analog Input | %
1087 | Phase A 14th Current Angle Harmonics | Phase A 14th Current Angle Harmonics | Analog Input | %
1088 | Phase B 14th Current Angle Harmonics | Phase B 14th Current Angle Harmonics | Analog Input | %
1089 | Phase C 14th Current Angle Harmonics | Phase C 14th Current Angle Harmonics | Analog Input | %
1090 | Phase N 14th Current Angle Harmonics | Phase N 14th Current Angle Harmonics | Analog Input | %
1091 | Phase A 15th Voltage Angle Harmonics | Phase A 15th Voltage Angle Harmonics | Analog Input | %
1092 | Phase B 15th Voltage Angle Harmonics | Phase B 15th Voltage Angle Harmonics | Analog Input | %
1093 | Phase C 15th Voltage Angle Harmonics | Phase C 15th Voltage Angle Harmonics | Analog Input | %
1094 | Phase A 15th Current Angle Harmonics | Phase A 15th Current Angle Harmonics | Analog Input | %
1095 | Phase B 15th Current Angle Harmonics | Phase B 15th Current Angle Harmonics | Analog Input | %
1096 | Phase C 15th Current Angle Harmonics | Phase C 15th Current Angle Harmonics | Analog Input | %
1097 | Phase N 15th Current Angle Harmonics | Phase N 15th Current Angle Harmonics | Analog Input | %
1098 | Phase A 16th Voltage Angle Harmonics | Phase A 16th Voltage Angle Harmonics | Analog Input | %
1099 | Phase B 16th Voltage Angle Harmonics | Phase B 16th Voltage Angle Harmonics | Analog Input | %
1100 | Phase C 16th Voltage Angle Harmonics | Phase C 16th Voltage Angle Harmonics | Analog Input | %
1101 | Phase A 16th Current Angle Harmonics | Phase A 16th Current Angle Harmonics | Analog Input | %
1102 | Phase B 16th Current Angle Harmonics | Phase B 16th Current Angle Harmonics | Analog Input | %
1103 | Phase C 16th Current Angle Harmonics | Phase C 16th Current Angle Harmonics | Analog Input | %
1104 | Phase N 16th Current Angle Harmonics | Phase N 16th Current Angle Harmonics | Analog Input | %
1105 | Phase A 17th Voltage Angle Harmonics | Phase A 17th Voltage Angle Harmonics | Analog Input | %
1106 | Phase B 17th Voltage Angle Harmonics | Phase B 17th Voltage Angle Harmonics | Analog Input | %
1107 | Phase C 17th Voltage Angle Harmonics | Phase C 17th Voltage Angle Harmonics | Analog Input | %
1108 | Phase A 17th Current Angle Harmonics | Phase A 17th Current Angle Harmonics | Analog Input | %
1109 | Phase B 17th Current Angle Harmonics | Phase B 17th Current Angle Harmonics | Analog Input | %
1110 | Phase C 17th Current Angle Harmonics | Phase C 17th Current Angle Harmonics | Analog Input | %
1111 | Phase N 17th Current Angle Harmonics | Phase N 17th Current Angle Harmonics | Analog Input | %
1112 | Phase A 18th Voltage Angle Harmonics | Phase A 18th Voltage Angle Harmonics | Analog Input | %
1113 | Phase B 18th Voltage Angle Harmonics | Phase B 18th Voltage Angle Harmonics | Analog Input | %
1114 | Phase C 18th Voltage Angle Harmonics | Phase C 18th Voltage Angle Harmonics | Analog Input | %
1115 | Phase A 18th Current Angle Harmonics | Phase A 18th Current Angle Harmonics | Analog Input | %
1116 | Phase B 18th Current Angle Harmonics | Phase B 18th Current Angle Harmonics | Analog Input | %
1117 | Phase C 18th Current Angle Harmonics | Phase C 18th Current Angle Harmonics | Analog Input | %
1118 | Phase N 18th Current Angle Harmonics | Phase N 18th Current Angle Harmonics | Analog Input | %
1119 | Phase A 19th Voltage Angle Harmonics | Phase A 19th Voltage Angle Harmonics | Analog Input | %
1120 | Phase B 19th Voltage Angle Harmonics | Phase B 19th Voltage Angle Harmonics | Analog Input | %
1121 | Phase C 19th Voltage Angle Harmonics | Phase C 19th Voltage Angle Harmonics | Analog Input | %
1122 | Phase A 19th Current Angle Harmonics | Phase A 19th Current Angle Harmonics | Analog Input | %
1123 | Phase B 19th Current Angle Harmonics | Phase B 19th Current Angle Harmonics | Analog Input | %
1124 | Phase C 19th Current Angle Harmonics | Phase C 19th Current Angle Harmonics | Analog Input | %
1125 | Phase N 19th Current Angle Harmonics | Phase N 19th Current Angle Harmonics | Analog Input | %
1126 | Phase A 20th Voltage Angle Harmonics | Phase A 20th Voltage Angle Harmonics | Analog Input | %
1127 | Phase B 20th Voltage Angle Harmonics | Phase B 20th Voltage Angle Harmonics | Analog Input | %
1128 | Phase C 20th Voltage Angle Harmonics | Phase C 20th Voltage Angle Harmonics | Analog Input | %
1129 | Phase A 20th Current Angle Harmonics | Phase A 20th Current Angle Harmonics | Analog Input | %
1130 | Phase B 20th Current Angle Harmonics | Phase B 20th Current Angle Harmonics | Analog Input | %
1131 | Phase C 20th Current Angle Harmonics | Phase C 20th Current Angle Harmonics | Analog Input | %
1132 | Phase N 20th Current Angle Harmonics | Phase N 20th Current Angle Harmonics | Analog Input | %
1133 | Phase A 21st Voltage Angle Harmonics | Phase A 21st Voltage Angle Harmonics | Analog Input | %
1134 | Phase B 21st Voltage Angle Harmonics | Phase B 21st Voltage Angle Harmonics | Analog Input | %
1135 | Phase C 21st Voltage Angle Harmonics | Phase C 21st Voltage Angle Harmonics | Analog Input | %
1136 | Phase A 21st Current Angle Harmonics | Phase A 21st Current Angle Harmonics | Analog Input | %
1137 | Phase B 21st Current Angle Harmonics | Phase B 21st Current Angle Harmonics | Analog Input | %
1138 | Phase C 21st Current Angle Harmonics | Phase C 21st Current Angle Harmonics | Analog Input | %
1139 | Phase N 21st Current Angle Harmonics | Phase N 21st Current Angle Harmonics | Analog Input | %
1140 | Phase A 22nd Voltage Angle Harmonics | Phase A 22nd Voltage Angle Harmonics | Analog Input | %
1141 | Phase B 22nd Voltage Angle Harmonics | Phase B 22nd Voltage Angle Harmonics | Analog Input | %
1142 | Phase C 22nd Voltage Angle Harmonics | Phase C 22nd Voltage Angle Harmonics | Analog Input | %
1143 | Phase A 22nd Current Angle Harmonics | Phase A 22nd Current Angle Harmonics | Analog Input | %
1144 | Phase B 22nd Current Angle Harmonics | Phase B 22nd Current Angle Harmonics | Analog Input | %
1145 | Phase C 22nd Current Angle Harmonics | Phase C 22nd Current Angle Harmonics | Analog Input | %
1146 | Phase N 22nd Current Angle Harmonics | Phase N 22nd Current Angle Harmonics | Analog Input | %
1147 | Phase A 23rd Voltage Angle Harmonics | Phase A 23rd Voltage Angle Harmonics | Analog Input | %
1148 | Phase B 23rd Voltage Angle Harmonics | Phase B 23rd Voltage Angle Harmonics | Analog Input | %
1149 | Phase C 23rd Voltage Angle Harmonics | Phase C 23rd Voltage Angle Harmonics | Analog Input | %
1150 | Phase A 23rd Current Angle Harmonics | Phase A 23rd Current Angle Harmonics | Analog Input | %
1151 | Phase B 23rd Current Angle Harmonics | Phase B 23rd Current Angle Harmonics | Analog Input | %
1152 | Phase C 23rd Current Angle Harmonics | Phase C 23rd Current Angle Harmonics | Analog Input | %
1153 | Phase N 23rd Current Angle Harmonics | Phase N 23rd Current Angle Harmonics | Analog Input | %
1154 | Phase A 24th Voltage Angle Harmonics | Phase A 24th Voltage Angle Harmonics | Analog Input | %
1155 | Phase B 24th Voltage Angle Harmonics | Phase B 24th Voltage Angle Harmonics | Analog Input | %
1156 | Phase C 24th Voltage Angle Harmonics | Phase C 24th Voltage Angle Harmonics | Analog Input | %
1157 | Phase A 24th Current Angle Harmonics | Phase A 24th Current Angle Harmonics | Analog Input | %
1158 | Phase B 24th Current Angle Harmonics | Phase B 24th Current Angle Harmonics | Analog Input | %
1159 | Phase C 24th Current Angle Harmonics | Phase C 24th Current Angle Harmonics | Analog Input | %
1160 | Phase N 24th Current Angle Harmonics | Phase N 24th Current Angle Harmonics | Analog Input | %
1161 | Phase A 25th Voltage Angle Harmonics | Phase A 25th Voltage Angle Harmonics | Analog Input | %
1162 | Phase B 25th Voltage Angle Harmonics | Phase B 25th Voltage Angle Harmonics | Analog Input | %
1163 | Phase C 25th Voltage Angle Harmonics | Phase C 25th Voltage Angle Harmonics | Analog Input | %
1164 | Phase A 25th Current Angle Harmonics | Phase A 25th Current Angle Harmonics | Analog Input | %
1165 | Phase B 25th Current Angle Harmonics | Phase B 25th Current Angle Harmonics | Analog Input | %
1166 | Phase C 25th Current Angle Harmonics | Phase C 25th Current Angle Harmonics | Analog Input | %
1167 | Phase N 25th Current Angle Harmonics | Phase N 25th Current Angle Harmonics | Analog Input | %
1168 | Phase A 26th Voltage Angle Harmonics | Phase A 26th Voltage Angle Harmonics | Analog Input | %
1169 | Phase B 26th Voltage Angle Harmonics | Phase B 26th Voltage Angle Harmonics | Analog Input | %
1170 | Phase C 26th Voltage Angle Harmonics | Phase C 26th Voltage Angle Harmonics | Analog Input | %
1171 | Phase A 26th Current Angle Harmonics | Phase A 26th Current Angle Harmonics | Analog Input | %
1172 | Phase B 26th Current Angle Harmonics | Phase B 26th Current Angle Harmonics | Analog Input | %
1173 | Phase C 26th Current Angle Harmonics | Phase C 26th Current Angle Harmonics | Analog Input | %
1174 | Phase N 26th Current Angle Harmonics | Phase N 26th Current Angle Harmonics | Analog Input | %
1175 | Phase A 27th Voltage Angle Harmonics | Phase A 27th Voltage Angle Harmonics | Analog Input | %
1176 | Phase B 27th Voltage Angle Harmonics | Phase B 27th Voltage Angle Harmonics | Analog Input | %
1177 | Phase C 27th Voltage Angle Harmonics | Phase C 27th Voltage Angle Harmonics | Analog Input | %
1178 | Phase A 27th Current Angle Harmonics | Phase A 27th Current Angle Harmonics | Analog Input | %
1179 | Phase B 27th Current Angle Harmonics | Phase B 27th Current Angle Harmonics | Analog Input | %
1180 | Phase C 27th Current Angle Harmonics | Phase C 27th Current Angle Harmonics | Analog Input | %
1181 | Phase N 27th Current Angle Harmonics | Phase N 27th Current Angle Harmonics | Analog Input | %
1182 | Phase A 28th Voltage Angle Harmonics | Phase A 28th Voltage Angle Harmonics | Analog Input | %
1183 | Phase B 28th Voltage Angle Harmonics | Phase B 28th Voltage Angle Harmonics | Analog Input | %
1184 | Phase C 28th Voltage Angle Harmonics | Phase C 28th Voltage Angle Harmonics | Analog Input | %
1185 | Phase A 28th Current Angle Harmonics | Phase A 28th Current Angle Harmonics | Analog Input | %
1186 | Phase B 28th Current Angle Harmonics | Phase B 28th Current Angle Harmonics | Analog Input | %
1187 | Phase C 28th Current Angle Harmonics | Phase C 28th Current Angle Harmonics | Analog Input | %
1188 | Phase N 28th Current Angle Harmonics | Phase N 28th Current Angle Harmonics | Analog Input | %
1189 | Phase A 29th Voltage Angle Harmonics | Phase A 29th Voltage Angle Harmonics | Analog Input | %
1190 | Phase B 29th Voltage Angle Harmonics | Phase B 29th Voltage Angle Harmonics | Analog Input | %
1191 | Phase C 29th Voltage Angle Harmonics | Phase C 29th Voltage Angle Harmonics | Analog Input | %
1192 | Phase A 29th Current Angle Harmonics | Phase A 29th Current Angle Harmonics | Analog Input | %
1193 | Phase B 29th Current Angle Harmonics | Phase B 29th Current Angle Harmonics | Analog Input | %
1194 | Phase C 29th Current Angle Harmonics | Phase C 29th Current Angle Harmonics | Analog Input | %
1195 | Phase N 29th Current Angle Harmonics | Phase N 29th Current Angle Harmonics | Analog Input | %
1196 | Phase A 30th Voltage Angle Harmonics | Phase A 30th Voltage Angle Harmonics | Analog Input | %
1197 | Phase B 30th Voltage Angle Harmonics | Phase B 30th Voltage Angle Harmonics | Analog Input | %
1198 | Phase C 30th Voltage Angle Harmonics | Phase C 30th Voltage Angle Harmonics | Analog Input | %
1199 | Phase A 30th Current Angle Harmonics | Phase A 30th Current Angle Harmonics | Analog Input | %
1200 | Phase B 30th Current Angle Harmonics | Phase B 30th Current Angle Harmonics | Analog Input | %
1201 | Phase C 30th Current Angle Harmonics | Phase C 30th Current Angle Harmonics | Analog Input | %
1202 | Phase N 30th Current Angle Harmonics | Phase N 30th Current Angle Harmonics | Analog Input | %
1203 | Phase A 31st Voltage Angle Harmonics | Phase A 31st Voltage Angle Harmonics | Analog Input | %
1204 | Phase B 31st Voltage Angle Harmonics | Phase B 31st Voltage Angle Harmonics | Analog Input | %
1205 | Phase C 31st Voltage Angle Harmonics | Phase C 31st Voltage Angle Harmonics | Analog Input | %
1206 | Phase A 31st Current Angle Harmonics | Phase A 31st Current Angle Harmonics | Analog Input | %
1207 | Phase B 31st Current Angle Harmonics | Phase B 31st Current Angle Harmonics | Analog Input | %
1208 | Phase C 31st Current Angle Harmonics | Phase C 31st Current Angle Harmonics | Analog Input | %
1209 | Phase N 31st Current Angle Harmonics | Phase N 31st Current Angle Harmonics | Analog Input | %
1210 | Phase A 32nd Voltage Angle Harmonics | Phase A 32nd Voltage Angle Harmonics | Analog Input | %
1211 | Phase B 32nd Voltage Angle Harmonics | Phase B 32nd Voltage Angle Harmonics | Analog Input | %
1212 | Phase C 32nd Voltage Angle Harmonics | Phase C 32nd Voltage Angle Harmonics | Analog Input | %
1213 | Phase A 32nd Current Angle Harmonics | Phase A 32nd Current Angle Harmonics | Analog Input | %
1214 | Phase B 32nd Current Angle Harmonics | Phase B 32nd Current Angle Harmonics | Analog Input | %
1215 | Phase C 32nd Current Angle Harmonics | Phase C 32nd Current Angle Harmonics | Analog Input | %
1216 | Phase N 32nd Current Angle Harmonics | Phase N 32nd Current Angle Harmonics | Analog Input | %
1217 | Phase A 33rd Voltage Angle Harmonics | Phase A 33rd Voltage Angle Harmonics | Analog Input | %
1218 | Phase B 33rd Voltage Angle Harmonics | Phase B 33rd Voltage Angle Harmonics | Analog Input | %
1219 | Phase C 33rd Voltage Angle Harmonics | Phase C 33rd Voltage Angle Harmonics | Analog Input | %
1220 | Phase A 33rd Current Angle Harmonics | Phase A 33rd Current Angle Harmonics | Analog Input | %
1221 | Phase B 33rd Current Angle Harmonics | Phase B 33rd Current Angle Harmonics | Analog Input | %
1222 | Phase C 33rd Current Angle Harmonics | Phase C 33rd Current Angle Harmonics | Analog Input | %
1223 | Phase N 33rd Current Angle Harmonics | Phase N 33rd Current Angle Harmonics | Analog Input | %
1224 | Phase A 34th Voltage Angle Harmonics | Phase A 34th Voltage Angle Harmonics | Analog Input | %
1225 | Phase B 34th Voltage Angle Harmonics | Phase B 34th Voltage Angle Harmonics | Analog Input | %
1226 | Phase C 34th Voltage Angle Harmonics | Phase C 34th Voltage Angle Harmonics | Analog Input | %
1227 | Phase A 34th Current Angle Harmonics | Phase A 34th Current Angle Harmonics | Analog Input | %
1228 | Phase B 34th Current Angle Harmonics | Phase B 34th Current Angle Harmonics | Analog Input | %
1229 | Phase C 34th Current Angle Harmonics | Phase C 34th Current Angle Harmonics | Analog Input | %
1230 | Phase N 34th Current Angle Harmonics | Phase N 34th Current Angle Harmonics | Analog Input | %
1231 | Phase A 35th Voltage Angle Harmonics | Phase A 35th Voltage Angle Harmonics | Analog Input | %
1232 | Phase B 35th Voltage Angle Harmonics | Phase B 35th Voltage Angle Harmonics | Analog Input | %
1233 | Phase C 35th Voltage Angle Harmonics | Phase C 35th Voltage Angle Harmonics | Analog Input | %
1234 | Phase A 35th Current Angle Harmonics | Phase A 35th Current Angle Harmonics | Analog Input | %
1235 | Phase B 35th Current Angle Harmonics | Phase B 35th Current Angle Harmonics | Analog Input | %
1236 | Phase C 35th Current Angle Harmonics | Phase C 35th Current Angle Harmonics | Analog Input | %
1237 | Phase N 35th Current Angle Harmonics | Phase N 35th Current Angle Harmonics | Analog Input | %
1238 | Phase A 36th Voltage Angle Harmonics | Phase A 36th Voltage Angle Harmonics | Analog Input | %
1239 | Phase B 36th Voltage Angle Harmonics | Phase B 36th Voltage Angle Harmonics | Analog Input | %
1240 | Phase C 36th Voltage Angle Harmonics | Phase C 36th Voltage Angle Harmonics | Analog Input | %
1241 | Phase A 36th Current Angle Harmonics | Phase A 36th Current Angle Harmonics | Analog Input | %
1242 | Phase B 36th Current Angle Harmonics | Phase B 36th Current Angle Harmonics | Analog Input | %
1243 | Phase C 36th Current Angle Harmonics | Phase C 36th Current Angle Harmonics | Analog Input | %
1244 | Phase N 36th Current Angle Harmonics | Phase N 36th Current Angle Harmonics | Analog Input | %
1245 | Phase A 37th Voltage Angle Harmonics | Phase A 37th Voltage Angle Harmonics | Analog Input | %
1246 | Phase B 37th Voltage Angle Harmonics | Phase B 37th Voltage Angle Harmonics | Analog Input | %
1247 | Phase C 37th Voltage Angle Harmonics | Phase C 37th Voltage Angle Harmonics | Analog Input | %
1248 | Phase A 37th Current Angle Harmonics | Phase A 37th Current Angle Harmonics | Analog Input | %
1249 | Phase B 37th Current Angle Harmonics | Phase B 37th Current Angle Harmonics | Analog Input | %
1250 | Phase C 37th Current Angle Harmonics | Phase C 37th Current Angle Harmonics | Analog Input | %
1251 | Phase N 37th Current Angle Harmonics | Phase N 37th Current Angle Harmonics | Analog Input | %
1252 | Phase A 38th Voltage Angle Harmonics | Phase A 38th Voltage Angle Harmonics | Analog Input | %
1253 | Phase B 38th Voltage Angle Harmonics | Phase B 38th Voltage Angle Harmonics | Analog Input | %
1254 | Phase C 38th Voltage Angle Harmonics | Phase C 38th Voltage Angle Harmonics | Analog Input | %
1255 | Phase A 38th Current Angle Harmonics | Phase A 38th Current Angle Harmonics | Analog Input | %
1256 | Phase B 38th Current Angle Harmonics | Phase B 38th Current Angle Harmonics | Analog Input | %
1257 | Phase C 38th Current Angle Harmonics | Phase C 38th Current Angle Harmonics | Analog Input | %
1258 | Phase N 38th Current Angle Harmonics | Phase N 38th Current Angle Harmonics | Analog Input | %
1259 | Phase A 39th Voltage Angle Harmonics | Phase A 39th Voltage Angle Harmonics | Analog Input | %
1260 | Phase B 39th Voltage Angle Harmonics | Phase B 39th Voltage Angle Harmonics | Analog Input | %
1261 | Phase C 39th Voltage Angle Harmonics | Phase C 39th Voltage Angle Harmonics | Analog Input | %
1262 | Phase A 39th Current Angle Harmonics | Phase A 39th Current Angle Harmonics | Analog Input | %
1263 | Phase B 39th Current Angle Harmonics | Phase B 39th Current Angle Harmonics | Analog Input | %
1264 | Phase C 39th Current Angle Harmonics | Phase C 39th Current Angle Harmonics | Analog Input | %
1265 | Phase N 39th Current Angle Harmonics | Phase N 39th Current Angle Harmonics | Analog Input | %
1266 | Phase A 40th Voltage Angle Harmonics | Phase A 40th Voltage Angle Harmonics | Analog Input | %
1267 | Phase B 40th Voltage Angle Harmonics | Phase B 40th Voltage Angle Harmonics | Analog Input | %
1268 | Phase C 40th Voltage Angle Harmonics | Phase C 40th Voltage Angle Harmonics | Analog Input | %
1269 | Phase A 40th Current Angle Harmonics | Phase A 40th Current Angle Harmonics | Analog Input | %
1270 | Phase B 40th Current Angle Harmonics | Phase B 40th Current Angle Harmonics | Analog Input | %
1271 | Phase C 40th Current Angle Harmonics | Phase C 40th Current Angle Harmonics | Analog Input | %
1272 | Phase N 40th Current Angle Harmonics | Phase N 40th Current Angle Harmonics | Analog Input | %
1273 | Phase A 41st Voltage Angle Harmonics | Phase A 41st Voltage Angle Harmonics | Analog Input | %
1274 | Phase B 41st Voltage Angle Harmonics | Phase B 41st Voltage Angle Harmonics | Analog Input | %
1275 | Phase C 41st Voltage Angle Harmonics | Phase C 41st Voltage Angle Harmonics | Analog Input | %
1276 | Phase A 41st Current Angle Harmonics | Phase A 41st Current Angle Harmonics | Analog Input | %
1277 | Phase B 41st Current Angle Harmonics | Phase B 41st Current Angle Harmonics | Analog Input | %
1278 | Phase C 41st Current Angle Harmonics | Phase C 41st Current Angle Harmonics | Analog Input | %
1279 | Phase N 41st Current Angle Harmonics | Phase N 41st Current Angle Harmonics | Analog Input | %
1280 | Phase A 42nd Voltage Angle Harmonics | Phase A 42nd Voltage Angle Harmonics | Analog Input | %
1281 | Phase B 42nd Voltage Angle Harmonics | Phase B 42nd Voltage Angle Harmonics | Analog Input | %
1282 | Phase C 42nd Voltage Angle Harmonics | Phase C 42nd Voltage Angle Harmonics | Analog Input | %
1283 | Phase A 42nd Current Angle Harmonics | Phase A 42nd Current Angle Harmonics | Analog Input | %
1284 | Phase B 42nd Current Angle Harmonics | Phase B 42nd Current Angle Harmonics | Analog Input | %
1285 | Phase C 42nd Current Angle Harmonics | Phase C 42nd Current Angle Harmonics | Analog Input | %
1286 | Phase N 42nd Current Angle Harmonics | Phase N 42nd Current Angle Harmonics | Analog Input | %
1287 | Phase A 43rd Voltage Angle Harmonics | Phase A 43rd Voltage Angle Harmonics | Analog Input | %
1288 | Phase B 43rd Voltage Angle Harmonics | Phase B 43rd Voltage Angle Harmonics | Analog Input | %
1289 | Phase C 43rd Voltage Angle Harmonics | Phase C 43rd Voltage Angle Harmonics | Analog Input | %
1290 | Phase A 43rd Current Angle Harmonics | Phase A 43rd Current Angle Harmonics | Analog Input | %
1291 | Phase B 43rd Current Angle Harmonics | Phase B 43rd Current Angle Harmonics | Analog Input | %
1292 | Phase C 43rd Current Angle Harmonics | Phase C 43rd Current Angle Harmonics | Analog Input | %
1293 | Phase N 43rd Current Angle Harmonics | Phase N 43rd Current Angle Harmonics | Analog Input | %
1294 | Phase A 44th Voltage Angle Harmonics | Phase A 44th Voltage Angle Harmonics | Analog Input | %
1295 | Phase B 44th Voltage Angle Harmonics | Phase B 44th Voltage Angle Harmonics | Analog Input | %
1296 | Phase C 44th Voltage Angle Harmonics | Phase C 44th Voltage Angle Harmonics | Analog Input | %
1297 | Phase A 44th Current Angle Harmonics | Phase A 44th Current Angle Harmonics | Analog Input | %
1298 | Phase B 44th Current Angle Harmonics | Phase B 44th Current Angle Harmonics | Analog Input | %
1299 | Phase C 44th Current Angle Harmonics | Phase C 44th Current Angle Harmonics | Analog Input | %
1300 | Phase N 44th Current Angle Harmonics | Phase N 44th Current Angle Harmonics | Analog Input | %
1301 | Phase A 45th Voltage Angle Harmonics | Phase A 45th Voltage Angle Harmonics | Analog Input | %
1302 | Phase B 45th Voltage Angle Harmonics | Phase B 45th Voltage Angle Harmonics | Analog Input | %
1303 | Phase C 45th Voltage Angle Harmonics | Phase C 45th Voltage Angle Harmonics | Analog Input | %
1304 | Phase A 45th Current Angle Harmonics | Phase A 45th Current Angle Harmonics | Analog Input | %
1305 | Phase B 45th Current Angle Harmonics | Phase B 45th Current Angle Harmonics | Analog Input | %
1306 | Phase C 45th Current Angle Harmonics | Phase C 45th Current Angle Harmonics | Analog Input | %
1307 | Phase N 45th Current Angle Harmonics | Phase N 45th Current Angle Harmonics | Analog Input | %
1308 | Phase A 46th Voltage Angle Harmonics | Phase A 46th Voltage Angle Harmonics | Analog Input | %
1309 | Phase B 46th Voltage Angle Harmonics | Phase B 46th Voltage Angle Harmonics | Analog Input | %
1310 | Phase C 46th Voltage Angle Harmonics | Phase C 46th Voltage Angle Harmonics | Analog Input | %
1311 | Phase A 46th Current Angle Harmonics | Phase A 46th Current Angle Harmonics | Analog Input | %
1312 | Phase B 46th Current Angle Harmonics | Phase B 46th Current Angle Harmonics | Analog Input | %
1313 | Phase C 46th Current Angle Harmonics | Phase C 46th Current Angle Harmonics | Analog Input | %
1314 | Phase N 46th Current Angle Harmonics | Phase N 46th Current Angle Harmonics | Analog Input | %
1315 | Phase A 47th Voltage Angle Harmonics | Phase A 47th Voltage Angle Harmonics | Analog Input | %
1316 | Phase B 47th Voltage Angle Harmonics | Phase B 47th Voltage Angle Harmonics | Analog Input | %
1317 | Phase C 47th Voltage Angle Harmonics | Phase C 47th Voltage Angle Harmonics | Analog Input | %
1318 | Phase A 47th Current Angle Harmonics | Phase A 47th Current Angle Harmonics | Analog Input | %
1319 | Phase B 47th Current Angle Harmonics | Phase B 47th Current Angle Harmonics | Analog Input | %
1320 | Phase C 47th Current Angle Harmonics | Phase C 47th Current Angle Harmonics | Analog Input | %
1321 | Phase N 47th Current Angle Harmonics | Phase N 47th Current Angle Harmonics | Analog Input | %
1322 | Phase A 48th Voltage Angle Harmonics | Phase A 48th Voltage Angle Harmonics | Analog Input | %
1323 | Phase B 48th Voltage Angle Harmonics | Phase B 48th Voltage Angle Harmonics | Analog Input | %
1324 | Phase C 48th Voltage Angle Harmonics | Phase C 48th Voltage Angle Harmonics | Analog Input | %
1325 | Phase A 48th Current Angle Harmonics | Phase A 48th Current Angle Harmonics | Analog Input | %
1326 | Phase B 48th Current Angle Harmonics | Phase B 48th Current Angle Harmonics | Analog Input | %
1327 | Phase C 48th Current Angle Harmonics | Phase C 48th Current Angle Harmonics | Analog Input | %
1328 | Phase N 48th Current Angle Harmonics | Phase N 48th Current Angle Harmonics | Analog Input | %
1329 | Phase A 49th Voltage Angle Harmonics | Phase A 49th Voltage Angle Harmonics | Analog Input | %
1330 | Phase B 49th Voltage Angle Harmonics | Phase B 49th Voltage Angle Harmonics | Analog Input | %
1331 | Phase C 49th Voltage Angle Harmonics | Phase C 49th Voltage Angle Harmonics | Analog Input | %
1332 | Phase A 49th Current Angle Harmonics | Phase A 49th Current Angle Harmonics | Analog Input | %
1333 | Phase B 49th Current Angle Harmonics | Phase B 49th Current Angle Harmonics | Analog Input | %
1334 | Phase C 49th Current Angle Harmonics | Phase C 49th Current Angle Harmonics | Analog Input | %
1335 | Phase N 49th Current Angle Harmonics | Phase N 49th Current Angle Harmonics | Analog Input | %
1336 | Phase A 50th Voltage Angle Harmonics | Phase A 50th Voltage Angle Harmonics | Analog Input | %
1337 | Phase B 50th Voltage Angle Harmonics | Phase B 50th Voltage Angle Harmonics | Analog Input | %
1338 | Phase C 50th Voltage Angle Harmonics | Phase C 50th Voltage Angle Harmonics | Analog Input | %
1339 | Phase A 50th Current Angle Harmonics | Phase A 50th Current Angle Harmonics | Analog Input | %
1340 | Phase B 50th Current Angle Harmonics | Phase B 50th Current Angle Harmonics | Analog Input | %
1341 | Phase C 50th Current Angle Harmonics | Phase C 50th Current Angle Harmonics | Analog Input | %
1342 | Phase N 50th Current Angle Harmonics | Phase N 50th Current Angle Harmonics | Analog Input | %
1343 | Phase A 51st Voltage Angle Harmonics | Phase A 51st Voltage Angle Harmonics | Analog Input | %
1344 | Phase B 51st Voltage Angle Harmonics | Phase B 51st Voltage Angle Harmonics | Analog Input | %
1345 | Phase C 51st Voltage Angle Harmonics | Phase C 51st Voltage Angle Harmonics | Analog Input | %
1346 | Phase A 51st Current Angle Harmonics | Phase A 51st Current Angle Harmonics | Analog Input | %
1347 | Phase B 51st Current Angle Harmonics | Phase B 51st Current Angle Harmonics | Analog Input | %
1348 | Phase C 51st Current Angle Harmonics | Phase C 51st Current Angle Harmonics | Analog Input | %
1349 | Phase N 51st Current Angle Harmonics | Phase N 51st Current Angle Harmonics | Analog Input | %
1350 | Phase A 52nd Voltage Angle Harmonics | Phase A 52nd Voltage Angle Harmonics | Analog Input | %
1351 | Phase B 52nd Voltage Angle Harmonics | Phase B 52nd Voltage Angle Harmonics | Analog Input | %
1352 | Phase C 52nd Voltage Angle Harmonics | Phase C 52nd Voltage Angle Harmonics | Analog Input | %
1353 | Phase A 52nd Current Angle Harmonics | Phase A 52nd Current Angle Harmonics | Analog Input | %
1354 | Phase B 52nd Current Angle Harmonics | Phase B 52nd Current Angle Harmonics | Analog Input | %
1355 | Phase C 52nd Current Angle Harmonics | Phase C 52nd Current Angle Harmonics | Analog Input | %
1356 | Phase N 52nd Current Angle Harmonics | Phase N 52nd Current Angle Harmonics | Analog Input | %
1357 | Phase A 53rd Voltage Angle Harmonics | Phase A 53rd Voltage Angle Harmonics | Analog Input | %
1358 | Phase B 53rd Voltage Angle Harmonics | Phase B 53rd Voltage Angle Harmonics | Analog Input | %
1359 | Phase C 53rd Voltage Angle Harmonics | Phase C 53rd Voltage Angle Harmonics | Analog Input | %
1360 | Phase A 53rd Current Angle Harmonics | Phase A 53rd Current Angle Harmonics | Analog Input | %
1361 | Phase B 53rd Current Angle Harmonics | Phase B 53rd Current Angle Harmonics | Analog Input | %
1362 | Phase C 53rd Current Angle Harmonics | Phase C 53rd Current Angle Harmonics | Analog Input | %
1363 | Phase N 53rd Current Angle Harmonics | Phase N 53rd Current Angle Harmonics | Analog Input | %
1364 | Phase A 54th Voltage Angle Harmonics | Phase A 54th Voltage Angle Harmonics | Analog Input | %
1365 | Phase B 54th Voltage Angle Harmonics | Phase B 54th Voltage Angle Harmonics | Analog Input | %
1366 | Phase C 54th Voltage Angle Harmonics | Phase C 54th Voltage Angle Harmonics | Analog Input | %
1367 | Phase A 54th Current Angle Harmonics | Phase A 54th Current Angle Harmonics | Analog Input | %
1368 | Phase B 54th Current Angle Harmonics | Phase B 54th Current Angle Harmonics | Analog Input | %
1369 | Phase C 54th Current Angle Harmonics | Phase C 54th Current Angle Harmonics | Analog Input | %
1370 | Phase N 54th Current Angle Harmonics | Phase N 54th Current Angle Harmonics | Analog Input | %
1371 | Phase A 55th Voltage Angle Harmonics | Phase A 55th Voltage Angle Harmonics | Analog Input | %
1372 | Phase B 55th Voltage Angle Harmonics | Phase B 55th Voltage Angle Harmonics | Analog Input | %
1373 | Phase C 55th Voltage Angle Harmonics | Phase C 55th Voltage Angle Harmonics | Analog Input | %
1374 | Phase A 55th Current Angle Harmonics | Phase A 55th Current Angle Harmonics | Analog Input | %
1375 | Phase B 55th Current Angle Harmonics | Phase B 55th Current Angle Harmonics | Analog Input | %
1376 | Phase C 55th Current Angle Harmonics | Phase C 55th Current Angle Harmonics | Analog Input | %
1377 | Phase N 55th Current Angle Harmonics | Phase N 55th Current Angle Harmonics | Analog Input | %
1378 | Phase A 56th Voltage Angle Harmonics | Phase A 56th Voltage Angle Harmonics | Analog Input | %
1379 | Phase B 56th Voltage Angle Harmonics | Phase B 56th Voltage Angle Harmonics | Analog Input | %
1380 | Phase C 56th Voltage Angle Harmonics | Phase C 56th Voltage Angle Harmonics | Analog Input | %
1381 | Phase A 56th Current Angle Harmonics | Phase A 56th Current Angle Harmonics | Analog Input | %
1382 | Phase B 56th Current Angle Harmonics | Phase B 56th Current Angle Harmonics | Analog Input | %
1383 | Phase C 56th Current Angle Harmonics | Phase C 56th Current Angle Harmonics | Analog Input | %
1384 | Phase N 56th Current Angle Harmonics | Phase N 56th Current Angle Harmonics | Analog Input | %
1385 | Phase A 57th Voltage Angle Harmonics | Phase A 57th Voltage Angle Harmonics | Analog Input | %
1386 | Phase B 57th Voltage Angle Harmonics | Phase B 57th Voltage Angle Harmonics | Analog Input | %
1387 | Phase C 57th Voltage Angle Harmonics | Phase C 57th Voltage Angle Harmonics | Analog Input | %
1388 | Phase A 57th Current Angle Harmonics | Phase A 57th Current Angle Harmonics | Analog Input | %
1389 | Phase B 57th Current Angle Harmonics | Phase B 57th Current Angle Harmonics | Analog Input | %
1390 | Phase C 57th Current Angle Harmonics | Phase C 57th Current Angle Harmonics | Analog Input | %
1391 | Phase N 57th Current Angle Harmonics | Phase N 57th Current Angle Harmonics | Analog Input | %
1392 | Phase A 58th Voltage Angle Harmonics | Phase A 58th Voltage Angle Harmonics | Analog Input | %
1393 | Phase B 58th Voltage Angle Harmonics | Phase B 58th Voltage Angle Harmonics | Analog Input | %
1394 | Phase C 58th Voltage Angle Harmonics | Phase C 58th Voltage Angle Harmonics | Analog Input | %
1395 | Phase A 58th Current Angle Harmonics | Phase A 58th Current Angle Harmonics | Analog Input | %
1396 | Phase B 58th Current Angle Harmonics | Phase B 58th Current Angle Harmonics | Analog Input | %
1397 | Phase C 58th Current Angle Harmonics | Phase C 58th Current Angle Harmonics | Analog Input | %
1398 | Phase N 58th Current Angle Harmonics | Phase N 58th Current Angle Harmonics | Analog Input | %
1399 | Phase A 59th Voltage Angle Harmonics | Phase A 59th Voltage Angle Harmonics | Analog Input | %
1400 | Phase B 59th Voltage Angle Harmonics | Phase B 59th Voltage Angle Harmonics | Analog Input | %
1401 | Phase C 59th Voltage Angle Harmonics | Phase C 59th Voltage Angle Harmonics | Analog Input | %
1402 | Phase A 59th Current Angle Harmonics | Phase A 59th Current Angle Harmonics | Analog Input | %
1403 | Phase B 59th Current Angle Harmonics | Phase B 59th Current Angle Harmonics | Analog Input | %
1404 | Phase C 59th Current Angle Harmonics | Phase C 59th Current Angle Harmonics | Analog Input | %
1405 | Phase N 59th Current Angle Harmonics | Phase N 59th Current Angle Harmonics | Analog Input | %
1406 | Phase A 60th Voltage Angle Harmonics | Phase A 60th Voltage Angle Harmonics | Analog Input | %
1407 | Phase B 60th Voltage Angle Harmonics | Phase B 60th Voltage Angle Harmonics | Analog Input | %
1408 | Phase C 60th Voltage Angle Harmonics | Phase C 60th Voltage Angle Harmonics | Analog Input | %
1409 | Phase A 60th Current Angle Harmonics | Phase A 60th Current Angle Harmonics | Analog Input | %
1410 | Phase B 60th Current Angle Harmonics | Phase B 60th Current Angle Harmonics | Analog Input | %
1411 | Phase C 60th Current Angle Harmonics | Phase C 60th Current Angle Harmonics | Analog Input | %
1412 | Phase N 60th Current Angle Harmonics | Phase N 60th Current Angle Harmonics | Analog Input | %
1413 | Phase A 61st Voltage Angle Harmonics | Phase A 61st Voltage Angle Harmonics | Analog Input | %
1414 | Phase B 61st Voltage Angle Harmonics | Phase B 61st Voltage Angle Harmonics | Analog Input | %
1415 | Phase C 61st Voltage Angle Harmonics | Phase C 61st Voltage Angle Harmonics | Analog Input | %
1416 | Phase A 61st Current Angle Harmonics | Phase A 61st Current Angle Harmonics | Analog Input | %
1417 | Phase B 61st Current Angle Harmonics | Phase B 61st Current Angle Harmonics | Analog Input | %
1418 | Phase C 61st Current Angle Harmonics | Phase C 61st Current Angle Harmonics | Analog Input | %
1419 | Phase N 61st Current Angle Harmonics | Phase N 61st Current Angle Harmonics | Analog Input | %
1420 | Phase A 62nd Voltage Angle Harmonics | Phase A 62nd Voltage Angle Harmonics | Analog Input | %
1421 | Phase B 62nd Voltage Angle Harmonics | Phase B 62nd Voltage Angle Harmonics | Analog Input | %
1422 | Phase C 62nd Voltage Angle Harmonics | Phase C 62nd Voltage Angle Harmonics | Analog Input | %
1423 | Phase A 62nd Current Angle Harmonics | Phase A 62nd Current Angle Harmonics | Analog Input | %
1424 | Phase B 62nd Current Angle Harmonics | Phase B 62nd Current Angle Harmonics | Analog Input | %
1425 | Phase C 62nd Current Angle Harmonics | Phase C 62nd Current Angle Harmonics | Analog Input | %
1426 | Phase N 62nd Current Angle Harmonics | Phase N 62nd Current Angle Harmonics | Analog Input | %
1427 | Phase A 63rd Voltage Angle Harmonics | Phase A 63rd Voltage Angle Harmonics | Analog Input | %
1428 | Phase B 63rd Voltage Angle Harmonics | Phase B 63rd Voltage Angle Harmonics | Analog Input | %
1429 | Phase C 63rd Voltage Angle Harmonics | Phase C 63rd Voltage Angle Harmonics | Analog Input | %
1430 | Phase A 63rd Current Angle Harmonics | Phase A 63rd Current Angle Harmonics | Analog Input | %
1431 | Phase B 63rd Current Angle Harmonics | Phase B 63rd Current Angle Harmonics | Analog Input | %
1432 | Phase C 63rd Current Angle Harmonics | Phase C 63rd Current Angle Harmonics | Analog Input | %
1433 | Phase N 63rd Current Angle Harmonics | Phase N 63rd Current Angle Harmonics | Analog Input | %
1434 | Phase A 64th Voltage Angle Harmonics | Phase A 64th Voltage Angle Harmonics | Analog Input | %
1435 | Phase B 64th Voltage Angle Harmonics | Phase B 64th Voltage Angle Harmonics | Analog Input | %
1436 | Phase C 64th Voltage Angle Harmonics | Phase C 64th Voltage Angle Harmonics | Analog Input | %
1437 | Phase A 64th Current Angle Harmonics | Phase A 64th Current Angle Harmonics | Analog Input | %
1438 | Phase B 64th Current Angle Harmonics | Phase B 64th Current Angle Harmonics | Analog Input | %
1439 | Phase C 64th Current Angle Harmonics | Phase C 64th Current Angle Harmonics | Analog Input | %
1440 | Phase N 64th Current Angle Harmonics | Phase N 64th Current Angle Harmonics | Analog Input | %
1441 | Phase A 65th Voltage Angle Harmonics | Phase A 65th Voltage Angle Harmonics | Analog Input | %
1442 | Phase B 65th Voltage Angle Harmonics | Phase B 65th Voltage Angle Harmonics | Analog Input | %
1443 | Phase C 65th Voltage Angle Harmonics | Phase C 65th Voltage Angle Harmonics | Analog Input | %
1444 | Phase A 65th Current Angle Harmonics | Phase A 65th Current Angle Harmonics | Analog Input | %
1445 | Phase B 65th Current Angle Harmonics | Phase B 65th Current Angle Harmonics | Analog Input | %
1446 | Phase C 65th Current Angle Harmonics | Phase C 65th Current Angle Harmonics | Analog Input | %
1447 | Phase N 65th Current Angle Harmonics | Phase N 65th Current Angle Harmonics | Analog Input | %
1448 | Phase A 66th Voltage Angle Harmonics | Phase A 66th Voltage Angle Harmonics | Analog Input | %
1449 | Phase B 66th Voltage Angle Harmonics | Phase B 66th Voltage Angle Harmonics | Analog Input | %
1450 | Phase C 66th Voltage Angle Harmonics | Phase C 66th Voltage Angle Harmonics | Analog Input | %
1451 | Phase A 66th Current Angle Harmonics | Phase A 66th Current Angle Harmonics | Analog Input | %
1452 | Phase B 66th Current Angle Harmonics | Phase B 66th Current Angle Harmonics | Analog Input | %
1453 | Phase C 66th Current Angle Harmonics | Phase C 66th Current Angle Harmonics | Analog Input | %
1454 | Phase N 66th Current Angle Harmonics | Phase N 66th Current Angle Harmonics | Analog Input | %
1455 | Phase A 67th Voltage Angle Harmonics | Phase A 67th Voltage Angle Harmonics | Analog Input | %
1456 | Phase B 67th Voltage Angle Harmonics | Phase B 67th Voltage Angle Harmonics | Analog Input | %
1457 | Phase C 67th Voltage Angle Harmonics | Phase C 67th Voltage Angle Harmonics | Analog Input | %
1458 | Phase A 67th Current Angle Harmonics | Phase A 67th Current Angle Harmonics | Analog Input | %
1459 | Phase B 67th Current Angle Harmonics | Phase B 67th Current Angle Harmonics | Analog Input | %
1460 | Phase C 67th Current Angle Harmonics | Phase C 67th Current Angle Harmonics | Analog Input | %
1461 | Phase N 67th Current Angle Harmonics | Phase N 67th Current Angle Harmonics | Analog Input | %
1462 | Phase A 68th Voltage Angle Harmonics | Phase A 68th Voltage Angle Harmonics | Analog Input | %
1463 | Phase B 68th Voltage Angle Harmonics | Phase B 68th Voltage Angle Harmonics | Analog Input | %
1464 | Phase C 68th Voltage Angle Harmonics | Phase C 68th Voltage Angle Harmonics | Analog Input | %
1465 | Phase A 68th Current Angle Harmonics | Phase A 68th Current Angle Harmonics | Analog Input | %
1466 | Phase B 68th Current Angle Harmonics | Phase B 68th Current Angle Harmonics | Analog Input | %
1467 | Phase C 68th Current Angle Harmonics | Phase C 68th Current Angle Harmonics | Analog Input | %
1468 | Phase N 68th Current Angle Harmonics | Phase N 68th Current Angle Harmonics | Analog Input | %
1469 | Phase A 69th Voltage Angle Harmonics | Phase A 69th Voltage Angle Harmonics | Analog Input | %
1470 | Phase B 69th Voltage Angle Harmonics | Phase B 69th Voltage Angle Harmonics | Analog Input | %
1471 | Phase C 69th Voltage Angle Harmonics | Phase C 69th Voltage Angle Harmonics | Analog Input | %
1472 | Phase A 69th Current Angle Harmonics | Phase A 69th Current Angle Harmonics | Analog Input | %
1473 | Phase B 69th Current Angle Harmonics | Phase B 69th Current Angle Harmonics | Analog Input | %
1474 | Phase C 69th Current Angle Harmonics | Phase C 69th Current Angle Harmonics | Analog Input | %
1475 | Phase N 69th Current Angle Harmonics | Phase N 69th Current Angle Harmonics | Analog Input | %
1476 | Phase A 70th Voltage Angle Harmonics | Phase A 70th Voltage Angle Harmonics | Analog Input | %
1477 | Phase B 70th Voltage Angle Harmonics | Phase B 70th Voltage Angle Harmonics | Analog Input | %
1478 | Phase C 70th Voltage Angle Harmonics | Phase C 70th Voltage Angle Harmonics | Analog Input | %
1479 | Phase A 70th Current Angle Harmonics | Phase A 70th Current Angle Harmonics | Analog Input | %
1480 | Phase B 70th Current Angle Harmonics | Phase B 70th Current Angle Harmonics | Analog Input | %
1481 | Phase C 70th Current Angle Harmonics | Phase C 70th Current Angle Harmonics | Analog Input | %
1482 | Phase N 70th Current Angle Harmonics | Phase N 70th Current Angle Harmonics | Analog Input | %
1483 | Phase A 71st Voltage Angle Harmonics | Phase A 71st Voltage Angle Harmonics | Analog Input | %
1484 | Phase B 71st Voltage Angle Harmonics | Phase B 71st Voltage Angle Harmonics | Analog Input | %
1485 | Phase C 71st Voltage Angle Harmonics | Phase C 71st Voltage Angle Harmonics | Analog Input | %
1486 | Phase A 71st Current Angle Harmonics | Phase A 71st Current Angle Harmonics | Analog Input | %
1487 | Phase B 71st Current Angle Harmonics | Phase B 71st Current Angle Harmonics | Analog Input | %
1488 | Phase C 71st Current Angle Harmonics | Phase C 71st Current Angle Harmonics | Analog Input | %
1489 | Phase N 71st Current Angle Harmonics | Phase N 71st Current Angle Harmonics | Analog Input | %
1490 | Phase A 72nd Voltage Angle Harmonics | Phase A 72nd Voltage Angle Harmonics | Analog Input | %
1491 | Phase B 72nd Voltage Angle Harmonics | Phase B 72nd Voltage Angle Harmonics | Analog Input | %
1492 | Phase C 72nd Voltage Angle Harmonics | Phase C 72nd Voltage Angle Harmonics | Analog Input | %
1493 | Phase A 72nd Current Angle Harmonics | Phase A 72nd Current Angle Harmonics | Analog Input | %
1494 | Phase B 72nd Current Angle Harmonics | Phase B 72nd Current Angle Harmonics | Analog Input | %
1495 | Phase C 72nd Current Angle Harmonics | Phase C 72nd Current Angle Harmonics | Analog Input | %
1496 | Phase N 72nd Current Angle Harmonics | Phase N 72nd Current Angle Harmonics | Analog Input | %
1497 | Phase A 73rd Voltage Angle Harmonics | Phase A 73rd Voltage Angle Harmonics | Analog Input | %
1498 | Phase B 73rd Voltage Angle Harmonics | Phase B 73rd Voltage Angle Harmonics | Analog Input | %
1499 | Phase C 73rd Voltage Angle Harmonics | Phase C 73rd Voltage Angle Harmonics | Analog Input | %
1500 | Phase A 73rd Current Angle Harmonics | Phase A 73rd Current Angle Harmonics | Analog Input | %
1501 | Phase B 73rd Current Angle Harmonics | Phase B 73rd Current Angle Harmonics | Analog Input | %
1502 | Phase C 73rd Current Angle Harmonics | Phase C 73rd Current Angle Harmonics | Analog Input | %
1503 | Phase N 73rd Current Angle Harmonics | Phase N 73rd Current Angle Harmonics | Analog Input | %
1504 | Phase A 74th Voltage Angle Harmonics | Phase A 74th Voltage Angle Harmonics | Analog Input | %
1505 | Phase B 74th Voltage Angle Harmonics | Phase B 74th Voltage Angle Harmonics | Analog Input | %
1506 | Phase C 74th Voltage Angle Harmonics | Phase C 74th Voltage Angle Harmonics | Analog Input | %
1507 | Phase A 74th Current Angle Harmonics | Phase A 74th Current Angle Harmonics | Analog Input | %
1508 | Phase B 74th Current Angle Harmonics | Phase B 74th Current Angle Harmonics | Analog Input | %
1509 | Phase C 74th Current Angle Harmonics | Phase C 74th Current Angle Harmonics | Analog Input | %
1510 | Phase N 74th Current Angle Harmonics | Phase N 74th Current Angle Harmonics | Analog Input | %
1511 | Phase A 75th Voltage Angle Harmonics | Phase A 75th Voltage Angle Harmonics | Analog Input | %
1512 | Phase B 75th Voltage Angle Harmonics | Phase B 75th Voltage Angle Harmonics | Analog Input | %
1513 | Phase C 75th Voltage Angle Harmonics | Phase C 75th Voltage Angle Harmonics | Analog Input | %
1514 | Phase A 75th Current Angle Harmonics | Phase A 75th Current Angle Harmonics | Analog Input | %
1515 | Phase B 75th Current Angle Harmonics | Phase B 75th Current Angle Harmonics | Analog Input | %
1516 | Phase C 75th Current Angle Harmonics | Phase C 75th Current Angle Harmonics | Analog Input | %
1517 | Phase N 75th Current Angle Harmonics | Phase N 75th Current Angle Harmonics | Analog Input | %
1518 | Phase A 76th Voltage Angle Harmonics | Phase A 76th Voltage Angle Harmonics | Analog Input | %
1519 | Phase B 76th Voltage Angle Harmonics | Phase B 76th Voltage Angle Harmonics | Analog Input | %
1520 | Phase C 76th Voltage Angle Harmonics | Phase C 76th Voltage Angle Harmonics | Analog Input | %
1521 | Phase A 76th Current Angle Harmonics | Phase A 76th Current Angle Harmonics | Analog Input | %
1522 | Phase B 76th Current Angle Harmonics | Phase B 76th Current Angle Harmonics | Analog Input | %
1523 | Phase C 76th Current Angle Harmonics | Phase C 76th Current Angle Harmonics | Analog Input | %
1524 | Phase N 76th Current Angle Harmonics | Phase N 76th Current Angle Harmonics | Analog Input | %
1525 | Phase A 77th Voltage Angle Harmonics | Phase A 77th Voltage Angle Harmonics | Analog Input | %
1526 | Phase B 77th Voltage Angle Harmonics | Phase B 77th Voltage Angle Harmonics | Analog Input | %
1527 | Phase C 77th Voltage Angle Harmonics | Phase C 77th Voltage Angle Harmonics | Analog Input | %
1528 | Phase A 77th Current Angle Harmonics | Phase A 77th Current Angle Harmonics | Analog Input | %
1529 | Phase B 77th Current Angle Harmonics | Phase B 77th Current Angle Harmonics | Analog Input | %
1530 | Phase C 77th Current Angle Harmonics | Phase C 77th Current Angle Harmonics | Analog Input | %
1531 | Phase N 77th Current Angle Harmonics | Phase N 77th Current Angle Harmonics | Analog Input | %
1532 | Phase A 78th Voltage Angle Harmonics | Phase A 78th Voltage Angle Harmonics | Analog Input | %
1533 | Phase B 78th Voltage Angle Harmonics | Phase B 78th Voltage Angle Harmonics | Analog Input | %
1534 | Phase C 78th Voltage Angle Harmonics | Phase C 78th Voltage Angle Harmonics | Analog Input | %
1535 | Phase A 78th Current Angle Harmonics | Phase A 78th Current Angle Harmonics | Analog Input | %
1536 | Phase B 78th Current Angle Harmonics | Phase B 78th Current Angle Harmonics | Analog Input | %
1537 | Phase C 78th Current Angle Harmonics | Phase C 78th Current Angle Harmonics | Analog Input | %
1538 | Phase N 78th Current Angle Harmonics | Phase N 78th Current Angle Harmonics | Analog Input | %
1539 | Phase A 79th Voltage Angle Harmonics | Phase A 79th Voltage Angle Harmonics | Analog Input | %
1540 | Phase B 79th Voltage Angle Harmonics | Phase B 79th Voltage Angle Harmonics | Analog Input | %
1541 | Phase C 79th Voltage Angle Harmonics | Phase C 79th Voltage Angle Harmonics | Analog Input | %
1542 | Phase A 79th Current Angle Harmonics | Phase A 79th Current Angle Harmonics | Analog Input | %
1543 | Phase B 79th Current Angle Harmonics | Phase B 79th Current Angle Harmonics | Analog Input | %
1544 | Phase C 79th Current Angle Harmonics | Phase C 79th Current Angle Harmonics | Analog Input | %
1545 | Phase N 79th Current Angle Harmonics | Phase N 79th Current Angle Harmonics | Analog Input | %
1546 | Phase A 80th Voltage Angle Harmonics | Phase A 80th Voltage Angle Harmonics | Analog Input | %
1547 | Phase B 80th Voltage Angle Harmonics | Phase B 80th Voltage Angle Harmonics | Analog Input | %
1548 | Phase C 80th Voltage Angle Harmonics | Phase C 80th Voltage Angle Harmonics | Analog Input | %
1549 | Phase A 80th Current Angle Harmonics | Phase A 80th Current Angle Harmonics | Analog Input | %
1550 | Phase B 80th Current Angle Harmonics | Phase B 80th Current Angle Harmonics | Analog Input | %
1551 | Phase C 80th Current Angle Harmonics | Phase C 80th Current Angle Harmonics | Analog Input | %
1552 | Phase N 80th Current Angle Harmonics | Phase N 80th Current Angle Harmonics | Analog Input | %
1553 | Phase A 81st Voltage Angle Harmonics | Phase A 81st Voltage Angle Harmonics | Analog Input | %
1554 | Phase B 81st Voltage Angle Harmonics | Phase B 81st Voltage Angle Harmonics | Analog Input | %
1555 | Phase C 81st Voltage Angle Harmonics | Phase C 81st Voltage Angle Harmonics | Analog Input | %
1556 | Phase A 81st Current Angle Harmonics | Phase A 81st Current Angle Harmonics | Analog Input | %
1557 | Phase B 81st Current Angle Harmonics | Phase B 81st Current Angle Harmonics | Analog Input | %
1558 | Phase C 81st Current Angle Harmonics | Phase C 81st Current Angle Harmonics | Analog Input | %
1559 | Phase N 81st Current Angle Harmonics | Phase N 81st Current Angle Harmonics | Analog Input | %
1560 | Phase A 82nd Voltage Angle Harmonics | Phase A 82nd Voltage Angle Harmonics | Analog Input | %
1561 | Phase B 82nd Voltage Angle Harmonics | Phase B 82nd Voltage Angle Harmonics | Analog Input | %
1562 | Phase C 82nd Voltage Angle Harmonics | Phase C 82nd Voltage Angle Harmonics | Analog Input | %
1563 | Phase A 82nd Current Angle Harmonics | Phase A 82nd Current Angle Harmonics | Analog Input | %
1564 | Phase B 82nd Current Angle Harmonics | Phase B 82nd Current Angle Harmonics | Analog Input | %
1565 | Phase C 82nd Current Angle Harmonics | Phase C 82nd Current Angle Harmonics | Analog Input | %
1566 | Phase N 82nd Current Angle Harmonics | Phase N 82nd Current Angle Harmonics | Analog Input | %
1567 | Phase A 83rd Voltage Angle Harmonics | Phase A 83rd Voltage Angle Harmonics | Analog Input | %
1568 | Phase B 83rd Voltage Angle Harmonics | Phase B 83rd Voltage Angle Harmonics | Analog Input | %
1569 | Phase C 83rd Voltage Angle Harmonics | Phase C 83rd Voltage Angle Harmonics | Analog Input | %
1570 | Phase A 83rd Current Angle Harmonics | Phase A 83rd Current Angle Harmonics | Analog Input | %
1571 | Phase B 83rd Current Angle Harmonics | Phase B 83rd Current Angle Harmonics | Analog Input | %
1572 | Phase C 83rd Current Angle Harmonics | Phase C 83rd Current Angle Harmonics | Analog Input | %
1573 | Phase N 83rd Current Angle Harmonics | Phase N 83rd Current Angle Harmonics | Analog Input | %
1574 | Phase A 84th Voltage Angle Harmonics | Phase A 84th Voltage Angle Harmonics | Analog Input | %
1575 | Phase B 84th Voltage Angle Harmonics | Phase B 84th Voltage Angle Harmonics | Analog Input | %
1576 | Phase C 84th Voltage Angle Harmonics | Phase C 84th Voltage Angle Harmonics | Analog Input | %
1577 | Phase A 84th Current Angle Harmonics | Phase A 84th Current Angle Harmonics | Analog Input | %
1578 | Phase B 84th Current Angle Harmonics | Phase B 84th Current Angle Harmonics | Analog Input | %
1579 | Phase C 84th Current Angle Harmonics | Phase C 84th Current Angle Harmonics | Analog Input | %
1580 | Phase N 84th Current Angle Harmonics | Phase N 84th Current Angle Harmonics | Analog Input | %
1581 | Phase A 85th Voltage Angle Harmonics | Phase A 85th Voltage Angle Harmonics | Analog Input | %
1582 | Phase B 85th Voltage Angle Harmonics | Phase B 85th Voltage Angle Harmonics | Analog Input | %
1583 | Phase C 85th Voltage Angle Harmonics | Phase C 85th Voltage Angle Harmonics | Analog Input | %
1584 | Phase A 85th Current Angle Harmonics | Phase A 85th Current Angle Harmonics | Analog Input | %
1585 | Phase B 85th Current Angle Harmonics | Phase B 85th Current Angle Harmonics | Analog Input | %
1586 | Phase C 85th Current Angle Harmonics | Phase C 85th Current Angle Harmonics | Analog Input | %
1587 | Phase N 85th Current Angle Harmonics | Phase N 85th Current Angle Harmonics | Analog Input | %
1588 | Phase A 86th Voltage Angle Harmonics | Phase A 86th Voltage Angle Harmonics | Analog Input | %
1589 | Phase B 86th Voltage Angle Harmonics | Phase B 86th Voltage Angle Harmonics | Analog Input | %
1590 | Phase C 86th Voltage Angle Harmonics | Phase C 86th Voltage Angle Harmonics | Analog Input | %
1591 | Phase A 86th Current Angle Harmonics | Phase A 86th Current Angle Harmonics | Analog Input | %
1592 | Phase B 86th Current Angle Harmonics | Phase B 86th Current Angle Harmonics | Analog Input | %
1593 | Phase C 86th Current Angle Harmonics | Phase C 86th Current Angle Harmonics | Analog Input | %
1594 | Phase N 86th Current Angle Harmonics | Phase N 86th Current Angle Harmonics | Analog Input | %
1595 | Phase A 87th Voltage Angle Harmonics | Phase A 87th Voltage Angle Harmonics | Analog Input | %
1596 | Phase B 87th Voltage Angle Harmonics | Phase B 87th Voltage Angle Harmonics | Analog Input | %
1597 | Phase C 87th Voltage Angle Harmonics | Phase C 87th Voltage Angle Harmonics | Analog Input | %
1598 | Phase A 87th Current Angle Harmonics | Phase A 87th Current Angle Harmonics | Analog Input | %
1599 | Phase B 87th Current Angle Harmonics | Phase B 87th Current Angle Harmonics | Analog Input | %
1600 | Phase C 87th Current Angle Harmonics | Phase C 87th Current Angle Harmonics | Analog Input | %
1601 | Phase N 87th Current Angle Harmonics | Phase N 87th Current Angle Harmonics | Analog Input | %
1602 | Phase A 88th Voltage Angle Harmonics | Phase A 88th Voltage Angle Harmonics | Analog Input | %
1603 | Phase B 88th Voltage Angle Harmonics | Phase B 88th Voltage Angle Harmonics | Analog Input | %
1604 | Phase C 88th Voltage Angle Harmonics | Phase C 88th Voltage Angle Harmonics | Analog Input | %
1605 | Phase A 88th Current Angle Harmonics | Phase A 88th Current Angle Harmonics | Analog Input | %
1606 | Phase B 88th Current Angle Harmonics | Phase B 88th Current Angle Harmonics | Analog Input | %
1607 | Phase C 88th Current Angle Harmonics | Phase C 88th Current Angle Harmonics | Analog Input | %
1608 | Phase N 88th Current Angle Harmonics | Phase N 88th Current Angle Harmonics | Analog Input | %
1609 | Phase A 89th Voltage Angle Harmonics | Phase A 89th Voltage Angle Harmonics | Analog Input | %
1610 | Phase B 89th Voltage Angle Harmonics | Phase B 89th Voltage Angle Harmonics | Analog Input | %
1611 | Phase C 89th Voltage Angle Harmonics | Phase C 89th Voltage Angle Harmonics | Analog Input | %
1612 | Phase A 89th Current Angle Harmonics | Phase A 89th Current Angle Harmonics | Analog Input | %
1613 | Phase B 89th Current Angle Harmonics | Phase B 89th Current Angle Harmonics | Analog Input | %
1614 | Phase C 89th Current Angle Harmonics | Phase C 89th Current Angle Harmonics | Analog Input | %
1615 | Phase N 89th Current Angle Harmonics | Phase N 89th Current Angle Harmonics | Analog Input | %
1616 | Phase A 90th Voltage Angle Harmonics | Phase A 90th Voltage Angle Harmonics | Analog Input | %
1617 | Phase B 90th Voltage Angle Harmonics | Phase B 90th Voltage Angle Harmonics | Analog Input | %
1618 | Phase C 90th Voltage Angle Harmonics | Phase C 90th Voltage Angle Harmonics | Analog Input | %
1619 | Phase A 90th Current Angle Harmonics | Phase A 90th Current Angle Harmonics | Analog Input | %
1620 | Phase B 90th Current Angle Harmonics | Phase B 90th Current Angle Harmonics | Analog Input | %
1621 | Phase C 90th Current Angle Harmonics | Phase C 90th Current Angle Harmonics | Analog Input | %
1622 | Phase N 90th Current Angle Harmonics | Phase N 90th Current Angle Harmonics | Analog Input | %
1623 | Phase A 91st Voltage Angle Harmonics | Phase A 91st Voltage Angle Harmonics | Analog Input | %
1624 | Phase B 91st Voltage Angle Harmonics | Phase B 91st Voltage Angle Harmonics | Analog Input | %
1625 | Phase C 91st Voltage Angle Harmonics | Phase C 91st Voltage Angle Harmonics | Analog Input | %
1626 | Phase A 91st Current Angle Harmonics | Phase A 91st Current Angle Harmonics | Analog Input | %
1627 | Phase B 91st Current Angle Harmonics | Phase B 91st Current Angle Harmonics | Analog Input | %
1628 | Phase C 91st Current Angle Harmonics | Phase C 91st Current Angle Harmonics | Analog Input | %
1629 | Phase N 91st Current Angle Harmonics | Phase N 91st Current Angle Harmonics | Analog Input | %
1630 | Phase A 92nd Voltage Angle Harmonics | Phase A 92nd Voltage Angle Harmonics | Analog Input | %
1631 | Phase B 92nd Voltage Angle Harmonics | Phase B 92nd Voltage Angle Harmonics | Analog Input | %
1632 | Phase C 92nd Voltage Angle Harmonics | Phase C 92nd Voltage Angle Harmonics | Analog Input | %
1633 | Phase A 92nd Current Angle Harmonics | Phase A 92nd Current Angle Harmonics | Analog Input | %
1634 | Phase B 92nd Current Angle Harmonics | Phase B 92nd Current Angle Harmonics | Analog Input | %
1635 | Phase C 92nd Current Angle Harmonics | Phase C 92nd Current Angle Harmonics | Analog Input | %
1636 | Phase N 92nd Current Angle Harmonics | Phase N 92nd Current Angle Harmonics | Analog Input | %
1637 | Phase A 93rd Voltage Angle Harmonics | Phase A 93rd Voltage Angle Harmonics | Analog Input | %
1638 | Phase B 93rd Voltage Angle Harmonics | Phase B 93rd Voltage Angle Harmonics | Analog Input | %
1639 | Phase C 93rd Voltage Angle Harmonics | Phase C 93rd Voltage Angle Harmonics | Analog Input | %
1640 | Phase A 93rd Current Angle Harmonics | Phase A 93rd Current Angle Harmonics | Analog Input | %
1641 | Phase B 93rd Current Angle Harmonics | Phase B 93rd Current Angle Harmonics | Analog Input | %
1642 | Phase C 93rd Current Angle Harmonics | Phase C 93rd Current Angle Harmonics | Analog Input | %
1643 | Phase N 93rd Current Angle Harmonics | Phase N 93rd Current Angle Harmonics | Analog Input | %
1644 | Phase A 94th Voltage Angle Harmonics | Phase A 94th Voltage Angle Harmonics | Analog Input | %
1645 | Phase B 94th Voltage Angle Harmonics | Phase B 94th Voltage Angle Harmonics | Analog Input | %
1646 | Phase C 94th Voltage Angle Harmonics | Phase C 94th Voltage Angle Harmonics | Analog Input | %
1647 | Phase A 94th Current Angle Harmonics | Phase A 94th Current Angle Harmonics | Analog Input | %
1648 | Phase B 94th Current Angle Harmonics | Phase B 94th Current Angle Harmonics | Analog Input | %
1649 | Phase C 94th Current Angle Harmonics | Phase C 94th Current Angle Harmonics | Analog Input | %
1650 | Phase N 94th Current Angle Harmonics | Phase N 94th Current Angle Harmonics | Analog Input | %
1651 | Phase A 95th Voltage Angle Harmonics | Phase A 95th Voltage Angle Harmonics | Analog Input | %
1652 | Phase B 95th Voltage Angle Harmonics | Phase B 95th Voltage Angle Harmonics | Analog Input | %
1653 | Phase C 95th Voltage Angle Harmonics | Phase C 95th Voltage Angle Harmonics | Analog Input | %
1654 | Phase A 95th Current Angle Harmonics | Phase A 95th Current Angle Harmonics | Analog Input | %
1655 | Phase B 95th Current Angle Harmonics | Phase B 95th Current Angle Harmonics | Analog Input | %
1656 | Phase C 95th Current Angle Harmonics | Phase C 95th Current Angle Harmonics | Analog Input | %
1657 | Phase N 95th Current Angle Harmonics | Phase N 95th Current Angle Harmonics | Analog Input | %
1658 | Phase A 96th Voltage Angle Harmonics | Phase A 96th Voltage Angle Harmonics | Analog Input | %
1659 | Phase B 96th Voltage Angle Harmonics | Phase B 96th Voltage Angle Harmonics | Analog Input | %
1660 | Phase C 96th Voltage Angle Harmonics | Phase C 96th Voltage Angle Harmonics | Analog Input | %
1661 | Phase A 96th Current Angle Harmonics | Phase A 96th Current Angle Harmonics | Analog Input | %
1662 | Phase B 96th Current Angle Harmonics | Phase B 96th Current Angle Harmonics | Analog Input | %
1663 | Phase C 96th Current Angle Harmonics | Phase C 96th Current Angle Harmonics | Analog Input | %
1664 | Phase N 96th Current Angle Harmonics | Phase N 96th Current Angle Harmonics | Analog Input | %
1665 | Phase A 97th Voltage Angle Harmonics | Phase A 97th Voltage Angle Harmonics | Analog Input | %
1666 | Phase B 97th Voltage Angle Harmonics | Phase B 97th Voltage Angle Harmonics | Analog Input | %
1667 | Phase C 97th Voltage Angle Harmonics | Phase C 97th Voltage Angle Harmonics | Analog Input | %
1668 | Phase A 97th Current Angle Harmonics | Phase A 97th Current Angle Harmonics | Analog Input | %
1669 | Phase B 97th Current Angle Harmonics | Phase B 97th Current Angle Harmonics | Analog Input | %
1670 | Phase C 97th Current Angle Harmonics | Phase C 97th Current Angle Harmonics | Analog Input | %
1671 | Phase N 97th Current Angle Harmonics | Phase N 97th Current Angle Harmonics | Analog Input | %
1672 | Phase A 98th Voltage Angle Harmonics | Phase A 98th Voltage Angle Harmonics | Analog Input | %
1673 | Phase B 98th Voltage Angle Harmonics | Phase B 98th Voltage Angle Harmonics | Analog Input | %
1674 | Phase C 98th Voltage Angle Harmonics | Phase C 98th Voltage Angle Harmonics | Analog Input | %
1675 | Phase A 98th Current Angle Harmonics | Phase A 98th Current Angle Harmonics | Analog Input | %
1676 | Phase B 98th Current Angle Harmonics | Phase B 98th Current Angle Harmonics | Analog Input | %
1677 | Phase C 98th Current Angle Harmonics | Phase C 98th Current Angle Harmonics | Analog Input | %
1678 | Phase N 98th Current Angle Harmonics | Phase N 98th Current Angle Harmonics | Analog Input | %
1679 | Phase A 99th Voltage Angle Harmonics | Phase A 99th Voltage Angle Harmonics | Analog Input | %
1680 | Phase B 99th Voltage Angle Harmonics | Phase B 99th Voltage Angle Harmonics | Analog Input | %
1681 | Phase C 99th Voltage Angle Harmonics | Phase C 99th Voltage Angle Harmonics | Analog Input | %
1682 | Phase A 99th Current Angle Harmonics | Phase A 99th Current Angle Harmonics | Analog Input | %
1683 | Phase B 99th Current Angle Harmonics | Phase B 99th Current Angle Harmonics | Analog Input | %
1684 | Phase C 99th Current Angle Harmonics | Phase C 99th Current Angle Harmonics | Analog Input | %
1685 | Phase N 99th Current Angle Harmonics | Phase N 99th Current Angle Harmonics | Analog Input | %
1686 | Phase A 100th Voltage Angle Harmonics | Phase A 100th Voltage Angle Harmonics | Analog Input | %
1687 | Phase B 100th Voltage Angle Harmonics | Phase B 100th Voltage Angle Harmonics | Analog Input | %
1688 | Phase C 100th Voltage Angle Harmonics | Phase C 100th Voltage Angle Harmonics | Analog Input | %
1689 | Phase A 100th Current Angle Harmonics | Phase A 100th Current Angle Harmonics | Analog Input | %
1690 | Phase B 100th Current Angle Harmonics | Phase B 100th Current Angle Harmonics | Analog Input | %
1691 | Phase C 100th Current Angle Harmonics | Phase C 100th Current Angle Harmonics | Analog Input | %
1692 | Phase N 100th Current Angle Harmonics | Phase N 100th Current Angle Harmonics | Analog Input | %
1693 | Phase A 101st Voltage Angle Harmonics | Phase A 101st Voltage Angle Harmonics | Analog Input | %
1694 | Phase B 101st Voltage Angle Harmonics | Phase B 101st Voltage Angle Harmonics | Analog Input | %
1695 | Phase C 101st Voltage Angle Harmonics | Phase C 101st Voltage Angle Harmonics | Analog Input | %
1696 | Phase A 101st Current Angle Harmonics | Phase A 101st Current Angle Harmonics | Analog Input | %
1697 | Phase B 101st Current Angle Harmonics | Phase B 101st Current Angle Harmonics | Analog Input | %
1698 | Phase C 101st Current Angle Harmonics | Phase C 101st Current Angle Harmonics | Analog Input | %
1699 | Phase N 101st Current Angle Harmonics | Phase N 101st Current Angle Harmonics | Analog Input | %
1700 | Phase A 102nd Voltage Angle Harmonics | Phase A 102nd Voltage Angle Harmonics | Analog Input | %
1701 | Phase B 102nd Voltage Angle Harmonics | Phase B 102nd Voltage Angle Harmonics | Analog Input | %
1702 | Phase C 102nd Voltage Angle Harmonics | Phase C 102nd Voltage Angle Harmonics | Analog Input | %
1703 | Phase A 102nd Current Angle Harmonics | Phase A 102nd Current Angle Harmonics | Analog Input | %
1704 | Phase B 102nd Current Angle Harmonics | Phase B 102nd Current Angle Harmonics | Analog Input | %
1705 | Phase C 102nd Current Angle Harmonics | Phase C 102nd Current Angle Harmonics | Analog Input | %
1706 | Phase N 102nd Current Angle Harmonics | Phase N 102nd Current Angle Harmonics | Analog Input | %
1707 | Phase A 103rd Voltage Angle Harmonics | Phase A 103rd Voltage Angle Harmonics | Analog Input | %
1708 | Phase B 103rd Voltage Angle Harmonics | Phase B 103rd Voltage Angle Harmonics | Analog Input | %
1709 | Phase C 103rd Voltage Angle Harmonics | Phase C 103rd Voltage Angle Harmonics | Analog Input | %
1710 | Phase A 103rd Current Angle Harmonics | Phase A 103rd Current Angle Harmonics | Analog Input | %
1711 | Phase B 103rd Current Angle Harmonics | Phase B 103rd Current Angle Harmonics | Analog Input | %
1712 | Phase C 103rd Current Angle Harmonics | Phase C 103rd Current Angle Harmonics | Analog Input | %
1713 | Phase N 103rd Current Angle Harmonics | Phase N 103rd Current Angle Harmonics | Analog Input | %
1714 | Phase A 104th Voltage Angle Harmonics | Phase A 104th Voltage Angle Harmonics | Analog Input | %
1715 | Phase B 104th Voltage Angle Harmonics | Phase B 104th Voltage Angle Harmonics | Analog Input | %
1716 | Phase C 104th Voltage Angle Harmonics | Phase C 104th Voltage Angle Harmonics | Analog Input | %
1717 | Phase A 104th Current Angle Harmonics | Phase A 104th Current Angle Harmonics | Analog Input | %
1718 | Phase B 104th Current Angle Harmonics | Phase B 104th Current Angle Harmonics | Analog Input | %
1719 | Phase C 104th Current Angle Harmonics | Phase C 104th Current Angle Harmonics | Analog Input | %
1720 | Phase N 104th Current Angle Harmonics | Phase N 104th Current Angle Harmonics | Analog Input | %
1721 | Phase A 105th Voltage Angle Harmonics | Phase A 105th Voltage Angle Harmonics | Analog Input | %
1722 | Phase B 105th Voltage Angle Harmonics | Phase B 105th Voltage Angle Harmonics | Analog Input | %
1723 | Phase C 105th Voltage Angle Harmonics | Phase C 105th Voltage Angle Harmonics | Analog Input | %
1724 | Phase A 105th Current Angle Harmonics | Phase A 105th Current Angle Harmonics | Analog Input | %
1725 | Phase B 105th Current Angle Harmonics | Phase B 105th Current Angle Harmonics | Analog Input | %
1726 | Phase C 105th Current Angle Harmonics | Phase C 105th Current Angle Harmonics | Analog Input | %
1727 | Phase N 105th Current Angle Harmonics | Phase N 105th Current Angle Harmonics | Analog Input | %
1728 | Phase A 106th Voltage Angle Harmonics | Phase A 106th Voltage Angle Harmonics | Analog Input | %
1729 | Phase B 106th Voltage Angle Harmonics | Phase B 106th Voltage Angle Harmonics | Analog Input | %
1730 | Phase C 106th Voltage Angle Harmonics | Phase C 106th Voltage Angle Harmonics | Analog Input | %
1731 | Phase A 106th Current Angle Harmonics | Phase A 106th Current Angle Harmonics | Analog Input | %
1732 | Phase B 106th Current Angle Harmonics | Phase B 106th Current Angle Harmonics | Analog Input | %
1733 | Phase C 106th Current Angle Harmonics | Phase C 106th Current Angle Harmonics | Analog Input | %
1734 | Phase N 106th Current Angle Harmonics | Phase N 106th Current Angle Harmonics | Analog Input | %
1735 | Phase A 107th Voltage Angle Harmonics | Phase A 107th Voltage Angle Harmonics | Analog Input | %
1736 | Phase B 107th Voltage Angle Harmonics | Phase B 107th Voltage Angle Harmonics | Analog Input | %
1737 | Phase C 107th Voltage Angle Harmonics | Phase C 107th Voltage Angle Harmonics | Analog Input | %
1738 | Phase A 107th Current Angle Harmonics | Phase A 107th Current Angle Harmonics | Analog Input | %
1739 | Phase B 107th Current Angle Harmonics | Phase B 107th Current Angle Harmonics | Analog Input | %
1740 | Phase C 107th Current Angle Harmonics | Phase C 107th Current Angle Harmonics | Analog Input | %
1741 | Phase N 107th Current Angle Harmonics | Phase N 107th Current Angle Harmonics | Analog Input | %
1742 | Phase A 108th Voltage Angle Harmonics | Phase A 108th Voltage Angle Harmonics | Analog Input | %
1743 | Phase B 108th Voltage Angle Harmonics | Phase B 108th Voltage Angle Harmonics | Analog Input | %
1744 | Phase C 108th Voltage Angle Harmonics | Phase C 108th Voltage Angle Harmonics | Analog Input | %
1745 | Phase A 108th Current Angle Harmonics | Phase A 108th Current Angle Harmonics | Analog Input | %
1746 | Phase B 108th Current Angle Harmonics | Phase B 108th Current Angle Harmonics | Analog Input | %
1747 | Phase C 108th Current Angle Harmonics | Phase C 108th Current Angle Harmonics | Analog Input | %
1748 | Phase N 108th Current Angle Harmonics | Phase N 108th Current Angle Harmonics | Analog Input | %
1749 | Phase A 109th Voltage Angle Harmonics | Phase A 109th Voltage Angle Harmonics | Analog Input | %
1750 | Phase B 109th Voltage Angle Harmonics | Phase B 109th Voltage Angle Harmonics | Analog Input | %
1751 | Phase C 109th Voltage Angle Harmonics | Phase C 109th Voltage Angle Harmonics | Analog Input | %
1752 | Phase A 109th Current Angle Harmonics | Phase A 109th Current Angle Harmonics | Analog Input | %
1753 | Phase B 109th Current Angle Harmonics | Phase B 109th Current Angle Harmonics | Analog Input | %
1754 | Phase C 109th Current Angle Harmonics | Phase C 109th Current Angle Harmonics | Analog Input | %
1755 | Phase N 109th Current Angle Harmonics | Phase N 109th Current Angle Harmonics | Analog Input | %
1756 | Phase A 110th Voltage Angle Harmonics | Phase A 110th Voltage Angle Harmonics | Analog Input | %
1757 | Phase B 110th Voltage Angle Harmonics | Phase B 110th Voltage Angle Harmonics | Analog Input | %
1758 | Phase C 110th Voltage Angle Harmonics | Phase C 110th Voltage Angle Harmonics | Analog Input | %
1759 | Phase A 110th Current Angle Harmonics | Phase A 110th Current Angle Harmonics | Analog Input | %
1760 | Phase B 110th Current Angle Harmonics | Phase B 110th Current Angle Harmonics | Analog Input | %
1761 | Phase C 110th Current Angle Harmonics | Phase C 110th Current Angle Harmonics | Analog Input | %
1762 | Phase N 110th Current Angle Harmonics | Phase N 110th Current Angle Harmonics | Analog Input | %
1763 | Phase A 111st Voltage Angle Harmonics | Phase A 111st Voltage Angle Harmonics | Analog Input | %
1764 | Phase B 111st Voltage Angle Harmonics | Phase B 111st Voltage Angle Harmonics | Analog Input | %
1765 | Phase C 111st Voltage Angle Harmonics | Phase C 111st Voltage Angle Harmonics | Analog Input | %
1766 | Phase A 111st Current Angle Harmonics | Phase A 111st Current Angle Harmonics | Analog Input | %
1767 | Phase B 111st Current Angle Harmonics | Phase B 111st Current Angle Harmonics | Analog Input | %
1768 | Phase C 111st Current Angle Harmonics | Phase C 111st Current Angle Harmonics | Analog Input | %
1769 | Phase N 111st Current Angle Harmonics | Phase N 111st Current Angle Harmonics | Analog Input | %
1770 | Phase A 112nd Voltage Angle Harmonics | Phase A 112nd Voltage Angle Harmonics | Analog Input | %
1771 | Phase B 112nd Voltage Angle Harmonics | Phase B 112nd Voltage Angle Harmonics | Analog Input | %
1772 | Phase C 112nd Voltage Angle Harmonics | Phase C 112nd Voltage Angle Harmonics | Analog Input | %
1773 | Phase A 112nd Current Angle Harmonics | Phase A 112nd Current Angle Harmonics | Analog Input | %
1774 | Phase B 112nd Current Angle Harmonics | Phase B 112nd Current Angle Harmonics | Analog Input | %
1775 | Phase C 112nd Current Angle Harmonics | Phase C 112nd Current Angle Harmonics | Analog Input | %
1776 | Phase N 112nd Current Angle Harmonics | Phase N 112nd Current Angle Harmonics | Analog Input | %
1777 | Phase A 113rd Voltage Angle Harmonics | Phase A 113rd Voltage Angle Harmonics | Analog Input | %
1778 | Phase B 113rd Voltage Angle Harmonics | Phase B 113rd Voltage Angle Harmonics | Analog Input | %
1779 | Phase C 113rd Voltage Angle Harmonics | Phase C 113rd Voltage Angle Harmonics | Analog Input | %
1780 | Phase A 113rd Current Angle Harmonics | Phase A 113rd Current Angle Harmonics | Analog Input | %
1781 | Phase B 113rd Current Angle Harmonics | Phase B 113rd Current Angle Harmonics | Analog Input | %
1782 | Phase C 113rd Current Angle Harmonics | Phase C 113rd Current Angle Harmonics | Analog Input | %
1783 | Phase N 113rd Current Angle Harmonics | Phase N 113rd Current Angle Harmonics | Analog Input | %
1784 | Phase A 114th Voltage Angle Harmonics | Phase A 114th Voltage Angle Harmonics | Analog Input | %
1785 | Phase B 114th Voltage Angle Harmonics | Phase B 114th Voltage Angle Harmonics | Analog Input | %
1786 | Phase C 114th Voltage Angle Harmonics | Phase C 114th Voltage Angle Harmonics | Analog Input | %
1787 | Phase A 114th Current Angle Harmonics | Phase A 114th Current Angle Harmonics | Analog Input | %
1788 | Phase B 114th Current Angle Harmonics | Phase B 114th Current Angle Harmonics | Analog Input | %
1789 | Phase C 114th Current Angle Harmonics | Phase C 114th Current Angle Harmonics | Analog Input | %
1790 | Phase N 114th Current Angle Harmonics | Phase N 114th Current Angle Harmonics | Analog Input | %
1791 | Phase A 115th Voltage Angle Harmonics | Phase A 115th Voltage Angle Harmonics | Analog Input | %
1792 | Phase B 115th Voltage Angle Harmonics | Phase B 115th Voltage Angle Harmonics | Analog Input | %
1793 | Phase C 115th Voltage Angle Harmonics | Phase C 115th Voltage Angle Harmonics | Analog Input | %
1794 | Phase A 115th Current Angle Harmonics | Phase A 115th Current Angle Harmonics | Analog Input | %
1795 | Phase B 115th Current Angle Harmonics | Phase B 115th Current Angle Harmonics | Analog Input | %
1796 | Phase C 115th Current Angle Harmonics | Phase C 115th Current Angle Harmonics | Analog Input | %
1797 | Phase N 115th Current Angle Harmonics | Phase N 115th Current Angle Harmonics | Analog Input | %
1798 | Phase A 116th Voltage Angle Harmonics | Phase A 116th Voltage Angle Harmonics | Analog Input | %
1799 | Phase B 116th Voltage Angle Harmonics | Phase B 116th Voltage Angle Harmonics | Analog Input | %
1800 | Phase C 116th Voltage Angle Harmonics | Phase C 116th Voltage Angle Harmonics | Analog Input | %
1801 | Phase A 116th Current Angle Harmonics | Phase A 116th Current Angle Harmonics | Analog Input | %
1802 | Phase B 116th Current Angle Harmonics | Phase B 116th Current Angle Harmonics | Analog Input | %
1803 | Phase C 116th Current Angle Harmonics | Phase C 116th Current Angle Harmonics | Analog Input | %
1804 | Phase N 116th Current Angle Harmonics | Phase N 116th Current Angle Harmonics | Analog Input | %
1805 | Phase A 117th Voltage Angle Harmonics | Phase A 117th Voltage Angle Harmonics | Analog Input | %
1806 | Phase B 117th Voltage Angle Harmonics | Phase B 117th Voltage Angle Harmonics | Analog Input | %
1807 | Phase C 117th Voltage Angle Harmonics | Phase C 117th Voltage Angle Harmonics | Analog Input | %
1808 | Phase A 117th Current Angle Harmonics | Phase A 117th Current Angle Harmonics | Analog Input | %
1809 | Phase B 117th Current Angle Harmonics | Phase B 117th Current Angle Harmonics | Analog Input | %
1810 | Phase C 117th Current Angle Harmonics | Phase C 117th Current Angle Harmonics | Analog Input | %
1811 | Phase N 117th Current Angle Harmonics | Phase N 117th Current Angle Harmonics | Analog Input | %
1812 | Phase A 118th Voltage Angle Harmonics | Phase A 118th Voltage Angle Harmonics | Analog Input | %
1813 | Phase B 118th Voltage Angle Harmonics | Phase B 118th Voltage Angle Harmonics | Analog Input | %
1814 | Phase C 118th Voltage Angle Harmonics | Phase C 118th Voltage Angle Harmonics | Analog Input | %
1815 | Phase A 118th Current Angle Harmonics | Phase A 118th Current Angle Harmonics | Analog Input | %
1816 | Phase B 118th Current Angle Harmonics | Phase B 118th Current Angle Harmonics | Analog Input | %
1817 | Phase C 118th Current Angle Harmonics | Phase C 118th Current Angle Harmonics | Analog Input | %
1818 | Phase N 118th Current Angle Harmonics | Phase N 118th Current Angle Harmonics | Analog Input | %
1819 | Phase A 119th Voltage Angle Harmonics | Phase A 119th Voltage Angle Harmonics | Analog Input | %
1820 | Phase B 119th Voltage Angle Harmonics | Phase B 119th Voltage Angle Harmonics | Analog Input | %
1821 | Phase C 119th Voltage Angle Harmonics | Phase C 119th Voltage Angle Harmonics | Analog Input | %
1822 | Phase A 119th Current Angle Harmonics | Phase A 119th Current Angle Harmonics | Analog Input | %
1823 | Phase B 119th Current Angle Harmonics | Phase B 119th Current Angle Harmonics | Analog Input | %
1824 | Phase C 119th Current Angle Harmonics | Phase C 119th Current Angle Harmonics | Analog Input | %
1825 | Phase N 119th Current Angle Harmonics | Phase N 119th Current Angle Harmonics | Analog Input | %
1826 | Phase A 120th Voltage Angle Harmonics | Phase A 120th Voltage Angle Harmonics | Analog Input | %
1827 | Phase B 120th Voltage Angle Harmonics | Phase B 120th Voltage Angle Harmonics | Analog Input | %
1828 | Phase C 120th Voltage Angle Harmonics | Phase C 120th Voltage Angle Harmonics | Analog Input | %
1829 | Phase A 120th Current Angle Harmonics | Phase A 120th Current Angle Harmonics | Analog Input | %
1830 | Phase B 120th Current Angle Harmonics | Phase B 120th Current Angle Harmonics | Analog Input | %
1831 | Phase C 120th Current Angle Harmonics | Phase C 120th Current Angle Harmonics | Analog Input | %
1832 | Phase N 120th Current Angle Harmonics | Phase N 120th Current Angle Harmonics | Analog Input | %
1833 | Phase A 121st Voltage Angle Harmonics | Phase A 121st Voltage Angle Harmonics | Analog Input | %
1834 | Phase B 121st Voltage Angle Harmonics | Phase B 121st Voltage Angle Harmonics | Analog Input | %
1835 | Phase C 121st Voltage Angle Harmonics | Phase C 121st Voltage Angle Harmonics | Analog Input | %
1836 | Phase A 121st Current Angle Harmonics | Phase A 121st Current Angle Harmonics | Analog Input | %
1837 | Phase B 121st Current Angle Harmonics | Phase B 121st Current Angle Harmonics | Analog Input | %
1838 | Phase C 121st Current Angle Harmonics | Phase C 121st Current Angle Harmonics | Analog Input | %
1839 | Phase N 121st Current Angle Harmonics | Phase N 121st Current Angle Harmonics | Analog Input | %
1840 | Phase A 122nd Voltage Angle Harmonics | Phase A 122nd Voltage Angle Harmonics | Analog Input | %
1841 | Phase B 122nd Voltage Angle Harmonics | Phase B 122nd Voltage Angle Harmonics | Analog Input | %
1842 | Phase C 122nd Voltage Angle Harmonics | Phase C 122nd Voltage Angle Harmonics | Analog Input | %
1843 | Phase A 122nd Current Angle Harmonics | Phase A 122nd Current Angle Harmonics | Analog Input | %
1844 | Phase B 122nd Current Angle Harmonics | Phase B 122nd Current Angle Harmonics | Analog Input | %
1845 | Phase C 122nd Current Angle Harmonics | Phase C 122nd Current Angle Harmonics | Analog Input | %
1846 | Phase N 122nd Current Angle Harmonics | Phase N 122nd Current Angle Harmonics | Analog Input | %
1847 | Phase A 123rd Voltage Angle Harmonics | Phase A 123rd Voltage Angle Harmonics | Analog Input | %
1848 | Phase B 123rd Voltage Angle Harmonics | Phase B 123rd Voltage Angle Harmonics | Analog Input | %
1849 | Phase C 123rd Voltage Angle Harmonics | Phase C 123rd Voltage Angle Harmonics | Analog Input | %
1850 | Phase A 123rd Current Angle Harmonics | Phase A 123rd Current Angle Harmonics | Analog Input | %
1851 | Phase B 123rd Current Angle Harmonics | Phase B 123rd Current Angle Harmonics | Analog Input | %
1852 | Phase C 123rd Current Angle Harmonics | Phase C 123rd Current Angle Harmonics | Analog Input | %
1853 | Phase N 123rd Current Angle Harmonics | Phase N 123rd Current Angle Harmonics | Analog Input | %
1854 | Phase A 124th Voltage Angle Harmonics | Phase A 124th Voltage Angle Harmonics | Analog Input | %
1855 | Phase B 124th Voltage Angle Harmonics | Phase B 124th Voltage Angle Harmonics | Analog Input | %
1856 | Phase C 124th Voltage Angle Harmonics | Phase C 124th Voltage Angle Harmonics | Analog Input | %
1857 | Phase A 124th Current Angle Harmonics | Phase A 124th Current Angle Harmonics | Analog Input | %
1858 | Phase B 124th Current Angle Harmonics | Phase B 124th Current Angle Harmonics | Analog Input | %
1859 | Phase C 124th Current Angle Harmonics | Phase C 124th Current Angle Harmonics | Analog Input | %
1860 | Phase N 124th Current Angle Harmonics | Phase N 124th Current Angle Harmonics | Analog Input | %
1861 | Phase A 125th Voltage Angle Harmonics | Phase A 125th Voltage Angle Harmonics | Analog Input | %
1862 | Phase B 125th Voltage Angle Harmonics | Phase B 125th Voltage Angle Harmonics | Analog Input | %
1863 | Phase C 125th Voltage Angle Harmonics | Phase C 125th Voltage Angle Harmonics | Analog Input | %
1864 | Phase A 125th Current Angle Harmonics | Phase A 125th Current Angle Harmonics | Analog Input | %
1865 | Phase B 125th Current Angle Harmonics | Phase B 125th Current Angle Harmonics | Analog Input | %
1866 | Phase C 125th Current Angle Harmonics | Phase C 125th Current Angle Harmonics | Analog Input | %
1867 | Phase N 125th Current Angle Harmonics | Phase N 125th Current Angle Harmonics | Analog Input | %
1868 | Phase A 126th Voltage Angle Harmonics | Phase A 126th Voltage Angle Harmonics | Analog Input | %
1869 | Phase B 126th Voltage Angle Harmonics | Phase B 126th Voltage Angle Harmonics | Analog Input | %
1870 | Phase C 126th Voltage Angle Harmonics | Phase C 126th Voltage Angle Harmonics | Analog Input | %
1871 | Phase A 126th Current Angle Harmonics | Phase A 126th Current Angle Harmonics | Analog Input | %
1872 | Phase B 126th Current Angle Harmonics | Phase B 126th Current Angle Harmonics | Analog Input | %
1873 | Phase C 126th Current Angle Harmonics | Phase C 126th Current Angle Harmonics | Analog Input | %
1874 | Phase N 126th Current Angle Harmonics | Phase N 126th Current Angle Harmonics | Analog Input | %
1875 | Phase A 127th Voltage Angle Harmonics | Phase A 127th Voltage Angle Harmonics | Analog Input | %
1876 | Phase B 127th Voltage Angle Harmonics | Phase B 127th Voltage Angle Harmonics | Analog Input | %
1877 | Phase C 127th Voltage Angle Harmonics | Phase C 127th Voltage Angle Harmonics | Analog Input | %
1878 | Phase A 127th Current Angle Harmonics | Phase A 127th Current Angle Harmonics | Analog Input | %
1879 | Phase B 127th Current Angle Harmonics | Phase B 127th Current Angle Harmonics | Analog Input | %
1880 | Phase C 127th Current Angle Harmonics | Phase C 127th Current Angle Harmonics | Analog Input | %
1881 | Phase N 127th Current Angle Harmonics | Phase N 127th Current Angle Harmonics | Analog Input | %
Voltage Flicker
1882 | Aggr 10min Phase A Voltage Flicker | Aggr 10min Phase A Voltage Flicker | Analog Input | no units
1883 | Aggr 10min Phase B Voltage Flicker | Aggr 10min Phase B Voltage Flicker | Analog Input | no units
1884 | Aggr 10min Phase C Voltage Flicker | Aggr 10min Phase C Voltage Flicker | Analog Input | no units
1885 | Aggr 2hr Phase A Voltage Flicker | Aggr 2hr Phase A Voltage Flicker | Analog Input | no units
1886 | Aggr 2hr Phase B Voltage Flicker | Aggr 2hr Phase B Voltage Flicker | Analog Input | no units
1887 | Aggr 2hr Phase C Voltage Flicker | Aggr 2hr Phase C Voltage Flicker | Analog Input | no units
Real-Time Parameters (200 ms RMS) - Displacement Power Factor etc.
1888 | Phase A Fundamental Line-to-Neutral Voltage | Phase A Fundamental Line-to-Neutral Voltage | Analog Input | V
1889 | Phase B Fundamental Line-to-Neutral Voltage | Phase B Fundamental Line-to-Neutral Voltage | Analog Input | V
1890 | Phase C Fundamental Line-to-Neutral Voltage | Phase C Fundamental Line-to-Neutral Voltage | Analog Input | V
1891 | Average Fundamental Line-to-Neutral Voltage | Average Fundamental Line-to-Neutral Voltage | Analog Input | V
1892 | Phase AB Fundamental Line-to-Line Voltage | Phase AB Fundamental Line-to-Line Voltage | Analog Input | V
1893 | Phase BC Fundamental Line-to-Line Voltage | Phase BC Fundamental Line-to-Line Voltage | Analog Input | V
1894 | Phase CA Fundamental Line-to-Line Voltage | Phase CA Fundamental Line-to-Line Voltage | Analog Input | V
1895 | Average Fundamental Line-to-Line Voltage | Average Fundamental Line-to-Line Voltage | Analog Input | V
1896 | Phase A Fundamental Line Current | Phase A Fundamental Line Current | Analog Input | A
1897 | Phase B Fundamental Line Current | Phase B Fundamental Line Current | Analog Input | A
1898 | Phase C Fundamental Line Current | Phase C Fundamental Line Current | Analog Input | A
1899 | Phase N Fundamental Line Current | Phase N Fundamental Line Current | Analog Input | A
1900 | Average Fundamental Line Current | Average Fundamental Line Current | Analog Input | A
1901 | Phase A Fundamental Active Power | Phase A Fundamental Active Power | Analog Input | kW
1902 | Phase B Fundamental Active Power | Phase B Fundamental Active Power | Analog Input | kW
1903 | Phase C Fundamental Active Power | Phase C Fundamental Active Power | Analog Input | kW
1904 | System Fundamental Active Power | System Fundamental Active Power | Analog Input | kW
1905 | Phase A Fundamental Reactive Power | Phase A Fundamental Reactive Power | Analog Input | kvar
1906 | Phase B Fundamental Reactive Power | Phase B Fundamental Reactive Power | Analog Input | kvar
1907 | Phase C Fundamental Reactive Power | Phase C Fundamental Reactive Power | Analog Input | kvar
1908 | System Fundamental Reactive Power | System Fundamental Reactive Power | Analog Input | kvar
1909 | Phase A Fundamental Apparent Power | Phase A Fundamental Apparent Power | Analog Input | kVA
1910 | Phase B Fundamental Apparent Power | Phase B Fundamental Apparent Power | Analog Input | kVA
1911 | Phase C Fundamental Apparent Power | Phase C Fundamental Apparent Power | Analog Input | kVA
1912 | System Fundamental Apparent Power | System Fundamental Apparent Power | Analog Input | kVA
1913 | Phase A Displacement Power Factor | Phase A Displacement Power Factor | Analog Input | PF
1914 | Phase B Displacement Power Factor | Phase B Displacement Power Factor | Analog Input | PF
1915 | Phase C Displacement Power Factor | Phase C Displacement Power Factor | Analog Input | PF
1916 | System Displacement Power Factor | System Displacement Power Factor | Analog Input | PF
Demand Parameters
1917 | Phase A Current Demand | Phase A Current Demand | Analog Input | A
1918 | Phase B Current Demand | Phase B Current Demand | Analog Input | A
1919 | Phase C Current Demand | Phase C Current Demand | Analog Input | A
1920 | Average Current Demand | Average Current Demand | Analog Input | A
1921 | Phase A Active Power Demand-Quad 1 | Phase A Active Power Demand-Quad 1 | Analog Input | kW
1922 | Phase B Active Power Demand-Quad 1 | Phase B Active Power Demand-Quad 1 | Analog Input | kW
1923 | Phase C Active Power Demand-Quad 1 | Phase C Active Power Demand-Quad 1 | Analog Input | kW
1924 | System Active Power Demand-Quad 1 | System Active Power Demand-Quad 1 | Analog Input | kW
1925 | Phase A Reactive Power Demand-Quad 1 | Phase A Reactive Power Demand-Quad 1 | Analog Input | kvar
1926 | Phase B Reactive Power Demand-Quad 1 | Phase B Reactive Power Demand-Quad 1 | Analog Input | kvar
1927 | Phase C Reactive Power Demand-Quad 1 | Phase C Reactive Power Demand-Quad 1 | Analog Input | kvar
1928 | System Reactive Power Demand-Quad 1 | System Reactive Power Demand-Quad 1 | Analog Input | kvar
1929 | Phase A Apparent Power Demand-Quad 1 | Phase A Apparent Power Demand-Quad 1 | Analog Input | kVA
1930 | Phase B Apparent Power Demand-Quad 1 | Phase B Apparent Power Demand-Quad 1 | Analog Input | kVA
1931 | Phase C Apparent Power Demand-Quad 1 | Phase C Apparent Power Demand-Quad 1 | Analog Input | kVA
1932 | System Apparent Power Demand-Quad 1 | System Apparent Power Demand-Quad 1 | Analog Input | kVA
1933 | Phase A Active Power Demand-Quad 2 | Phase A Active Power Demand-Quad 2 | Analog Input | kW
1934 | Phase B Active Power Demand-Quad 2 | Phase B Active Power Demand-Quad 2 | Analog Input | kW
1935 | Phase C Active Power Demand-Quad 2 | Phase C Active Power Demand-Quad 2 | Analog Input | kW
1936 | System Active Power Demand-Quad 2 | System Active Power Demand-Quad 2 | Analog Input | kW
1937 | Phase A Reactive Power Demand-Quad 2 | Phase A Reactive Power Demand-Quad 2 | Analog Input | kvar
1938 | Phase B Reactive Power Demand-Quad 2 | Phase B Reactive Power Demand-Quad 2 | Analog Input | kvar
1939 | Phase C Reactive Power Demand-Quad 2 | Phase C Reactive Power Demand-Quad 2 | Analog Input | kvar
1940 | System Reactive Power Demand-Quad 2 | System Reactive Power Demand-Quad 2 | Analog Input | kvar
1941 | Phase A Apparent Power Demand-Quad 2 | Phase A Apparent Power Demand-Quad 2 | Analog Input | kVA
1942 | Phase B Apparent Power Demand-Quad 2 | Phase B Apparent Power Demand-Quad 2 | Analog Input | kVA
1943 | Phase C Apparent Power Demand-Quad 2 | Phase C Apparent Power Demand-Quad 2 | Analog Input | kVA
1944 | System Apparent Power Demand-Quad 2 | System Apparent Power Demand-Quad 2 | Analog Input | kVA
1945 | Phase A Active Power Demand-Quad 3 | Phase A Active Power Demand-Quad 3 | Analog Input | kW
1946 | Phase B Active Power Demand-Quad 3 | Phase B Active Power Demand-Quad 3 | Analog Input | kW
1947 | Phase C Active Power Demand-Quad 3 | Phase C Active Power Demand-Quad 3 | Analog Input | kW
1948 | System Active Power Demand-Quad 3 | System Active Power Demand-Quad 3 | Analog Input | kW
1949 | Phase A Reactive Power Demand-Quad 3 | Phase A Reactive Power Demand-Quad 3 | Analog Input | kvar
1950 | Phase B Reactive Power Demand-Quad 3 | Phase B Reactive Power Demand-Quad 3 | Analog Input | kvar
1951 | Phase C Reactive Power Demand-Quad 3 | Phase C Reactive Power Demand-Quad 3 | Analog Input | kvar
1952 | System Reactive Power Demand-Quad 3 | System Reactive Power Demand-Quad 3 | Analog Input | kvar
1953 | Phase A Apparent Power Demand-Quad 3 | Phase A Apparent Power Demand-Quad 3 | Analog Input | kVA
1954 | Phase B Apparent Power Demand-Quad 3 | Phase B Apparent Power Demand-Quad 3 | Analog Input | kVA
1955 | Phase C Apparent Power Demand-Quad 3 | Phase C Apparent Power Demand-Quad 3 | Analog Input | kVA
1956 | System Apparent Power Demand-Quad 3 | System Apparent Power Demand-Quad 3 | Analog Input | kVA
1957 | Phase A Active Power Demand-Quad 4 | Phase A Active Power Demand-Quad 4 | Analog Input | kW
1958 | Phase B Active Power Demand-Quad 4 | Phase B Active Power Demand-Quad 4 | Analog Input | kW
1959 | Phase C Active Power Demand-Quad 4 | Phase C Active Power Demand-Quad 4 | Analog Input | kW
1960 | System Active Power Demand-Quad 4 | System Active Power Demand-Quad 4 | Analog Input | kW
1961 | Phase A Reactive Power Demand-Quad 4 | Phase A Reactive Power Demand-Quad 4 | Analog Input | kvar
1962 | Phase B Reactive Power Demand-Quad 4 | Phase B Reactive Power Demand-Quad 4 | Analog Input | kvar
1963 | Phase C Reactive Power Demand-Quad 4 | Phase C Reactive Power Demand-Quad 4 | Analog Input | kvar
1964 | System Reactive Power Demand-Quad 4 | System Reactive Power Demand-Quad 4 | Analog Input | kvar
1965 | Phase A Apparent Power Demand-Quad 4 | Phase A Apparent Power Demand-Quad 4 | Analog Input | kVA
1966 | Phase B Apparent Power Demand-Quad 4 | Phase B Apparent Power Demand-Quad 4 | Analog Input | kVA
1967 | Phase C Apparent Power Demand-Quad 4 | Phase C Apparent Power Demand-Quad 4 | Analog Input | kVA
1968 | System Apparent Power Demand-Quad 4 | System Apparent Power Demand-Quad 4 | Analog Input | kVA
1969 | Phase A Active Power Demand-Import | Phase A Active Power Demand-Import | Analog Input | kW
1970 | Phase B Active Power Demand-Import | Phase B Active Power Demand-Import | Analog Input | kW
1971 | Phase C Active Power Demand-Import | Phase C Active Power Demand-Import | Analog Input | kW
1972 | System Active Power Demand-Import | System Active Power Demand-Import | Analog Input | kW
1973 | Phase A Reactive Power Demand-Import | Phase A Reactive Power Demand-Import | Analog Input | kvar
1974 | Phase B Reactive Power Demand-Import | Phase B Reactive Power Demand-Import | Analog Input | kvar
1975 | Phase C Reactive Power Demand-Import | Phase C Reactive Power Demand-Import | Analog Input | kvar
1976 | System Reactive Power Demand-Import | System Reactive Power Demand-Import | Analog Input | kvar
1977 | Phase A Active Power Demand-Export | Phase A Active Power Demand-Export | Analog Input | kW
1978 | Phase B Active Power Demand-Export | Phase B Active Power Demand-Export | Analog Input | kW
1979 | Phase C Active Power Demand-Export | Phase C Active Power Demand-Export | Analog Input | kW
1980 | System Active Power Demand-Export | System Active Power Demand-Export | Analog Input | kW
1981 | Phase A Reactive Power Demand-Export | Phase A Reactive Power Demand-Export | Analog Input | kvar
1982 | Phase B Reactive Power Demand-Export | Phase B Reactive Power Demand-Export | Analog Input | kvar
1983 | Phase C Reactive Power Demand-Export | Phase C Reactive Power Demand-Export | Analog Input | kvar
1984 | System Reactive Power Demand-Export | System Reactive Power Demand-Export | Analog Input | kvar
1985 | Phase A Active Power Demand-Net | Phase A Active Power Demand-Net | Analog Input | kW
1986 | Phase B Active Power Demand-Net | Phase B Active Power Demand-Net | Analog Input | kW
1987 | Phase C Active Power Demand-Net | Phase C Active Power Demand-Net | Analog Input | kW
1988 | System Active Power Demand-Net | System Active Power Demand-Net | Analog Input | kW
1989 | Phase A Reactive Power Demand-Net | Phase A Reactive Power Demand-Net | Analog Input | kvar
1990 | Phase B Reactive Power Demand-Net | Phase B Reactive Power Demand-Net | Analog Input | kvar
1991 | Phase C Reactive Power Demand-Net | Phase C Reactive Power Demand-Net | Analog Input | kvar
1992 | System Reactive Power Demand-Net | System Reactive Power Demand-Net | Analog Input | kvar
1993 | Phase A Active Power Demand-Total | Phase A Active Power Demand-Total | Analog Input | kW
1994 | Phase B Active Power Demand-Total | Phase B Active Power Demand-Total | Analog Input | kW
1995 | Phase C Active Power Demand-Total | Phase C Active Power Demand-Total | Analog Input | kW
1996 | System Active Power Demand-Total | System Active Power Demand-Total | Analog Input | kW
1997 | Phase A Reactive Power Demand-Total | Phase A Reactive Power Demand-Total | Analog Input | kvar
1998 | Phase B Reactive Power Demand-Total | Phase B Reactive Power Demand-Total | Analog Input | kvar
1999 | Phase C Reactive Power Demand-Total | Phase C Reactive Power Demand-Total | Analog Input | kvar
2000 | System Reactive Power Demand-Total | System Reactive Power Demand-Total | Analog Input | kvar
2001 | Phase A Apparent Power Demand | Phase A Apparent Power Demand | Analog Input | kVA
2002 | Phase B Apparent Power Demand | Phase B Apparent Power Demand | Analog Input | kVA
2003 | Phase C Apparent Power Demand | Phase C Apparent Power Demand | Analog Input | kVA
2004 | System Apparent Power Demand | System Apparent Power Demand | Analog Input | kVA
Energy Parameters (Accumulative)
2005 | Accumulative Phase A Active Energy-Quad 1 | Accumulative Phase A Active Energy-Quad 1 | Analog Input | kWh
2006 | Accumulative Phase B Active Energy-Quad 1 | Accumulative Phase B Active Energy-Quad 1 | Analog Input | kWh
2007 | Accumulative Phase C Active Energy-Quad 1 | Accumulative Phase C Active Energy-Quad 1 | Analog Input | kWh
2008 | Accumulative System Active Energy-Quad 1 | Accumulative System Active Energy-Quad 1 | Analog Input | kWh
2009 | Accumulative Phase A Reactive Energy-Quad 1 | Accumulative Phase A Reactive Energy-Quad 1 | Analog Input | kvarh
2010 | Accumulative Phase B Reactive Energy-Quad 1 | Accumulative Phase B Reactive Energy-Quad 1 | Analog Input | kvarh
2011 | Accumulative Phase C Reactive Energy-Quad 1 | Accumulative Phase C Reactive Energy-Quad 1 | Analog Input | kvarh
2012 | Accumulative System Reactive Energy-Quad 1 | Accumulative System Reactive Energy-Quad 1 | Analog Input | kvarh
2013 | Accumulative Phase A Apparent Energy-Quad 1 | Accumulative Phase A Apparent Energy-Quad 1 | Analog Input | kVAh
2014 | Accumulative Phase B Apparent Energy-Quad 1 | Accumulative Phase B Apparent Energy-Quad 1 | Analog Input | kVAh
2015 | Accumulative Phase C Apparent Energy-Quad 1 | Accumulative Phase C Apparent Energy-Quad 1 | Analog Input | kVAh
2016 | Accumulative System Apparent Energy-Quad 1 | Accumulative System Apparent Energy-Quad 1 | Analog Input | kVAh
2017 | Accumulative Phase A Active Energy-Quad 2 | Accumulative Phase A Active Energy-Quad 2 | Analog Input | kWh
2018 | Accumulative Phase B Active Energy-Quad 2 | Accumulative Phase B Active Energy-Quad 2 | Analog Input | kWh
2019 | Accumulative Phase C Active Energy-Quad 2 | Accumulative Phase C Active Energy-Quad 2 | Analog Input | kWh
2020 | Accumulative System Active Energy-Quad 2 | Accumulative System Active Energy-Quad 2 | Analog Input | kWh
2021 | Accumulative Phase A Reactive Energy-Quad 2 | Accumulative Phase A Reactive Energy-Quad 2 | Analog Input | kvarh
2022 | Accumulative Phase B Reactive Energy-Quad 2 | Accumulative Phase B Reactive Energy-Quad 2 | Analog Input | kvarh
2023 | Accumulative Phase C Reactive Energy-Quad 2 | Accumulative Phase C Reactive Energy-Quad 2 | Analog Input | kvarh
2024 | Accumulative System Reactive Energy-Quad 2 | Accumulative System Reactive Energy-Quad 2 | Analog Input | kvarh
2025 | Accumulative Phase A Apparent Energy-Quad 2 | Accumulative Phase A Apparent Energy-Quad 2 | Analog Input | kVAh
2026 | Accumulative Phase B Apparent Energy-Quad 2 | Accumulative Phase B Apparent Energy-Quad 2 | Analog Input | kVAh
2027 | Accumulative Phase C Apparent Energy-Quad 2 | Accumulative Phase C Apparent Energy-Quad 2 | Analog Input | kVAh
2028 | Accumulative System Apparent Energy-Quad 2 | Accumulative System Apparent Energy-Quad 2 | Analog Input | kVAh
2029 | Accumulative Phase A Active Energy-Quad 3 | Accumulative Phase A Active Energy-Quad 3 | Analog Input | kWh
2030 | Accumulative Phase B Active Energy-Quad 3 | Accumulative Phase B Active Energy-Quad 3 | Analog Input | kWh
2031 | Accumulative Phase C Active Energy-Quad 3 | Accumulative Phase C Active Energy-Quad 3 | Analog Input | kWh
2032 | Accumulative System Active Energy-Quad 3 | Accumulative System Active Energy-Quad 3 | Analog Input | kWh
2033 | Accumulative Phase A Reactive Energy-Quad 3 | Accumulative Phase A Reactive Energy-Quad 3 | Analog Input | kvarh
2034 | Accumulative Phase B Reactive Energy-Quad 3 | Accumulative Phase B Reactive Energy-Quad 3 | Analog Input | kvarh
2035 | Accumulative Phase C Reactive Energy-Quad 3 | Accumulative Phase C Reactive Energy-Quad 3 | Analog Input | kvarh
2036 | Accumulative System Reactive Energy-Quad 3 | Accumulative System Reactive Energy-Quad 3 | Analog Input | kvarh
2037 | Accumulative Phase A Apparent Energy-Quad 3 | Accumulative Phase A Apparent Energy-Quad 3 | Analog Input | kVAh
2038 | Accumulative Phase B Apparent Energy-Quad 3 | Accumulative Phase B Apparent Energy-Quad 3 | Analog Input | kVAh
2039 | Accumulative Phase C Apparent Energy-Quad 3 | Accumulative Phase C Apparent Energy-Quad 3 | Analog Input | kVAh
2040 | Accumulative System Apparent Energy-Quad 3 | Accumulative System Apparent Energy-Quad 3 | Analog Input | kVAh
2041 | Accumulative Phase A Active Energy-Quad 4 | Accumulative Phase A Active Energy-Quad 4 | Analog Input | kWh
2042 | Accumulative Phase B Active Energy-Quad 4 | Accumulative Phase B Active Energy-Quad 4 | Analog Input | kWh
2043 | Accumulative Phase C Active Energy-Quad 4 | Accumulative Phase C Active Energy-Quad 4 | Analog Input | kWh
2044 | Accumulative System Active Energy-Quad 4 | Accumulative System Active Energy-Quad 4 | Analog Input | kWh
2045 | Accumulative Phase A Reactive Energy-Quad 4 | Accumulative Phase A Reactive Energy-Quad 4 | Analog Input | kvarh
2046 | Accumulative Phase B Reactive Energy-Quad 4 | Accumulative Phase B Reactive Energy-Quad 4 | Analog Input | kvarh
2047 | Accumulative Phase C Reactive Energy-Quad 4 | Accumulative Phase C Reactive Energy-Quad 4 | Analog Input | kvarh
2048 | Accumulative System Reactive Energy-Quad 4 | Accumulative System Reactive Energy-Quad 4 | Analog Input | kvarh
2049 | Accumulative Phase A Apparent Energy-Quad 4 | Accumulative Phase A Apparent Energy-Quad 4 | Analog Input | kVAh
2050 | Accumulative Phase B Apparent Energy-Quad 4 | Accumulative Phase B Apparent Energy-Quad 4 | Analog Input | kVAh
2051 | Accumulative Phase C Apparent Energy-Quad 4 | Accumulative Phase C Apparent Energy-Quad 4 | Analog Input | kVAh
2052 | Accumulative System Apparent Energy-Quad 4 | Accumulative System Apparent Energy-Quad 4 | Analog Input | kVAh
2053 | Accumulative Phase A Active Energy-Import | Accumulative Phase A Active Energy-Import | Analog Input | kWh
2054 | Accumulative Phase B Active Energy-Import | Accumulative Phase B Active Energy-Import | Analog Input | kWh
2055 | Accumulative Phase C Active Energy-Import | Accumulative Phase C Active Energy-Import | Analog Input | kWh
2056 | Accumulative System Active Energy-Import | Accumulative System Active Energy-Import | Analog Input | kWh
2057 | Accumulative Phase A Reactive Energy-Import | Accumulative Phase A Reactive Energy-Import | Analog Input | kvarh
2058 | Accumulative Phase B Reactive Energy-Import | Accumulative Phase B Reactive Energy-Import | Analog Input | kvarh
2059 | Accumulative Phase C Reactive Energy-Import | Accumulative Phase C Reactive Energy-Import | Analog Input | kvarh
2060 | Accumulative System Reactive Energy-Import | Accumulative System Reactive Energy-Import | Analog Input | kvarh
2061 | Accumulative Phase A Active Energy-Export | Accumulative Phase A Active Energy-Export | Analog Input | kWh
2062 | Accumulative Phase B Active Energy-Export | Accumulative Phase B Active Energy-Export | Analog Input | kWh
2063 | Accumulative Phase C Active Energy-Export | Accumulative Phase C Active Energy-Export | Analog Input | kWh
2064 | Accumulative System Active Energy-Export | Accumulative System Active Energy-Export | Analog Input | kWh
2065 | Accumulative Phase A Reactive Energy-Export | Accumulative Phase A Reactive Energy-Export | Analog Input | kvarh
2066 | Accumulative Phase B Reactive Energy-Export | Accumulative Phase B Reactive Energy-Export | Analog Input | kvarh
2067 | Accumulative Phase C Reactive Energy-Export | Accumulative Phase C Reactive Energy-Export | Analog Input | kvarh
2068 | Accumulative System Reactive Energy-Export | Accumulative System Reactive Energy-Export | Analog Input | kvarh
2069 | Accumulative Phase A Active Energy-Net | Accumulative Phase A Active Energy-Net | Analog Input | kWh
2070 | Accumulative Phase B Active Energy-Net | Accumulative Phase B Active Energy-Net | Analog Input | kWh
2071 | Accumulative Phase C Active Energy-Net | Accumulative Phase C Active Energy-Net | Analog Input | kWh
2072 | Accumulative System Active Energy-Net | Accumulative System Active Energy-Net | Analog Input | kWh
2073 | Accumulative Phase A Reactive Energy-Net | Accumulative Phase A Reactive Energy-Net | Analog Input | kvarh
2074 | Accumulative Phase B Reactive Energy-Net | Accumulative Phase B Reactive Energy-Net | Analog Input | kvarh
2075 | Accumulative Phase C Reactive Energy-Net | Accumulative Phase C Reactive Energy-Net | Analog Input | kvarh
2076 | Accumulative System Reactive Energy-Net | Accumulative System Reactive Energy-Net | Analog Input | kvarh
2077 | Accumulative Phase A Active Energy-Total | Accumulative Phase A Active Energy-Total | Analog Input | kWh
2078 | Accumulative Phase B Active Energy-Total | Accumulative Phase B Active Energy-Total | Analog Input | kWh
2079 | Accumulative Phase C Active Energy-Total | Accumulative Phase C Active Energy-Total | Analog Input | kWh
2080 | Accumulative System Active Energy-Total | Accumulative System Active Energy-Total | Analog Input | kWh
2081 | Accumulative Phase A Reactive Energy-Total | Accumulative Phase A Reactive Energy-Total | Analog Input | kvarh
2082 | Accumulative Phase B Reactive Energy-Total | Accumulative Phase B Reactive Energy-Total | Analog Input | kvarh
2083 | Accumulative Phase C Reactive Energy-Total | Accumulative Phase C Reactive Energy-Total | Analog Input | kvarh
2084 | Accumulative System Reactive Energy-Total | Accumulative System Reactive Energy-Total | Analog Input | kvarh
2085 | Accumulative Phase A Apparent Energy | Accumulative Phase A Apparent Energy | Analog Input | kVAh
2086 | Accumulative Phase B Apparent Energy | Accumulative Phase B Apparent Energy | Analog Input | kVAh
2087 | Accumulative Phase C Apparent Energy | Accumulative Phase C Apparent Energy | Analog Input | kVAh
2088 | Accumulative System Apparent Energy | Accumulative System Apparent Energy | Analog Input | kVAh
I/O Module - Digital Input Counters
2089 | IO01 DI COUNTER 1 | IO01 DI COUNTER 1 | Analog Input | no units
2090 | IO01 DI COUNTER 2 | IO01 DI COUNTER 2 | Analog Input | no units
2091 | IO01 DI COUNTER 3 | IO01 DI COUNTER 3 | Analog Input | no units
2092 | IO01 DI COUNTER 4 | IO01 DI COUNTER 4 | Analog Input | no units
2093 | IO11 DI COUNTER 1 | IO11 DI COUNTER 1 | Analog Input | no units
2094 | IO11 DI COUNTER 2 | IO11 DI COUNTER 2 | Analog Input | no units
2095 | IO11 DI COUNTER 3 | IO11 DI COUNTER 3 | Analog Input | no units
2096 | IO11 DI COUNTER 4 | IO11 DI COUNTER 4 | Analog Input | no units
2097 | IO11 DI COUNTER 5 | IO11 DI COUNTER 5 | Analog Input | no units
2098 | IO11 DI COUNTER 6 | IO11 DI COUNTER 6 | Analog Input | no units
2099 | IO12 DI COUNTER 1 | IO12 DI COUNTER 1 | Analog Input | no units
2100 | IO12 DI COUNTER 2 | IO12 DI COUNTER 2 | Analog Input | no units
2101 | IO12 DI COUNTER 3 | IO12 DI COUNTER 3 | Analog Input | no units
2102 | IO12 DI COUNTER 4 | IO12 DI COUNTER 4 | Analog Input | no units
2103 | IO12 DI COUNTER 5 | IO12 DI COUNTER 5 | Analog Input | no units
2104 | IO12 DI COUNTER 6 | IO12 DI COUNTER 6 | Analog Input | no units
2105 | IO13 DI COUNTER 1 | IO13 DI COUNTER 1 | Analog Input | no units
2106 | IO13 DI COUNTER 2 | IO13 DI COUNTER 2 | Analog Input | no units
2107 | IO13 DI COUNTER 3 | IO13 DI COUNTER 3 | Analog Input | no units
2108 | IO13 DI COUNTER 4 | IO13 DI COUNTER 4 | Analog Input | no units
2109 | IO13 DI COUNTER 5 | IO13 DI COUNTER 5 | Analog Input | no units
2110 | IO13 DI COUNTER 6 | IO13 DI COUNTER 6 | Analog Input | no units
2111 | IO14 DI COUNTER 1 | IO14 DI COUNTER 1 | Analog Input | no units
2112 | IO14 DI COUNTER 2 | IO14 DI COUNTER 2 | Analog Input | no units
2113 | IO14 DI COUNTER 3 | IO14 DI COUNTER 3 | Analog Input | no units
2114 | IO14 DI COUNTER 4 | IO14 DI COUNTER 4 | Analog Input | no units
2115 | IO14 DI COUNTER 5 | IO14 DI COUNTER 5 | Analog Input | no units
2116 | IO14 DI COUNTER 6 | IO14 DI COUNTER 6 | Analog Input | no units
2117 | IO21 DI COUNTER 1 | IO21 DI COUNTER 1 | Analog Input | no units
2118 | IO21 DI COUNTER 2 | IO21 DI COUNTER 2 | Analog Input | no units
2119 | IO21 DI COUNTER 3 | IO21 DI COUNTER 3 | Analog Input | no units
2120 | IO21 DI COUNTER 4 | IO21 DI COUNTER 4 | Analog Input | no units
2121 | IO22 DI COUNTER 1 | IO22 DI COUNTER 1 | Analog Input | no units
2122 | IO22 DI COUNTER 2 | IO22 DI COUNTER 2 | Analog Input | no units
2123 | IO22 DI COUNTER 3 | IO22 DI COUNTER 3 | Analog Input | no units
2124 | IO22 DI COUNTER 4 | IO22 DI COUNTER 4 | Analog Input | no units
2125 | IO23 DI COUNTER 1 | IO23 DI COUNTER 1 | Analog Input | no units
2126 | IO23 DI COUNTER 2 | IO23 DI COUNTER 2 | Analog Input | no units
2127 | IO23 DI COUNTER 3 | IO23 DI COUNTER 3 | Analog Input | no units
2128 | IO23 DI COUNTER 4 | IO23 DI COUNTER 4 | Analog Input | no units
2129 | IO24 DI COUNTER 1 | IO24 DI COUNTER 1 | Analog Input | no units
2130 | IO24 DI COUNTER 2 | IO24 DI COUNTER 2 | Analog Input | no units
2131 | IO24 DI COUNTER 3 | IO24 DI COUNTER 3 | Analog Input | no units
2132 | IO24 DI COUNTER 4 | IO24 DI COUNTER 4 | Analog Input | no units
2133 | IO31 DI COUNTER 1 | IO31 DI COUNTER 1 | Analog Input | no units
2134 | IO31 DI COUNTER 2 | IO31 DI COUNTER 2 | Analog Input | no units
2135 | IO31 DI COUNTER 3 | IO31 DI COUNTER 3 | Analog Input | no units
2136 | IO31 DI COUNTER 4 | IO31 DI COUNTER 4 | Analog Input | no units
2137 | IO32 DI COUNTER 1 | IO32 DI COUNTER 1 | Analog Input | no units
2138 | IO32 DI COUNTER 2 | IO32 DI COUNTER 2 | Analog Input | no units
2139 | IO32 DI COUNTER 3 | IO32 DI COUNTER 3 | Analog Input | no units
2140 | IO32 DI COUNTER 4 | IO32 DI COUNTER 4 | Analog Input | no units
2141 | IO33 DI COUNTER 1 | IO33 DI COUNTER 1 | Analog Input | no units
2142 | IO33 DI COUNTER 2 | IO33 DI COUNTER 2 | Analog Input | no units
2143 | IO33 DI COUNTER 3 | IO33 DI COUNTER 3 | Analog Input | no units
2144 | IO33 DI COUNTER 4 | IO33 DI COUNTER 4 | Analog Input | no units
2145 | IO34 DI COUNTER 1 | IO34 DI COUNTER 1 | Analog Input | no units
2146 | IO34 DI COUNTER 2 | IO34 DI COUNTER 2 | Analog Input | no units
2147 | IO34 DI COUNTER 3 | IO34 DI COUNTER 3 | Analog Input | no units
2148 | IO34 DI COUNTER 4 | IO34 DI COUNTER 4 | Analog Input | no units
I/O Module - Analog Inputs
2149 | IO31 AI 1 | IO31 AI 1 | Analog Input | no units
2150 | IO31 AI 2 | IO31 AI 2 | Analog Input | no units
2151 | IO32 AI 1 | IO32 AI 1 | Analog Input | no units
2152 | IO32 AI 2 | IO32 AI 2 | Analog Input | no units
2153 | IO33 AI 1 | IO33 AI 1 | Analog Input | no units
2154 | IO33 AI 2 | IO33 AI 2 | Analog Input | no units
2155 | IO34 AI 1 | IO34 AI 1 | Analog Input | no units
2156 | IO34 AI 2 | IO34 AI 2 | Analog Input | no units
I/O Module - Analog Outputs
2157 | IO21 AO 1 | IO21 AO 1 | Analog Input | no units
2158 | IO21 AO 2 | IO21 AO 2 | Analog Input | no units
2159 | IO22 AO 1 | IO22 AO 1 | Analog Input | no units
2160 | IO22 AO 2 | IO22 AO 2 | Analog Input | no units
2161 | IO23 AO 1 | IO23 AO 1 | Analog Input | no units
2162 | IO23 AO 2 | IO23 AO 2 | Analog Input | no units
2163 | IO24 AO 1 | IO24 AO 1 | Analog Input | no units
2164 | IO24 AO 2 | IO24 AO 2 | Analog Input | no units
Binary Input Objects
I/O Module - Digital Input Status
1 | IO01 DI STATUS 1 | IO01 DI STATUS 1 | Binary Input | -
2 | IO01 DI STATUS 2 | IO01 DI STATUS 2 | Binary Input | -
3 | IO01 DI STATUS 3 | IO01 DI STATUS 3 | Binary Input | -
4 | IO01 DI STATUS 4 | IO01 DI STATUS 4 | Binary Input | -
5 | IO11 DI STATUS 1 | IO11 DI STATUS 1 | Binary Input | -
6 | IO11 DI STATUS 2 | IO11 DI STATUS 2 | Binary Input | -
7 | IO11 DI STATUS 3 | IO11 DI STATUS 3 | Binary Input | -
8 | IO11 DI STATUS 4 | IO11 DI STATUS 4 | Binary Input | -
9 | IO11 DI STATUS 5 | IO11 DI STATUS 5 | Binary Input | -
10 | IO11 DI STATUS 6 | IO11 DI STATUS 6 | Binary Input | -
11 | IO12 DI STATUS 1 | IO12 DI STATUS 1 | Binary Input | -
12 | IO12 DI STATUS 2 | IO12 DI STATUS 2 | Binary Input | -
13 | IO12 DI STATUS 3 | IO12 DI STATUS 3 | Binary Input | -
14 | IO12 DI STATUS 4 | IO12 DI STATUS 4 | Binary Input | -
15 | IO12 DI STATUS 5 | IO12 DI STATUS 5 | Binary Input | -
16 | IO12 DI STATUS 6 | IO12 DI STATUS 6 | Binary Input | -
17 | IO13 DI STATUS 1 | IO13 DI STATUS 1 | Binary Input | -
18 | IO13 DI STATUS 2 | IO13 DI STATUS 2 | Binary Input | -
19 | IO13 DI STATUS 3 | IO13 DI STATUS 3 | Binary Input | -
20 | IO13 DI STATUS 4 | IO13 DI STATUS 4 | Binary Input | -
21 | IO13 DI STATUS 5 | IO13 DI STATUS 5 | Binary Input | -
22 | IO13 DI STATUS 6 | IO13 DI STATUS 6 | Binary Input | -
23 | IO14 DI STATUS 1 | IO14 DI STATUS 1 | Binary Input | -
24 | IO14 DI STATUS 2 | IO14 DI STATUS 2 | Binary Input | -
25 | IO14 DI STATUS 3 | IO14 DI STATUS 3 | Binary Input | -
26 | IO14 DI STATUS 4 | IO14 DI STATUS 4 | Binary Input | -
27 | IO14 DI STATUS 5 | IO14 DI STATUS 5 | Binary Input | -
28 | IO14 DI STATUS 6 | IO14 DI STATUS 6 | Binary Input | -
29 | IO21 DI STATUS 1 | IO21 DI STATUS 1 | Binary Input | -
30 | IO21 DI STATUS 2 | IO21 DI STATUS 2 | Binary Input | -
31 | IO21 DI STATUS 3 | IO21 DI STATUS 3 | Binary Input | -
32 | IO21 DI STATUS 4 | IO21 DI STATUS 4 | Binary Input | -
33 | IO22 DI STATUS 1 | IO22 DI STATUS 1 | Binary Input | -
34 | IO22 DI STATUS 2 | IO22 DI STATUS 2 | Binary Input | -
35 | IO22 DI STATUS 3 | IO22 DI STATUS 3 | Binary Input | -
36 | IO22 DI STATUS 4 | IO22 DI STATUS 4 | Binary Input | -
37 | IO23 DI STATUS 1 | IO23 DI STATUS 1 | Binary Input | -
38 | IO23 DI STATUS 2 | IO23 DI STATUS 2 | Binary Input | -
39 | IO23 DI STATUS 3 | IO23 DI STATUS 3 | Binary Input | -
40 | IO23 DI STATUS 4 | IO23 DI STATUS 4 | Binary Input | -
41 | IO24 DI STATUS 1 | IO24 DI STATUS 1 | Binary Input | -
42 | IO24 DI STATUS 2 | IO24 DI STATUS 2 | Binary Input | -
43 | IO24 DI STATUS 3 | IO24 DI STATUS 3 | Binary Input | -
44 | IO24 DI STATUS 4 | IO24 DI STATUS 4 | Binary Input | -
45 | IO31 DI STATUS 1 | IO31 DI STATUS 1 | Binary Input | -
46 | IO31 DI STATUS 2 | IO31 DI STATUS 2 | Binary Input | -
47 | IO31 DI STATUS 3 | IO31 DI STATUS 3 | Binary Input | -
48 | IO31 DI STATUS 4 | IO31 DI STATUS 4 | Binary Input | -
49 | IO32 DI STATUS 1 | IO32 DI STATUS 1 | Binary Input | -
50 | IO32 DI STATUS 2 | IO32 DI STATUS 2 | Binary Input | -
51 | IO32 DI STATUS 3 | IO32 DI STATUS 3 | Binary Input | -
52 | IO32 DI STATUS 4 | IO32 DI STATUS 4 | Binary Input | -
53 | IO33 DI STATUS 1 | IO33 DI STATUS 1 | Binary Input | -
54 | IO33 DI STATUS 2 | IO33 DI STATUS 2 | Binary Input | -
55 | IO33 DI STATUS 3 | IO33 DI STATUS 3 | Binary Input | -
56 | IO33 DI STATUS 4 | IO33 DI STATUS 4 | Binary Input | -
57 | IO34 DI STATUS 1 | IO34 DI STATUS 1 | Binary Input | -
58 | IO34 DI STATUS 2 | IO34 DI STATUS 2 | Binary Input | -
59 | IO34 DI STATUS 3 | IO34 DI STATUS 3 | Binary Input | -
60 | IO34 DI STATUS 4 | IO34 DI STATUS 4 | Binary Input | -
I/O Module - Relay Output Status
61 | IO11 RO 1 | IO11 RO 1 | Binary Input | -
62 | IO11 RO 2 | IO11 RO 2 | Binary Input | -
63 | IO12 RO 1 | IO12 RO 1 | Binary Input | -
64 | IO12 RO 2 | IO12 RO 2 | Binary Input | -
65 | IO13 RO 1 | IO13 RO 1 | Binary Input | -
66 | IO13 RO 2 | IO13 RO 2 | Binary Input | -
67 | IO14 RO 1 | IO14 RO 1 | Binary Input | -
68 | IO14 RO 2 | IO14 RO 2 | Binary Input | -
69 | IO31 RO 1 | IO31 RO 1 | Binary Input | -
70 | IO31 RO 2 | IO31 RO 2 | Binary Input | -
71 | IO32 RO 1 | IO32 RO 1 | Binary Input | -
72 | IO32 RO 2 | IO32 RO 2 | Binary Input | -
73 | IO33 RO 1 | IO33 RO 1 | Binary Input | -
74 | IO33 RO 2 | IO33 RO 2 | Binary Input | -
75 | IO34 RO 1 | IO34 RO 1 | Binary Input | -
76 | IO34 RO 2 | IO34 RO 2 | Binary Input | -

## Notes
Notes
Source:
Acuvim-S firmware v1.04p13 (tag v1.04p13, 2026-09-22). Objects are defined by the parameter mapping and BACnet mapper tables in the firmware database (createParamDefault).
Object counts:
Analog Input: 2164 objects (instances 1-2164)
Binary Input: 76 objects (instances 1-76)
Availability:
I/O module objects (DI counters, DI status, AI, AO, RO) are only meaningful when the corresponding I/O module (IO01, IO11-IO14, IO21-IO24, IO31-IO34) is installed.
COV_Increment is supported on BACnet/IP only (not on MS/TP). Default COV increment is 0 for every Analog Input.
Writable properties: Analog Input - Present_Value, Out_Of_Service, Description, COV_Increment (IP only). Binary Input - Present_Value, Out_Of_Service, Description.
Units (BACnet Engineering Units enumeration):
amperes (3) -> shown as "A"
volts (5) -> shown as "V"
kilovolt-amperes (9) -> shown as "kVA"
kilovolt-amperes-reactive (12) -> shown as "kvar"
degrees-phase (14) -> shown as "degrees"
power-factor (15) -> shown as "PF"
kilowatt-hours (19) -> shown as "kWh"
hertz (27) -> shown as "Hz"
kilowatts (48) -> shown as "kW"
no-units (95) -> shown as "no units"
percent (98) -> shown as "%"
kilovolt-ampere-hours (240) -> shown as "kVAh"
kilovolt-ampere-hours-reactive (243) -> shown as "kvarh"