## Real Time Parameters
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value | Release version
Real time basic parameters（100ms)
| 0x3000 | 0x3001 | 12288 | 12289 | Freq_rms | float32 | R | 2
| 0x3002 | 0x3003 | 12290 | 12291 | Ua_rms | float32 | R | 2
| 0x3004 | 0x3005 | 12292 | 12293 | Ub_rms | float32 | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Uc_rms | float32 | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Uvag_rms | float32 | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Uab_rms | float32 | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Ubc_rms | float32 | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Uca_rms | float32 | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Ulag_rms | float32 | R | 2
| 0x3012 | 0x3013 | 12306 | 12307 | Ia_rms | float32 | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | Ib_rms | float32 | R | 2
| 0x3016 | 0x3017 | 12310 | 12311 | Ic_rms | float32 | R | 2
| 0x3018 | 0x3019 | 12312 | 12313 | Ivag_rms | float32 | R | 2
| 0x301A | 0x301B | 12314 | 12315 | In_rms | float32 | R | 2
| 0x301C | 0x301D | 12316 | 12317 | Pa_rms | float32 | R | 2
| 0x301E | 0x301F | 12318 | 12319 | Pb_rms | float32 | R | 2
| 0x3020 | 0x3021 | 12320 | 12321 | Pc_rms | float32 | R | 2
| 0x3022 | 0x3023 | 12322 | 12323 | P_rms | float32 | R | 2
| 0x3024 | 0x3025 | 12324 | 12325 | Qa_rms | float32 | R | 2
| 0x3026 | 0x3027 | 12326 | 12327 | Qb_rms | float32 | R | 2
| 0x3028 | 0x3029 | 12328 | 12329 | Qc_rms | float32 | R | 2
| 0x302A | 0x302B | 12330 | 12331 | Q_rms | float32 | R | 2
| 0x302C | 0x302D | 12332 | 12333 | Sa_rms | float32 | R | 2
| 0x302E | 0x302F | 12334 | 12335 | Sb_rms | float32 | R | 2
| 0x3030 | 0x3031 | 12336 | 12337 | Sc_rms | float32 | R | 2
| 0x3032 | 0x3033 | 12338 | 12339 | S_rms | float32 | R | 2
| 0x3034 | 0x3035 | 12340 | 12341 | PFa_rms | float32 | R | 2
| 0x3036 | 0x3037 | 12342 | 12343 | PFb_rms | float32 | R | 2
| 0x3038 | 0x3039 | 12344 | 12345 | PFc_rms | float32 | R | 2
| 0x303A | 0x303B | 12346 | 12347 | PF_rms | float32 | R | 2
| 0x303C | 0x303D | 12348 | 12349 | AI1 value， fast read | float32 | R | 2
| 0x303E | 0x303F | 12350 | 12351 | AI2 value， fast read | float32 | R | 2
| 0x3040 | 0x3041 | 12352 | 12353 | AI3 value， fast read | float32 | R | 2
| 0x3042 | 0x3043 | 12354 | 12355 | AI4 value， fast read | float32 | R | 2
| 0x3044 | 0x3045 | 12356 | 12357 | Displacement Power factor, Phase A | float32 | R | 2
| 0x3046 | 0x3047 | 12358 | 12359 | Displacement Power factor, Phase B | float32 | R | 2
| 0x3048 | 0x3049 | 12360 | 12361 | Displacement Power factor, Phase C | float32 | R | 2
| 0x304A | 0x304B | 12362 | 12363 | Predictive Demand P | float32 | R | 2
| 0x304C | 0x304D | 12364 | 12365 | Predictive Demand Q | float32 | R | 2
| 0x304E | 0x304F | 12366 | 12367 | Predictive Demand S | float32 | R | 2
| 0x3050 | 0x3051 | 12368 | 12369 | P Max, Phase A - Last Interval | float32 | R | 2
| 0x3052 | 0x3053 | 12370 | 12371 | P Max, Phase B - Last Interval | float32 | R | 2
| 0x3054 | 0x3055 | 12372 | 12373 | P Max, Phase C - Last Interval | float32 | R | 2
| 0x3056 | 0x3057 | 12374 | 12375 | P Max, Total - Last Interval | float32 | R | 2
| 0x3058 | 0x3059 | 12376 | 12377 | P Min, Phase A - Last Interval | float32 | R | 2
| 0x305A | 0x305B | 12378 | 12379 | P Min, Phase B - Last Interval | float32 | R | 2
| 0x305C | 0x305D | 12380 | 12381 | P Min, Phase C - Last Interval | float32 | R | 2
| 0x305E | 0x305F | 12382 | 12383 | P Min, Total - Last Interval | float32 | R | 2
| 0x3060 | 0x3061 | 12384 | 12385 | P Mean, Phase A - Last Interval | float32 | R | 2
| 0x3062 | 0x3063 | 12386 | 12387 | P Mean, Phase B - Last Interval | float32 | R | 2
| 0x3064 | 0x3065 | 12388 | 12389 | P Mean, Phase C - Last Interval | float32 | R | 2
| 0x3066 | 0x3067 | 12390 | 12391 | P Mean, Total - Last Interval | float32 | R | 2
| 0x3068 | 0x3069 | 12392 | 12393 | Q Max, Phase A - Last Interval | float32 | R | 2
| 0x306A | 0x306B | 12394 | 12395 | Q Max, Phase B - Last Interval | float32 | R | 2
| 0x306C | 0x306D | 12396 | 12397 | Q Max, Phase C - Last Interval | float32 | R | 2
| 0x306E | 0x306F | 12398 | 12399 | Q Max, Total - Last Interval | float32 | R | 2
| 0x3070 | 0x3071 | 12400 | 12401 | Q Min, Phase A - Last Interval | float32 | R | 2
| 0x3072 | 0x3073 | 12402 | 12403 | Q Min, Phase B - Last Interval | float32 | R | 2
| 0x3074 | 0x3075 | 12404 | 12405 | Q Min, Phase C - Last Interval | float32 | R | 2
| 0x3076 | 0x3077 | 12406 | 12407 | Q Min, Total - Last Interval | float32 | R | 2
| 0x3078 | 0x3079 | 12408 | 12409 | Q Mean, Phase A - Last Interval | float32 | R | 2
| 0x307A | 0x307B | 12410 | 12411 | Q Mean, Phase B - Last Interval | float32 | R | 2
| 0x307C | 0x307D | 12412 | 12413 | Q Mean, Phase C - Last Interval | float32 | R | 2
| 0x307E | 0x307F | 12414 | 12415 | Q Mean, Total - Last Interval | float32 | R | 2
| 0x3080 | 0x3081 | 12416 | 12417 | S Max, Phase A - Last Interval | float32 | R | 2
| 0x3082 | 0x3083 | 12418 | 12419 | S Max, Phase B - Last Interval | float32 | R | 2
| 0x3084 | 0x3085 | 12420 | 12421 | S Max, Phase C - Last Interval | float32 | R | 2
| 0x3086 | 0x3087 | 12422 | 12423 | S Max, Total - Last Interval | float32 | R | 2
| 0x3088 | 0x3089 | 12424 | 12425 | S Min, Phase A - Last Interval | float32 | R | 2
| 0x308A | 0x308B | 12426 | 12427 | S Min, Phase B - Last Interval | float32 | R | 2
| 0x308C | 0x308D | 12428 | 12429 | S Min, Phase C - Last Interval | float32 | R | 2
| 0x308E | 0x308F | 12430 | 12431 | S Min, Total - Last Interval | float32 | R | 2
| 0x3090 | 0x3091 | 12432 | 12433 | S Mean, Phase A - Last Interval | float32 | R | 2
| 0x3092 | 0x3093 | 12434 | 12435 | S Mean, Phase B - Last Interval | float32 | R | 2
| 0x3094 | 0x3095 | 12436 | 12437 | S Mean, Phase C - Last Interval | float32 | R | 2
| 0x3096 | 0x3097 | 12438 | 12439 | S Mean, Total - Last Interval | float32 | R | 2
| 0x3098 | 0x3099 | 12440 | 12441 | I Max, Phase A - Last Interval | float32 | R | 2
| 0x309A | 0x309B | 12442 | 12443 | I Max, Phase B - Last Interval | float32 | R | 2
| 0x309C | 0x309D | 12444 | 12445 | I Max, Phase C - Last Interval | float32 | R | 2
| 0x309E | 0x309F | 12446 | 12447 | I Max, Phase N - Last Interval | float32 | R | 2
| 0x30A0 | 0x30A1 | 12448 | 12449 | I Max, average - Last Interval | float32 | R | 2
| 0x30A2 | 0x30A3 | 12450 | 12451 | I Min, Phase A - Last Interval | float32 | R | 2
| 0x30A4 | 0x30A5 | 12452 | 12453 | I Min, Phase B - Last Interval | float32 | R | 2
| 0x30A6 | 0x30A7 | 12454 | 12455 | I Min, Phase C - Last Interval | float32 | R | 2
| 0x30A8 | 0x30A9 | 12456 | 12457 | I Min, Phase N - Last Interval | float32 | R | 2
| 0x30AA | 0x30AB | 12458 | 12459 | I Min, average - Last Interval | float32 | R | 2
| 0x30AC | 0x30AD | 12460 | 12461 | I Mean, Phase A - Last Interval | float32 | R | 2
| 0x30AE | 0x30AF | 12462 | 12463 | I Mean, Phase B - Last Interval | float32 | R | 2
| 0x30B0 | 0x30B1 | 12464 | 12465 | I Mean, Phase C - Last Interval | float32 | R | 2
| 0x30B2 | 0x30B3 | 12466 | 12467 | I Mean, Phase N - Last Interval | float32 | R | 2
| 0x30B4 | 0x30B5 | 12468 | 12469 | I Mean, average - Last Interval | float32 | R | 2
| 0x30B6 | 0x30B7 | 12470 | 12471 | V Max, Phase A - Last Interval | float32 | R | 2
| 0x30B8 | 0x30B9 | 12472 | 12473 | V Max, Phase B - Last Interval | float32 | R | 2
| 0x30BA | 0x30BB | 12474 | 12475 | V Max, Phase C - Last Interval | float32 | R | 2
| 0x30BC | 0x30BD | 12476 | 12477 | V Max, Phase AB - Last Interval | float32 | R | 2
| 0x30BE | 0x30BF | 12478 | 12479 | V Max, Phase BC - Last Interval | float32 | R | 2
| 0x30C0 | 0x30C1 | 12480 | 12481 | V Max, Phase CA - Last Interval | float32 | R | 2
| 0x30C2 | 0x30C3 | 12482 | 12483 | V Min, Phase A - Last Interval | float32 | R | 2
| 0x30C4 | 0x30C5 | 12484 | 12485 | V Min, Phase B - Last Interval | float32 | R | 2
| 0x30C6 | 0x30C7 | 12486 | 12487 | V Min, Phase C - Last Interval | float32 | R | 2
| 0x30C8 | 0x30C9 | 12488 | 12489 | V Min, Phase AB - Last Interval | float32 | R | 2
| 0x30CA | 0x30CB | 12490 | 12491 | V Min, Phase BC - Last Interval | float32 | R | 2
| 0x30CC | 0x30CD | 12492 | 12493 | V Min, Phase CA - Last Interval | float32 | R | 2
| 0x30CE | 0x30CF | 12494 | 12495 | V Mean, Phase A - Last Interval | float32 | R | 2
| 0x30D0 | 0x30D1 | 12496 | 12497 | V Mean, Phase B - Last Interval | float32 | R | 2
| 0x30D2 | 0x30D3 | 12498 | 12499 | V Mean, Phase C - Last Interval | float32 | R | 2
| 0x30D4 | 0x30D5 | 12500 | 12501 | V Mean, Phase AB - Last Interval | float32 | R | 2
| 0x30D6 | 0x30D7 | 12502 | 12503 | V Mean, Phase BC - Last Interval | float32 | R | 2
| 0x30D8 | 0x30D9 | 12504 | 12505 | V Mean, Phase CA - Last Interval | float32 | R | 2
| 0x30DA | 0x30DB | 12506 | 12507 | Displacement Power factor, System | float32 | R | 2
140
Real time basic parameters（Integer）
| 0x3200 | 0x3200 | 12800 | 12800 | Freq_rms | int16 | R | 1
| 0x3201 | 0x3201 | 12801 | 12801 | Ua_rms | int16 | R | 1
| 0x3202 | 0x3202 | 12802 | 12802 | Ub_rms | int16 | R | 1
| 0x3203 | 0x3203 | 12803 | 12803 | Uc_rms | int16 | R | 1
| 0x3204 | 0x3204 | 12804 | 12804 | Uvag_rms | int16 | R | 1
| 0x3205 | 0x3205 | 12805 | 12805 | Uab_rms | int16 | R | 1
| 0x3206 | 0x3206 | 12806 | 12806 | Ubc_rms | int16 | R | 1
| 0x3207 | 0x3207 | 12807 | 12807 | Uca_rms | int16 | R | 1
| 0x3208 | 0x3208 | 12808 | 12808 | Ulag_rms | int16 | R | 1
| 0x3209 | 0x3209 | 12809 | 12809 | Ia_rms | int16 | R | 1
| 0x320A | 0x320A | 12810 | 12810 | Ib_rms | int16 | R | 1
| 0x320B | 0x320B | 12811 | 12811 | Ic_rms | int16 | R | 1
| 0x320C | 0x320C | 12812 | 12812 | Ivag_rms | int16 | R | 1
| 0x320D | 0x320D | 12813 | 12813 | In_rms | int16 | R | 1
| 0x320E | 0x320E | 12814 | 12814 | Pa_rms | int16 | R | 1
| 0x320F | 0x320F | 12815 | 12815 | Pb_rms | int16 | R | 1
| 0x3210 | 0x3210 | 12816 | 12816 | Pc_rms | int16 | R | 1
| 0x3211 | 0x3211 | 12817 | 12817 | P_rms | int16 | R | 1
| 0x3212 | 0x3212 | 12818 | 12818 | Qa_rms | int16 | R | 1
| 0x3213 | 0x3213 | 12819 | 12819 | Qb_rms | int16 | R | 1
| 0x3214 | 0x3214 | 12820 | 12820 | Qc_rms | int16 | R | 1
| 0x3215 | 0x3215 | 12821 | 12821 | Q_rms | int16 | R | 1
| 0x3216 | 0x3216 | 12822 | 12822 | Sa_rms | int16 | R | 1
| 0x3217 | 0x3217 | 12823 | 12823 | Sb_rms | int16 | R | 1
| 0x3218 | 0x3218 | 12824 | 12824 | Sc_rms | int16 | R | 1
| 0x3219 | 0x3219 | 12825 | 12825 | S_rms | int16 | R | 1
| 0x321A | 0x321A | 12826 | 12826 | PFa_rms | int16 | R | 1
| 0x321B | 0x321B | 12827 | 12827 | PFb_rms | int16 | R | 1
| 0x321C | 0x321C | 12828 | 12828 | PFc_rms | int16 | R | 1
| 0x321D | 0x321D | 12829 | 12829 | PF_rms | int16 | R | 1
| 0x321E | 0x321E | 12830 | 12830 | Unbl_u2 | int16 | R | 1
| 0x321F | 0x321F | 12831 | 12831 | Unbl_i2 | int16 | R | 1
| 0x3220 | 0x3220 | 12832 | 12832 | Rlc_val | int16 | R | 1
| 0x3221 | 0x3221 | 12833 | 12833 | P_dema | int16 | R | 1
| 0x3222 | 0x3222 | 12834 | 12834 | Q_dema | int16 | R | 1
| 0x3223 | 0x3223 | 12835 | 12835 | S_dema | int16 | R | 1
| 0x3224 | 0x3224 | 12836 | 12836 | Ia demand | int16 | R | 1
| 0x3225 | 0x3225 | 12837 | 12837 | Ib demand | int16 | R | 1
| 0x3226 | 0x3226 | 12838 | 12838 | Ic demand | int16 | R | 1
Basic parameters（20ms）
Acuvim II V4/Eaton/Acuvim-L V4
| 0x3400 | 0x3401 | 13312 | 13313 | FAST_RMS_UA | float32 | R | 2
| 0x3402 | 0x3403 | 13314 | 13315 | FAST_RMS_UB | float32 | R | 2
| 0x3404 | 0x3405 | 13316 | 13317 | FAST_RMS_UC | float32 | R | 2
| 0x3406 | 0x3407 | 13318 | 13319 | FAST_RMS_UAB | float32 | R | 2
| 0x3408 | 0x3409 | 13320 | 13321 | FAST_RMS_UBC | float32 | R | 2
| 0x340A | 0x340B | 13322 | 13323 | FAST_RMS_UCA | float32 | R | 2
| 0x340C | 0x340D | 13324 | 13325 | FAST_RMS_IA | float32 | R | 2
| 0x340E | 0x340F | 13326 | 13327 | FAST_RMS_IB | float32 | R | 2
| 0x3410 | 0x3411 | 13328 | 13329 | FAST_RMS_IC | float32 | R | 2
| 0x3412 | 0x3413 | 13330 | 13331 | FAST_RMS_UAVG | float32 | R | 2
| 0x3414 | 0x3415 | 13332 | 13333 | FAST_RMS_VLLAVG | float32 | R | 2
| 0x3416 | 0x3417 | 13334 | 13335 | FAST_RMS_IAVG | float32 | R | 2
| 0x3418 | 0x3419 | 13336 | 13337 | FAST_RMS_PSUM | float32 | R | 2
| 0x341A | 0x341B | 13338 | 13339 | FAST_RMS_QSUM | float32 | R | 2
| 0x341C | 0x341D | 13340 | 13341 | FAST_RMS_FREQ | float32 | R | 2
| 0x341E | 0x341F | 13342 | 13343 | Counter | float32 | R | 2
Acuvim II V2
| 0x3500 | 0x3501 | 13568 | 13569 | FAST_RMS_UA | float32 | R | 2
| 0x3502 | 0x3503 | 13570 | 13571 | FAST_RMS_UB | float32 | R | 2
| 0x3504 | 0x3505 | 13572 | 13573 | FAST_RMS_UC | float32 | R | 2
| 0x3506 | 0x3507 | 13574 | 13575 | FAST_RMS_IA | float32 | R | 2
| 0x3508 | 0x3509 | 13576 | 13577 | FAST_RMS_IB | float32 | R | 2
| 0x350A | 0x350B | 13578 | 13579 | FAST_RMS_IC | float32 | R | 2
| 0x350C | 0x350D | 13580 | 13581 | FAST_RMS_FREQ | float32 | R | 2
| 0x350E | 0x350F | 13582 | 13583 | FAST_RMS_UAB | float32 | R | 2
| 0x3510 | 0x3511 | 13584 | 13585 | FAST_RMS_UBC | float32 | R | 2
| 0x3512 | 0x3513 | 13586 | 13587 | FAST_RMS_UCA | float32 | R | 2
| 0x3514 | 0x3515 | 13588 | 13589 | FAST_RMS_PSUM | float32 | R | 2
| 0x3516 | 0x3517 | 13590 | 13591 | FAST_RMS_QSUM | float32 | R | 2
Real time basic parameters（1S）
| 0x4000 | 0x4001 | 16384 | 16385 | Freq_rms | float32 | R | 2
| 0x4002 | 0x4003 | 16386 | 16387 | Ua_rms | float32 | R | 2
| 0x4004 | 0x4005 | 16388 | 16389 | Ub_rms | float32 | R | 2
| 0x4006 | 0x4007 | 16390 | 16391 | Uc_rms | float32 | R | 2
| 0x4008 | 0x4009 | 16392 | 16393 | Uvag_rms | float32 | R | 2
| 0x400A | 0x400B | 16394 | 16395 | Uab_rms | float32 | R | 2
| 0x400C | 0x400D | 16396 | 16397 | Ubc_rms | float32 | R | 2
| 0x400E | 0x400F | 16398 | 16399 | Uca_rms | float32 | R | 2
| 0x4010 | 0x4011 | 16400 | 16401 | Ulag_rms | float32 | R | 2
| 0x4012 | 0x4013 | 16402 | 16403 | Ia_rms | float32 | R | 2
| 0x4014 | 0x4015 | 16404 | 16405 | Ib_rms | float32 | R | 2
| 0x4016 | 0x4017 | 16406 | 16407 | Ic_rms | float32 | R | 2
| 0x4018 | 0x4019 | 16408 | 16409 | Ivag_rms | float32 | R | 2
| 0x401A | 0x401B | 16410 | 16411 | In_rms | float32 | R | 2
| 0x401C | 0x401D | 16412 | 16413 | Pa_rms | float32 | R | 2
| 0x401E | 0x401F | 16414 | 16415 | Pb_rms | float32 | R | 2
| 0x4020 | 0x4021 | 16416 | 16417 | Pc_rms | float32 | R | 2
| 0x4022 | 0x4023 | 16418 | 16419 | P_rms | float32 | R | 2
| 0x4024 | 0x4025 | 16420 | 16421 | Qa_rms | float32 | R | 2
| 0x4026 | 0x4027 | 16422 | 16423 | Qb_rms | float32 | R | 2
| 0x4028 | 0x4029 | 16424 | 16425 | Qc_rms | float32 | R | 2
| 0x402A | 0x402B | 16426 | 16427 | Q_rms | float32 | R | 2
| 0x402C | 0x402D | 16428 | 16429 | Sa_rms | float32 | R | 2
| 0x402E | 0x402F | 16430 | 16431 | Sb_rms | float32 | R | 2
| 0x4030 | 0x4031 | 16432 | 16433 | Sc_rms | float32 | R | 2
| 0x4032 | 0x4033 | 16434 | 16435 | S_rms | float32 | R | 2
| 0x4034 | 0x4035 | 16436 | 16437 | PFa_rms | float32 | R | 2
| 0x4036 | 0x4037 | 16438 | 16439 | PFb_rms | float32 | R | 2
| 0x4038 | 0x4039 | 16440 | 16441 | PFc_rms | float32 | R | 2
| 0x403A | 0x403B | 16442 | 16443 | PF_rms | float32 | R | 2
| 0x403C | 0x403D | 16444 | 16445 | Unbl_u2 | float32 | R | 2
| 0x403E | 0x403F | 16446 | 16447 | Unbl_i2 | float32 | R | 2
| 0x4040 | 0x4041 | 16448 | 16449 | Rlc_val | float32 | R | 2
| 0x4042 | 0x4043 | 16450 | 16451 | P_dema | float32 | R | 2
| 0x4044 | 0x4045 | 16452 | 16453 | Q_dema | float32 | R | 2
| 0x4046 | 0x4047 | 16454 | 16455 | S_dema | float32 | R | 2
Energy （1S）
| 0x4048 | 0x4049 | 16456 | 16457 | Ep_imp Import active energy | uint32 | R/W | 2
| 0x404A | 0x404B | 16458 | 16459 | Ep_exp Expot active energy | uint32 | R/W | 2
| 0x404C | 0x404D | 16460 | 16461 | Eq_imp Import reactive energy | uint32 | R/W | 2
| 0x404E | 0x404F | 16462 | 16463 | Eq_exp Expot reactive energy | uint32 | R/W | 2
| 0x4050 | 0x4051 | 16464 | 16465 | Ep_total Total active energy | uint32 | R/W | 2
| 0x4052 | 0x4053 | 16466 | 16467 | Ep_net Net active energy | int32 | R/W | 2
| 0x4054 | 0x4055 | 16468 | 16469 | Eq_total Total reactive energy | uint32 | R/W | 2
| 0x4056 | 0x4057 | 16470 | 16471 | Eq_net Net reactive energy | int32 | R/W | 2
| 0x4058 | 0x4059 | 16472 | 16473 | Es Apparent energy | uint32 | R/W | 2
Harmonics - THD（3S）
| 0x405A |  | 16474 |  | THD_V1(V12) | int16 | R | 1 |  | two decimal
| 0x405B |  | 16475 |  | THD_V2(V31) | int16 | R | 1
| 0x405C |  | 16476 |  | THD_V3(V23) | int16 | R | 1
| 0x405D |  | 16477 |  | THD_avg | int16 | R | 1
| 0x405E |  | 16478 |  | THD_I1 | int16 | R | 1
| 0x405F |  | 16479 |  | THD_I2 | int16 | R | 1
| 0x4060 |  | 16480 |  | THD_I3 | int16 | R | 1
| 0x4061 |  | 16481 |  | THD_Iavg | int16 | R | 1
| 0x4062 | 0x407F | 16482 | 16511 | V1(V12) 2-31st harmonic | int16 | R | 30
| 0x4080 |  | 16512 |  | Odd THD_V1(V12) | int16 | R | 1
| 0x4081 |  | 16513 |  | Even THD_V1(V12) | int16 | R | 1
| 0x4082 |  | 16514 |  | V1(V12) crest factor | int16 | R | 1
| 0x4083 |  | 16515 |  | V1(V12) Telephone Harmonic Form Factor | int16 | R | 1
| 0x4084 | 0x40A1 | 16516 | 16545 | V2(V31) 2-31st harmonic | int16 | R | 30
| 0x40A2 |  | 16546 |  | Odd THD_V2(V31) | int16 | R | 1
| 0x40A3 |  | 16547 |  | Even THD_V2(V31) | int16 | R | 1
| 0x40A4 |  | 16548 |  | V2(V31) crest factor | int16 | R | 1
| 0x40A5 |  | 16549 |  | V2(V31) Telephone Harmonic Form Factor | int16 | R | 1
| 0x40A6 | 0x40C3 | 16550 | 16579 | V3(V23) 2-31st harmonic | int16 | R | 30
| 0x40C4 |  | 16580 |  | Odd THD_V3(V23) | int16 | R | 1
| 0x40C5 |  | 16581 |  | Even THD_V3(V23) | int16 | R | 1
| 0x40C6 |  | 16582 |  | V3(V23) crest factor | int16 | R | 1
| 0x40C7 |  | 16583 |  | V3(V23) Telephone Harmonic Form Factor | int16 | R | 1
| 0x40C8 | 0x40E5 | 16584 | 16613 | I1 2nd-31st harmonic | int16 | R | 30
| 0x40E6 |  | 16614 |  | Odd THD_I1 | int16 | R | 1
| 0x40E7 |  | 16615 |  | Even THD_I1 | int16 | R | 1
| 0x40E8 |  | 16616 |  | I1 K factor | int16 | R | 1
| 0x40E9 | 0x4106 | 16617 | 16646 | I2 2nd-31st harmonic | int16 | R | 30
| 0x4107 |  | 16647 |  | Odd THD_I2 | int16 | R | 1
| 0x4108 |  | 16648 |  | Even THD_I2 | int16 | R | 1
| 0x4109 |  | 16649 |  | I2 K factor | int16 | R | 1
| 0x410A | 0x4127 | 16650 | 16679 | I3 2nd-31st harmonic | int16 | R | 30
| 0x4128 |  | 16680 |  | Odd THD_I3 | int16 | R | 1
| 0x4129 |  | 16681 |  | Even THD_I3 | int16 | R | 1
| 0x412A |  | 16682 |  | I3 K factor | int16 | R | 1
| 0x412B |  | 16683 |  | TDD_I1 | int16 | R | 1
| 0x412C |  | 16684 |  | TDD_I2 | int16 | R | 1
| 0x412D |  | 16685 |  | TDD_I3 | int16 | R | 1
| 0x412E |  | 16686 |  | TDD_Iavg | int16 | R | 1
| 0x412F |  | 16687 |  | I1 crest factor | int16 | R | 1
| 0x4130 |  | 16688 |  | I2 crest factor | int16 | R | 1
| 0x4131 |  | 16689 |  | I3 crest factor | int16 | R | 1
| 0x4132 |  | 16690 |  | In crest factor | int16 | R | 1
Sequence
| 0x4294 |  | 17044 |  | Real part of Voltage Positive Sequence | int16 | R | 1
| 0x4295 |  | 17045 |  | Imag part of Voltage Postive Sequence | int16 | R | 1
| 0x4296 |  | 17046 |  | Real part of Voltage Negative Sequence | int16 | R | 1
| 0x4297 |  | 17047 |  | Imag part of Voltage Negative Sequence | int16 | R | 1
| 0x4298 |  | 17048 |  | Real part of Voltage Zero Sequence | int16 | R | 1
| 0x4299 |  | 17049 |  | Imag part of Voltage Zero Sequence | int16 | R | 1
| 0x429A |  | 17050 |  | Real part of Current Positive Sequence | int16 | R | 1
| 0x429B |  | 17051 |  | Imag part of Current Postive Sequence | int16 | R | 1
| 0x429C |  | 17052 |  | Real part of Current Negative Sequence | int16 | R | 1
| 0x429D |  | 17053 |  | Imag part of Current Negative Sequence | int16 | R | 1
| 0x429E |  | 17054 |  | Real part of Current Zero Sequence | int16 | R | 1
| 0x429F |  | 17055 |  | Imag part of Current Zero Sequence | int16 | R | 1
Phase Angle
| 0x42A0 |  | 17056 |  | Phase Angle of V2 to V1 | word | R | 1
| 0x42A1 |  | 17057 |  | Phase Angle of V3 to V1 | word | R | 1
| 0x42A2 |  | 17058 |  | Phase Angle of I1 to V1 | word | R | 1
| 0x42A3 |  | 17059 |  | Phase Angle of I2 to V1 | word | R | 1
| 0x42A4 |  | 17060 |  | Phase Angle of I3 to V1 | word | R | 1
| 0x42A5 |  | 17061 |  | Phase Angle of V1 to V1 | word | R | 1
Harmonics - individual（3S）
| 0x4500 | 0x451F | 17664 | 17695 | V1(V12) 32nd - 63rd harmonic | word | R | 32
| 0x4520 | 0x453F | 17696 | 17727 | V2(V31) 32nd - 63rd harmonic | word | R | 32
| 0x4540 | 0x455F | 17728 | 17759 | V3(V23) 32nd - 63rd harmonic | word | R | 32
| 0x4560 | 0x457F | 17760 | 17791 | I1 32nd - 63rd harmonic | word | R | 32
| 0x4580 | 0x459F | 17792 | 17823 | I2 32nd - 63rd harmonic | word | R | 32
| 0x45A0 | 0x45BF | 17824 | 17855 | I3 32nd - 63rd harmonic | word | R | 32
Load percentage
| 0x45F0 | 0x45F1 | 17904 | 17905 | Load percentage | float32 | R | 2
Current demand
| 0x4600 | 0x4601 | 17920 | 17921 | Ia demand | float32 | R | 2
| 0x4602 | 0x4603 | 17922 | 17923 | Ib demand | float32 | R | 2
| 0x4604 | 0x4605 | 17924 | 17925 | Ic demand | float32 | R | 2
Energy - continue（1S）
| 0x4620 | 0x4621 | 17952 | 17953 | Epa_imp Phase A import active energy | uint32 | R/W | 2
| 0x4622 | 0x4623 | 17954 | 17955 | Epa_exp Phase A expot active energy | uint32 | R/W | 2
| 0x4624 | 0x4625 | 17956 | 17957 | Epb_imp Phase B import active energy | uint32 | R/W | 2
| 0x4626 | 0x4627 | 17958 | 17959 | Epb_exp Phase B expot active energy | uint32 | R/W | 2
| 0x4628 | 0x4629 | 17960 | 17961 | Epc_imp Phase C import active energy | uint32 | R/W | 2
| 0x462A | 0x462B | 17962 | 17963 | Epc_exp Phase C expot active energy | uint32 | R/W | 2
| 0x462C | 0x462D | 17964 | 17965 | Eqa_imp Phase A import reactive energy | uint32 | R/W | 2
| 0x462E | 0x462F | 17966 | 17967 | Eqa_exp Phase A expot reactive energy | uint32 | R/W | 2
| 0x4630 | 0x4631 | 17968 | 17969 | Eqb_imp Phase B import reactive energy | uint32 | R/W | 2
| 0x4632 | 0x4633 | 17970 | 17971 | Eqb_exp Phase B expot reactive energy | uint32 | R/W | 2
| 0x4634 | 0x4635 | 17972 | 17973 | Eqc_imp Phase C import reactive energy | uint32 | R/W | 2
| 0x4636 | 0x4637 | 17974 | 17975 | Eqc_exp Phase C expot reactive energy | uint32 | R/W | 2
| 0x4638 | 0x4639 | 17976 | 17977 | Esa Phase A Apparent energy | uint32 | R/W | 2
| 0x463A | 0x463B | 17978 | 17979 | Esb Phase B Apparent energy | uint32 | R/W | 2
| 0x463C | 0x463D | 17980 | 17981 | Esc Phase C Apparent energy | uint32 | R/W | 2
Import/Export Apparent Energy
| 0x4900 | 0x4901 | 18688 | 18689 | Es_imp Import apparent energy | uint32 | R/W | 2
| 0x4902 | 0x4903 | 18690 | 18691 | Esa_imp Phase A import apparent energy | uint32 | R/W | 2
| 0x4904 | 0x4905 | 18692 | 18693 | Esb_imp Phase B import apparent energy | uint32 | R/W | 2
| 0x4906 | 0x4907 | 18694 | 18695 | Esc_imp Phase C import apparent energy | uint32 | R/W | 2
| 0x4908 | 0x4909 | 18696 | 18697 | Es_exp Export apparent energy | uint32 | R/W | 2
| 0x490A | 0x490B | 18698 | 18699 | Esa_exp Phase A export apparent energy | uint32 | R/W | 2
| 0x490C | 0x490D | 18700 | 18701 | Esb_exp Phase B export apparent energy | uint32 | R/W | 2
| 0x490E | 0x490F | 18702 | 18703 | Esc_exp Phase C export apparent energy | uint32 | R/W | 2
Four-quadrant reactive energy
| 0x4910 | 0x4911 | 18704 | 18705 | Reactive energy-Q1 | uint32 | R/W | 2
| 0x4912 | 0x4913 | 18706 | 18707 | Phase A reactive energy-Q1 | uint32 | R/W | 2
| 0x4914 | 0x4915 | 18708 | 18709 | Phase B reactive energy-Q1 | uint32 | R/W | 2
| 0x4916 | 0x4917 | 18710 | 18711 | Phase C reactive energy-Q1 | uint32 | R/W | 2
| 0x4918 | 0x4919 | 18712 | 18713 | Reactive energy-Q2 | uint32 | R/W | 2
| 0x491A | 0x491B | 18714 | 18715 | Phase A reactive energy-Q2 | uint32 | R/W | 2
| 0x491C | 0x491D | 18716 | 18717 | B phase reactive energy-Q2 | uint32 | R/W | 2
| 0x491E | 0x491F | 18718 | 18719 | Phase B reactive energy-Q2 | uint32 | R/W | 2
| 0x4920 | 0x4921 | 18720 | 18721 | Reactive energy-Q3 | uint32 | R/W | 2
| 0x4922 | 0x4923 | 18722 | 18723 | Phase A reactive energy-Q3 | uint32 | R/W | 2
| 0x4924 | 0x4925 | 18724 | 18725 | Phase B reactive energy-Q3 | uint32 | R/W | 2
| 0x4926 | 0x4927 | 18726 | 18727 | Phase C reactive energy-Q3 | uint32 | R/W | 2
| 0x4928 | 0x4929 | 18728 | 18729 | Reactive energy-Q4 | uint32 | R/W | 2
| 0x492A | 0x492B | 18730 | 18731 | Phase A reactive energy-Q4 | uint32 | R/W | 2
| 0x492C | 0x492D | 18732 | 18733 | Phase B reactive energy-Q4 | uint32 | R/W | 2
| 0x492E | 0x492F | 18734 | 18735 | Phase C reactive energy-Q4 | uint32 | R/W | 2
Moving Average Parameters
for 1 Cycle RMS | 0x493D | 0x493E | 18749 | 18750 | V1 | float32 | R | 2
| 0x493F | 0x4940 | 18751 | 18752 | V2 | float32 | R | 2
| 0x4941 | 0x4942 | 18753 | 18754 | V3 | float32 | R | 2
| 0x4943 | 0x4944 | 18755 | 18756 | V12 | float32 | R | 2
| 0x4945 | 0x4946 | 18757 | 18758 | V23 | float32 | R | 2
| 0x4947 | 0x4948 | 18759 | 18760 | V31 | float32 | R | 2
| 0x4949 | 0x494A | 18761 | 18762 | I1 | float32 | R | 2
| 0x494B | 0x494C | 18763 | 18764 | I2 | float32 | R | 2
| 0x494D | 0x494E | 18765 | 18766 | I3 | float32 | R | 2
| 0x494F | 0x4950 | 18767 | 18768 | In | float32 | R | 2
| 0x4951 | 0x4952 | 18769 | 18770 | P, phase A | float32 | R | 2
| 0x4953 | 0x4954 | 18771 | 18772 | P, phase B | float32 | R | 2
| 0x4955 | 0x4956 | 18773 | 18774 | P, phase C | float32 | R | 2
| 0x4957 | 0x4958 | 18775 | 18776 | S, phase A | float32 | R | 2
| 0x4959 | 0x495A | 18777 | 18778 | S, phase B | float32 | R | 2
| 0x495B | 0x495C | 18779 | 18780 | S, phase C | float32 | R | 2
| 0x495D | 0x495E | 18781 | 18782 | P, system | float32 | R | 2
| 0x495F | 0x4960 | 18783 | 18784 | Residual Current | float32 | R | 2 |  | 0
36
Accumulated Energy （1S）
| 0x4980 | 0x4985 | 18816 | 18821 | Energy accumulated start time | uint16 | R | 6
| 0x4986 | 0x498B | 18822 | 18827 | Energy accumulated end time | uint16 | R | 6
| 0x498C | 0x498D | 18828 | 18829 | Ep_imp Import active energy | uint32 | R | 2
| 0x498E | 0x498F | 18830 | 18831 | Ep_exp Expot active energy | uint32 | R | 2
| 0x4990 | 0x4991 | 18832 | 18833 | Eq_imp Import reactive energy | uint32 | R | 2
| 0x4992 | 0x4993 | 18834 | 18835 | Eq_exp Expot reactive energy | uint32 | R | 2
| 0x4994 | 0x4995 | 18836 | 18837 | Ep_total Total active energy | uint32 | R | 2
| 0x4996 | 0x4997 | 18838 | 18839 | Ep_net Net active energy | int32 | R | 2
| 0x4998 | 0x4999 | 18840 | 18841 | Eq_total Total reactive energy | uint32 | R | 2
| 0x499A | 0x499B | 18842 | 18843 | Eq_net Net reactive energy | int32 | R | 2
| 0x499C | 0x499D | 18844 | 18845 | Es Apparent energy | uint32 | R | 2
30
Harmonic - amplitude and phase angle
Values in secondary side | 0x6E00 | 0x6E3D | 28160 | 28221 | V1 or V12 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 | Actual voltage U = reading data / 10
| 0x6E3E | 0x6E7B | 28222 | 28283 | V2 or V23 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6E7C | 0x6EB9 | 28284 | 28345 | V3 or V31 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 |  | 0 | 0
| 0x6EBA | 0x6EF7 | 28346 | 28407 | I1 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 | Actual current I = reading data / 1000
| 0x6EF8 | 0x6F35 | 28408 | 28469 | I2 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6F36 | 0x6F73 | 28470 | 28531 | I3 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6F74 | 0x6FB1 | 28532 | 28593 | V1 or V12 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62 | Actual phase angle = reading data / 10
| 0x6FB2 | 0x6FEF | 28594 | 28655 | V2 or V23 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x6FF0 | 0x702D | 28656 | 28717 | V3 or V31 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x702E | 0x706B | 28718 | 28779 | I1 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x706C | 0x70A9 | 28780 | 28841 | I2 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x70AA | 0x70E7 | 28842 | 28903 | I3 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62

## Acuvim-L Parameters
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default Value | Factory Default
Basic Readings (word)
| 0x2000 |  | 8192 |  | Freq | int16 | R | 1 | 4500～6500
| 0x2001 |  | 8193 |  | Va | int16 | R | 1 | 0～65535
| 0x2002 |  | 8194 |  | Vb | int16 | R | 1 | 0～65535
| 0x2003 |  | 8195 |  | Vc | int16 | R | 1 | 0～65535
| 0x2004 |  | 8196 |  | Vlnagv | int16 | R | 1 | 0～65535
| 0x2005 |  | 8197 |  | Vab | int16 | R | 1 | 0～65535
| 0x2006 |  | 8198 |  | Vbc | int16 | R | 1 | 0～65535
| 0x2007 |  | 8199 |  | Vca | int16 | R | 1 | 0～65535
| 0x2008 |  | 8200 |  | Vllavg | int16 | R | 1 | 0～65535
| 0x2009 |  | 8201 |  | Ia | int16 | R | 1 | 0～65535
| 0x200A |  | 8202 |  | Ib | int16 | R | 1 | 0～65535
| 0x200B |  | 8203 |  | Ic | int16 | R | 1 | 0～65535
| 0x200C |  | 8204 |  | In_calc | int16 | R | 1 | 0～65535
| 0x200D |  | 8205 |  | In_measure | int16 | R | 1 | 0～65535
| 0x200E |  | 8206 |  | Itotal | int16 | R | 1 | 0～65535
| 0x200F |  | 8207 |  | Iavg | int16 | R | 1 | 0～65535
| 0x2010 |  | 8208 |  | Pa | int16 | R | 1 | -32768～32767
| 0x2011 |  | 8209 |  | Pb | int16 | R | 1 | -32768～32767
| 0x2012 |  | 8210 |  | Pc | int16 | R | 1 | -32768～32767
| 0x2013 |  | 8211 |  | P | int16 | R | 1 | -32768～32767
| 0x2014 |  | 8212 |  | Qa | int16 | R | 1 | -32768～32767
| 0x2015 |  | 8213 |  | Qb | int16 | R | 1 | -32768～32767
| 0x2016 |  | 8214 |  | Qc | int16 | R | 1 | -32768～32767
| 0x2017 |  | 8215 |  | Q | int16 | R | 1 | -32768～32767
| 0x2018 |  | 8216 |  | Sa | int16 | R | 1 | 0～65535
| 0x2019 |  | 8217 |  | Sb | int16 | R | 1 | 0～65535
| 0x201A |  | 8218 |  | Sc | int16 | R | 1 | 0～65535
| 0x201B |  | 8219 |  | S | int16 | R | 1 | 0～65535
| 0x201C |  | 8220 |  | PFa | int16 | R | 1 | -1000～1000
| 0x201D |  | 8221 |  | PFb | int16 | R | 1 | -1000～1000
| 0x201E |  | 8222 |  | PFc | int16 | R | 1 | -1000～1000
| 0x201F |  | 8223 |  | PF | int16 | R | 1 | -1000～1000
| 0x2020 |  | 8224 |  | U_unbl | int16 | R | 1 | 0～1000
| 0x2021 |  | 8225 |  | I_unbl | int16 | R | 1 | 0～1000
| 0x2022 |  | 8226 |  | LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2023 |  | 8227 |  | P demand | int16 | R | 1 | -32768～32767
| 0x2024 |  | 8228 |  | Q Demand | int16 | R | 1 | -32768～32767
| 0x2025 |  | 8229 |  | S Demand | int16 | R | 1 | 0～65535
| 0x2026 |  | 8230 |  | Ia Demand | int16 | R | 1 | 0～65535
| 0x2027 |  | 8231 |  | Ib Demand | int16 | R | 1 | 0～65535
| 0x2028 |  | 8232 |  | Ic Demand | int16 | R | 1 | 0～65535
| 0x2029 |  | 8233 |  | In Demand | int16 | R | 1 | 0～65535
Energy
| 0x2080 | 0x2081 | 8320 | 8321 | Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2082 | 0x2083 | 8322 | 8323 | Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x2084 | 0x2085 | 8324 | 8325 | Ep_total | uint32 | R/W | 2 | 0～999999999
| 0x2086 | 0x2087 | 8326 | 8327 | Ep_net | int32 | R/W | 2 | -999999999～999999999
| 0x2088 | 0x2089 | 8328 | 8329 | Ep_q1 | uint32 | R/W | 2 | 0～999999999
| 0x208A | 0x208B | 8330 | 8331 | Ep_q2 | uint32 | R/W | 2 | 0～999999999
| 0x208C | 0x208D | 8332 | 8333 | Ep_q3 | uint32 | R/W | 2 | 0～999999999
| 0x208E | 0x208F | 8334 | 8335 | Ep_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2090 | 0x2091 | 8336 | 8337 | Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2092 | 0x2093 | 8338 | 8339 | Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2094 | 0x2095 | 8340 | 8341 | Eq_total | uint32 | R/W | 2 | 0～999999999
| 0x2096 | 0x2097 | 8342 | 8343 | Eq_net | int32 | R/W | 2 | -999999999～999999999
| 0x2098 | 0x2099 | 8344 | 8345 | Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x209A | 0x209B | 8346 | 8347 | Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x209C | 0x209D | 8348 | 8349 | Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x209E | 0x209F | 8350 | 8351 | Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x20A0 | 0x20A1 | 8352 | 8353 | Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20A2 | 0x20A3 | 8354 | 8355 | ES_exp | uint32 | R/W | 2 | 0～999999999
| 0x20A4 | 0x20A5 | 8356 | 8357 | Es_total | uint32 | R/W | 2 | 0～999999999
| 0x20A6 | 0x20A7 | 8358 | 8359 | Es_net | int32 | R/W | 2 | -999999999～999999999
| 0x20A8 | 0x20A9 | 8360 | 8361 | Es_q1 | uint32 | R/W | 2 | 0～999999999
| 0x20AA | 0x20AB | 8362 | 8363 | Es_q2 | uint32 | R/W | 2 | 0～999999999
| 0x20AC | 0x20AD | 8364 | 8365 | Es_q3 | uint32 | R/W | 2 | 0～999999999
| 0x20AE | 0x20AF | 8366 | 8367 | Es_q4 | uint32 | R/W | 2 | 0～999999999
| 0x20B0 | 0x20B1 | 8368 | 8369 | Phase A Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20B2 | 0x20B3 | 8370 | 8371 | Phase A Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20B4 | 0x20B5 | 8372 | 8373 | Phase B Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20B6 | 0x20B7 | 8374 | 8375 | Phase B Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20B8 | 0x20B9 | 8376 | 8377 | Phase C Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20BA | 0x20BB | 8378 | 8379 | Phase C Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20BC | 0x20BD | 8380 | 8381 | Phase A Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20BE | 0x20BF | 8382 | 8383 | Phase A Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C0 | 0x20C1 | 8384 | 8385 | Phase B Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20C2 | 0x20C3 | 8386 | 8387 | Phase B Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C4 | 0x20C5 | 8388 | 8389 | Phase C Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20C6 | 0x20C7 | 8390 | 8391 | Phase C Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C8 | 0x20C9 | 8392 | 8393 | Phase A Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20CA | 0x20CB | 8394 | 8395 | Phase A Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x20CC | 0x20CD | 8396 | 8397 | Phase B Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20CE | 0x20CF | 8398 | 8399 | Phase B Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x20D0 | 0x20D1 | 8400 | 8401 | Phase C Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20D2 | 0x20D3 | 8402 | 8403 | Phase C Es_exp | uint32 | R/W | 2 | 0～999999999
Basic Readings (Float)
| 0x2180 | 0x2181 | 8576 | 8577 | Freq | float32 | R | 2
| 0x2182 | 0x2183 | 8578 | 8579 | Va | float32 | R | 2
| 0x2184 | 0x2185 | 8580 | 8581 | Vb | float32 | R | 2
| 0x2186 | 0x2187 | 8582 | 8583 | Vc | float32 | R | 2
| 0x2188 | 0x2189 | 8584 | 8585 | Vlnagv | float32 | R | 2
| 0x218A | 0x218B | 8586 | 8587 | Vab | float32 | R | 2
| 0x218C | 0x218D | 8588 | 8589 | Vbc | float32 | R | 2
| 0x218E | 0x218F | 8590 | 8591 | Vca | float32 | R | 2
| 0x2190 | 0x2191 | 8592 | 8593 | Vllavg | float32 | R | 2
| 0x2192 | 0x2193 | 8594 | 8595 | Ia | float32 | R | 2
| 0x2194 | 0x2195 | 8596 | 8597 | Ib | float32 | R | 2
| 0x2196 | 0x2197 | 8598 | 8599 | Ic | float32 | R | 2
| 0x2198 | 0x2199 | 8600 | 8601 | In_calc | float32 | R | 2
| 0x219A | 0x219B | 8602 | 8603 | In_measure | float32 | R | 2
| 0x219C | 0x219D | 8604 | 8605 | Itotal | float32 | R | 2
| 0x219E | 0x219F | 8606 | 8607 | Iavg | float32 | R | 2
| 0x21A0 | 0x21A1 | 8608 | 8609 | Pa | float32 | R | 2
| 0x21A2 | 0x21A3 | 8610 | 8611 | Pb | float32 | R | 2
| 0x21A4 | 0x21A5 | 8612 | 8613 | Pc | float32 | R | 2
| 0x21A6 | 0x21A7 | 8614 | 8615 | P | float32 | R | 2
| 0x21A8 | 0x21A9 | 8616 | 8617 | Qa | float32 | R | 2
| 0x21AA | 0x21AB | 8618 | 8619 | Qb | float32 | R | 2
| 0x21AC | 0x21AD | 8620 | 8621 | Qc | float32 | R | 2
| 0x21AE | 0x21AF | 8622 | 8623 | Q | float32 | R | 2
| 0x21B0 | 0x21B1 | 8624 | 8625 | Sa | float32 | R | 2
| 0x21B2 | 0x21B3 | 8626 | 8627 | Sb | float32 | R | 2
| 0x21B4 | 0x21B5 | 8628 | 8629 | Sc | float32 | R | 2
| 0x21B6 | 0x21B7 | 8630 | 8631 | S | float32 | R | 2
| 0x21B8 | 0x21B9 | 8632 | 8633 | PFa | float32 | R | 2
| 0x21BA | 0x21BB | 8634 | 8635 | PFb | float32 | R | 2
| 0x21BC | 0x21BD | 8636 | 8637 | PFc | float32 | R | 2
| 0x21BE | 0x21BF | 8638 | 8639 | PF | float32 | R | 2
| 0x21C0 | 0x21C1 | 8640 | 8641 | U_unbl | float32 | R | 2
| 0x21C2 | 0x21C3 | 8642 | 8643 | I_unbl | float32 | R | 2
| 0x21C4 | 0x21C5 | 8644 | 8645 | LN (L/C/R) | float32 | R | 2
| 0x21C6 | 0x21C7 | 8646 | 8647 | P demand | float32 | R | 2
| 0x21C8 | 0x21C9 | 8648 | 8649 | Q Demand | float32 | R | 2
| 0x21CA | 0x21CB | 8650 | 8651 | S Demand | float32 | R | 2
| 0x21CC | 0x21CD | 8652 | 8653 | Ia Demand | float32 | R | 2
| 0x21CE | 0x21CF | 8654 | 8655 | Ib Demand | float32 | R | 2
| 0x21D0 | 0x21D1 | 8656 | 8657 | Ic Demand | float32 | R | 2
| 0x21D2 | 0x21D3 | 8658 | 8659 | In Demand | float32 | R | 2
Phase Angle | 0x21D4 | 0x21D5 | 8660 | 8661 | Phase Angle of V2 to V1 | float32 | R | 2
| 0x21D6 | 0x21D7 | 8662 | 8663 | Phase Angle of V3 to V1 | float32 | R | 2
| 0x21D8 | 0x21D9 | 8664 | 8665 | Phase Angle of I1 to V1 | float32 | R | 2
| 0x21DA | 0x21DB | 8666 | 8667 | Phase Angle of I2 to V1 | float32 | R | 2
| 0x21DC | 0x21DD | 8668 | 8669 | Phase Angle of I3 to V1 | float32 | R | 2
Acuvim-LV3 values in primary side | 0x0600 | 0x0601 | 1536 | 1537 | Freq_rms | Float | R | 2
| 0x0602 | 0x0603 | 1538 | 1539 | Ua_rms | Float | R | 2
| 0x0604 | 0x0605 | 1540 | 1541 | Ub_rms | Float | R | 2
| 0x0606 | 0x0607 | 1542 | 1543 | Uc_rms | Float | R | 2
| 0x0608 | 0x0609 | 1544 | 1545 | Uab_rms | Float | R | 2
| 0x060A | 0x060B | 1546 | 1547 | Ubc_rms | Float | R | 2
| 0x060C | 0x060D | 1548 | 1549 | Uca_rms | Float | R | 2
| 0x060E | 0x060F | 1550 | 1551 | I a RMS | Float | R | 2
| 0x0610 | 0x0611 | 1552 | 1553 | I b RMS | Float | R | 2
| 0x0612 | 0x0613 | 1554 | 1555 | I c RMS | Float | R | 2
| 0x0614 | 0x0615 | 1556 | 1557 | I n RMS (calculation) | Float | R | 2
| 0x0616 | 0x0617 | 1558 | 1559 | Pa_rms | Float | R | 2
| 0x0618 | 0x0619 | 1560 | 1561 | Pb_rms | Float | R | 2
| 0x061A | 0x061B | 1562 | 1563 | Pc_rms | Float | R | 2
| 0x061C | 0x061D | 1564 | 1565 | P_rms | Float | R | 2
| 0x061E | 0x061F | 1566 | 1567 | Qa_rms | Float | R | 2
| 0x0620 | 0x0621 | 1568 | 1569 | Qb_rms | Float | R | 2
| 0x0622 | 0x0623 | 1570 | 1571 | Qc_rms | Float | R | 2
| 0x0624 | 0x0625 | 1572 | 1573 | Q_rms | Float | R | 2
| 0x0626 | 0x0627 | 1574 | 1575 | S_rms | Float | R | 2
| 0x0628 | 0x0629 | 1576 | 1577 | PFa_rms | Float | R | 2
| 0x062A | 0x062B | 1578 | 1579 | PFb_rms | Float | R | 2
| 0x062C | 0x062D | 1580 | 1581 | PFc_rms | Float | R | 2
| 0x062E | 0x062F | 1582 | 1583 | PF_rms | Float | R | 2
| 0x0630 | 0x0631 | 1584 | 1585 | Unbl_u2 | Float | R | 2
| 0x0632 | 0x0633 | 1586 | 1587 | Unbl_i2 | Float | R | 2
| 0x0634 | 0x0635 | 1588 | 1589 | Spare | Float | R | 2
| 0x0636 | 0x0637 | 1590 | 1591 | Sa_rms | Float | R | 2
| 0x0638 | 0x0639 | 1592 | 1593 | Sb_rms | Float | R | 2
| 0x063A | 0x063B | 1594 | 1595 | Sc_rms | Float | R | 2
| 0x063C | 0x063D | 1596 | 1597 | Spare | Float | R | 2
| 0x063E | 0x063F | 1598 | 1599 | S_dema | Float | R | 2
| 0x0640 | 0x0641 | 1600 | 1601 | P_dema | Float | R | 2
| 0x0642 | 0x0643 | 1602 | 1603 | Q_dema | Float | R | 2
| 0x0644 | 0x0645 | 1604 | 1605 | Ia demand | Float | R | 2
| 0x0646 | 0x0647 | 1606 | 1607 | Ib demand | Float | R | 2
| 0x0648 | 0x0649 | 1608 | 1609 | Ic demand | Float | R | 2
| 0x064A | 0x064B | 1610 | 1611 | Spare | Float | R | 2

## Independent Input Channel
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default Value | Factory Default
Basic Readings (word)
| 0x2400 |  | 9216 |  | Channel 4 Current | int16 | R | 1 | 0～65535
| 0x2401 |  | 9217 |  | Channel 4 Angle | int16 | R | 1 | -1800～1800
| 0x2402 |  | 9218 |  | Channel 4 Active Power | int16 | R | 1 | -32768～32767
| 0x2403 |  | 9219 |  | Channel 4 Reactive Power | int16 | R | 1 | -32768～32767
| 0x2404 |  | 9220 |  | Channel 4 Apparent Power | int16 | R | 1 | 0～65535
| 0x2405 |  | 9221 |  | Channel 4 PF | int16 | R | 1 | -1000～1000
| 0x2406 |  | 9222 |  | Channel 4 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2407 |  | 9223 |  | Channel 4 Current Demand | int16 | R | 1 | 0～65535
| 0x2408 |  | 9224 |  | Summation 2 Iavg | int16 | R | 1 | 0～65535
| 0x2409 |  | 9225 |  | Summation 2 P | int16 | R | 1 | -32768～32767
| 0x240A |  | 9226 |  | Summation 2 Q | int16 | R | 1 | -32768～32767
| 0x240B |  | 9227 |  | Summation 2 S | int16 | R | 1 | 0～65535
| 0x240C |  | 9228 |  | Summation 2 PF | int16 | R | 1 | -1000～1000
| 0x240D |  | 9229 |  | Summation 2 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x240E |  | 9230 |  | Channel 1 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x240F |  | 9231 |  | Channel 2 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2410 |  | 9232 |  | Channel 3 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2411 |  | 9233 |  | Channel 1 P demand | int16 | R | 1 | -32768～32767
| 0x2412 |  | 9234 |  | Channel 2 P Demand | int16 | R | 1 | -32768～32767
| 0x2413 |  | 9235 |  | Channel 3 P Demand | int16 | R | 1 | 0～65535
| 0x2414 |  | 9236 |  | Channel 4 P demand | int16 | R | 1 | -32768～32767
| 0x2415 |  | 9237 |  | Summation 2 P demand | int16 | R | 1 | -32768～32767
| 0x2416 |  | 9238 |  | Channel 1 Q Demand | int16 | R | 1 | -32768～32767
| 0x2417 |  | 9239 |  | Channel 2 Q Demand | int16 | R | 1 | 0～65535
| 0x2418 |  | 9240 |  | Channel 3 Q demand | int16 | R | 1 | -32768～32767
| 0x2419 |  | 9241 |  | Channel 4 Q Demand | int16 | R | 1 | -32768～32767
| 0x241A |  | 9242 |  | Summation 2 Q Demand | int16 | R | 1 | -32768～32767
| 0x241B |  | 9243 |  | Channel 1 S Demand | int16 | R | 1 | 0～65535
| 0x241C |  | 9244 |  | Channel 2 S demand | int16 | R | 1 | -32768～32767
| 0x241D |  | 9245 |  | Channel 3 S Demand | int16 | R | 1 | -32768～32767
| 0x241E |  | 9246 |  | Channel 4 S Demand | int16 | R | 1 | 0～65535
| 0x241F |  | 9247 |  | Summation 2 S Demand | int16 | R | 1 | 0～65535
Energy
| 0x2500 | 0x2501 | 9472 | 9473 | Channel 4 Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2502 | 0x2503 | 9474 | 9475 | Channel 4 Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x2504 | 0x2505 | 9476 | 9477 | Channel 4 Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2506 | 0x2507 | 9478 | 9479 | Channel 4 Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2508 | 0x2509 | 9480 | 9481 | Channel 4 Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x250A | 0x250B | 9482 | 9483 | Channel 4 Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x250C | 0x250D | 9484 | 9485 | Channel 4 Es_total | uint32 | R/W | 2 | 0～999999999
| 0x250E | 0x250F | 9486 | 9487 | Channel 4 Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2510 | 0x2511 | 9488 | 9489 | Channel 4 Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2512 | 0x2513 | 9490 | 9491 | Channel 4 Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2514 | 0x2515 | 9492 | 9493 | Channel 4 Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2516 | 0x2517 | 9494 | 9495 | Summation 2 Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2518 | 0x2519 | 9496 | 9497 | Summation 2 Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x251A | 0x251B | 9498 | 9499 | Summation 2 Ep_total | uint32 | R/W | 2 | 0～999999999
| 0x251C | 0x251D | 9500 | 9501 | Summation 2 Ep_net | int32 | R/W | 2 | -999999999～999999999
| 0x251E | 0x251F | 9502 | 9503 | Summation 2 Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2520 | 0x2521 | 9504 | 9505 | Summation 2 Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2522 | 0x2523 | 9506 | 9507 | Summation 2 Eq_total | uint32 | R/W | 2 | 0～999999999
| 0x2524 | 0x2525 | 9508 | 9509 | Summation 2 Eq_net | int32 | R/W | 2 | -999999999～999999999
| 0x2526 | 0x2527 | 9510 | 9511 | Summation 2 Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x2528 | 0x2529 | 9512 | 9513 | Summation 2 ES_exp | uint32 | R/W | 2 | 0～999999999
| 0x252A | 0x252B | 9514 | 9515 | Summation 2 Es_total | uint32 | R/W | 2 | 0～999999999
| 0x252C | 0x252D | 9516 | 9517 | Summation 2 Es_net | int32 | R/W | 2 | -999999999～999999999
| 0x252E | 0x252F | 9518 | 9519 | Summation 2 Ep_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2530 | 0x2531 | 9520 | 9521 | Summation 2 Ep_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2532 | 0x2533 | 9522 | 9523 | Summation 2 Ep_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2534 | 0x2535 | 9524 | 9525 | Summation 2 Ep_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2536 | 0x2537 | 9526 | 9527 | Summation 2 Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2538 | 0x2539 | 9528 | 9529 | Summation 2 Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x253A | 0x253B | 9530 | 9531 | Summation 2 Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x253C | 0x253D | 9532 | 9533 | Summation 2 Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x253E | 0x253F | 9534 | 9535 | Summation 2 Es_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2540 | 0x2541 | 9536 | 9537 | Summation 2 Es_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2542 | 0x2543 | 9538 | 9539 | Summation 2 Es_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2544 | 0x2545 | 9540 | 9541 | Summation 2 Es_q4 | uint32 | R/W | 2 | 0～999999999
Basic Readings (Float)
| 0x2600 | 0x2601 | 9728 | 9729 | Channel 4 Current | float32 | R | 2
| 0x2602 | 0x2603 | 9730 | 9731 | Channel 4 Angle | float32 | R | 2
| 0x2604 | 0x2605 | 9732 | 9733 | Channel 4 Active Power | float32 | R | 2
| 0x2606 | 0x2607 | 9734 | 9735 | Channel 4 Reactive Power | float32 | R | 2
| 0x2608 | 0x2609 | 9736 | 9737 | Channel 4 Apparent Power | float32 | R | 2
| 0x260A | 0x260B | 9738 | 9739 | Channel 4 PF | float32 | R | 2
| 0x260C | 0x260D | 9740 | 9741 | Channel 4 LN (L/C/R) | float32 | R | 2
| 0x260E | 0x260F | 9742 | 9743 | Channel 4 Current Demand | float32 | R | 2
| 0x2610 | 0x2611 | 9744 | 9745 | Summation 2 Iavg | float32 | R | 2
| 0x2612 | 0x2613 | 9746 | 9747 | Summation 2 P | float32 | R | 2
| 0x2614 | 0x2615 | 9748 | 9749 | Summation 2 Q | float32 | R | 2
| 0x2616 | 0x2617 | 9750 | 9751 | Summation 2 S | float32 | R | 2
| 0x2618 | 0x2619 | 9752 | 9753 | Summation 2 PF | float32 | R | 2
| 0x261A | 0x261B | 9754 | 9755 | Summation 2 LN (L/C/R) | float32 | R | 2
| 0x261C | 0x261D | 9756 | 9757 | Channel 1 LN (L/C/R) | float32 | R | 2
| 0x261E | 0x261F | 9758 | 9759 | Channel 2 LN (L/C/R) | float32 | R | 2
| 0x2620 | 0x2621 | 9760 | 9761 | Channel 3 LN (L/C/R) | float32 | R | 2
| 0x2622 | 0x2623 | 9762 | 9763 | Channel 1 P demand | float32 | R | 2
| 0x2624 | 0x2625 | 9764 | 9765 | Channel 2 P Demand | float32 | R | 2
| 0x2626 | 0x2627 | 9766 | 9767 | Channel 3 P Demand | float32 | R | 2
| 0x2628 | 0x2629 | 9768 | 9769 | Channel 4 P demand | float32 | R | 2
| 0x262A | 0x262B | 9770 | 9771 | Summation 2 P demand | float32 | R | 2
| 0x262C | 0x262D | 9772 | 9773 | Channel 1 Q Demand | float32 | R | 2
| 0x262E | 0x262F | 9774 | 9775 | Channel 2 Q Demand | float32 | R | 2
| 0x2630 | 0x2631 | 9776 | 9777 | Channel 3 Q demand | float32 | R | 2
| 0x2632 | 0x2633 | 9778 | 9779 | Channel 4 Q Demand | float32 | R | 2
| 0x2634 | 0x2635 | 9780 | 9781 | Summation 2 Q Demand | float32 | R | 2
| 0x2636 | 0x2637 | 9782 | 9783 | Channel 1 S Demand | float32 | R | 2
| 0x2638 | 0x2639 | 9784 | 9785 | Channel 2 S demand | float32 | R | 2
| 0x263A | 0x263B | 9786 | 9787 | Channel 3 S Demand | float32 | R | 2
| 0x263C | 0x263D | 9788 | 9789 | Channel 4 S Demand | float32 | R | 2
| 0x263E | 0x263F | 9790 | 9791 | Summation 2 S Demand | float32 | R | 2
Harmonics（3S）
| 0x5220 |  | 21024 |  | Channel 4 current THD | int16 | R | 1
| 0x5221 | 0x523E | 21025 | 21054 | Channel 4 current 2nd-31st harmonic | int16 | R | 30
| 0x523F |  | 21055 |  | Channel 4 current odd THD | int16 | R | 1
| 0x5240 |  | 21056 |  | Channel 4 current even THD | int16 | R | 1
| 0x5241 |  | 21057 |  | Channel 4 current K factor | int16 | R | 1
| 0x5242 | 0x5261 | 21058 | 21089 | Channel 4 current 32nd-63rd harmonic | int16 | R | 32
Harmonic amplitude and phase angle (secondary side)
| 0x5262 | 0x529F | 21090 | 21151 | Channel 4 current harmonic amplitude (2nd - 63st) | int16 | R | 62 | Actual current I = reading data / 1000
| 0x52A0 | 0x52DD | 21152 | 21213 | Channel 4 current Harmonic phase angle (2nd - 63rd） | int16 | R | 62 | Actual phase angle = reading data / 10

## Dual Source Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Dual Source Energy Settings
| 0x1680 | 0x1680 | 5760 | 5760 | Dual source energy enable/disable | word | R/W | 1 | 0: Disabled; 1: Enabled | 0 | 0
| 0x1681 | 0x1681 | 5761 | 5761 | Energy 1 selection | word | R/W | 1 | 0: Not selected 1: Active energy 2: Phase A active energy 3: Phase B active energy 4: Phase C active energy 5: Reactive energy 6: Phase A reactive energy 7: Phase B reactive energy 8: Phase C reactive energy 9: Apparent energy 10: Phase A apparent energy 11: Phase B apparent energy 12: Phase C apparent energy | 0 | 0
| 0x1682 | 0x1682 | 5762 | 5762 | Energy 2 selection | word | R/W | 1 |  | 0 | 0
| 0x1683 | 0x1683 | 5763 | 5763 | Energy 3 selection | word | R/W | 1 |  | 0 | 0
| 0x1684 | 0x1684 | 5764 | 5764 | Control mode | word | R/W | 1 | 0: Controlled by communication 1 ~ 28: Controlled by DI1-DI28 | 0 | 0
| 0x1685 | 0x1685 | 5765 | 5765 | Direction flag | word | R/W | 1 | When control mode is controlled by commnication, the value is writeable via communication; when control mode is controlled by DI, the value is readonly. 0: grid direction; 1: generator direction. | 0 | 0
| 0x1686 | 0x1686 | 5766 | 5766 | clear Dual Source energy | word | R/W | 1 | write 1 to clear | 0 | 0
| 0x1687 | 0x1687 | 5767 | 5767 | clear Dual Source energy switching record | word | R/W | 1 | write 1 to clear | 0 | 0
Dual Source Energy Readings
| 0x4930 | 0x4931 | 18736 | 18737 | Energy 1 - Grid Direction | uint32 | R | 2
| 0x4932 | 0x4933 | 18738 | 18739 | Energy 1 - Generator Direction | uint32 | R | 2
| 0x4934 | 0x4935 | 18740 | 18741 | Energy 2 - Grid Direction | uint32 | R | 2
| 0x4936 | 0x4937 | 18742 | 18743 | Energy 2 - Generator Direction | uint32 | R | 2
| 0x4938 | 0x4939 | 18744 | 18745 | Energy 3 - Grid Direction | uint32 | R | 2
| 0x493A | 0x493B | 18746 | 18747 | Energy 3 - Generator Direction | uint32 | R | 2
Dual Source Energy switching records
| 0x6D00 | 0x6D00 | 27904 | 27904 | the number of records to read | word | R/W | 1 | 1 to 20 | 0 | 0
| 0x6D01 | 0x6D01 | 27905 | 27905 | The ID of current switching record | word | R | 1 | 0 to 20 | 0 | 0
| 0x6D02 | 0x6D02 | 27906 | 27906 | The length of bytes that can be read by the current window | word | R | 1 | 0 to 85; 0: the window data is invalid. | 0 | 0
| 0x6D03 | 0x6D03 | 27907 | 27907 | 1st switch record - timestamp year&month | word | R | 1 | High byte: year Low byte: month
| 0x6D04 | 0x6D04 | 27908 | 27908 | 1st switch record - timestamp date&hour | word | R | 1 | High byte: date Low byte: hour
| 0x6D05 | 0x6D05 | 27909 | 27909 | 1st switch record - timestamp minute&second | word | R | 1 | High byte: minute Low byte: second
| 0x6D06 | 0x6D06 | 27910 | 27910 | 1st switch record - switch command source | word | R | 1 | 0: Controlled by communication 1 ~ 28: Controlled by DI1-DI28
| 0x6D07 | 0x6D07 | 27911 | 27911 | 1st switch record - switch command | word | R | 1 | 0: grid direction, 1: generator direction
| 0x6D08 | 0x6D09 | 27912 | 27913 | 1st Switch Record - Energy 1 - Grid Direction | word | R | 2
| 0x6D0A | 0x6D0B | 27914 | 27915 | 1st Switch Record - Energy 1 - Generator Direction | word | R | 2
| 0x6D0C | 0x6D0D | 27916 | 27917 | 1st Switch Record - Energy 2 - Grid Direction | word | R | 2
| 0x6D0E | 0x6D0F | 27918 | 27919 | 1st Switch Record - Energy 2 - Generator Direction | word | R | 2
| 0x6D10 | 0x6D11 | 27920 | 27921 | 1st Switch Record - Energy 3 - Grid Direction | word | R | 2
| 0x6D12 | 0x6D13 | 27922 | 27923 | 1st Switch Record - Energy 3 - Generator Direction | word | R | 2
| 0x6D14 | 0x6D24 | 27924 | 27940 | 2nd switch record data | word | R | 17
| 0x6D25 | 0x6D35 | 27941 | 27957 | 3rd switch record data | word | R | 17
| 0x6D36 | 0x6D46 | 27958 | 27974 | 4th switch record data | word | R | 17
| 0x6D47 | 0x6D57 | 27975 | 27991 | 5th switch record data | word | R | 17

## Max,Min
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Max value record
| 0x4136 |  | 16694 |  | Max of V1 | int16 | R | 1
| 0x4137 | 0x413C | 16695 | 16700 | Time Stamp | int16 | R | 6
| 0x413D |  | 16701 |  | Max of V2 | int16 | R | 1
| 0x413E | 0x4143 | 16702 | 16707 | Time Stamp | int16 | R | 6
| 0x4144 |  | 16708 |  | Max of V3 | int16 | R | 1
| 0x4145 | 0x414A | 16709 | 16714 | Time Stamp | int16 | R | 6
| 0x414B |  | 16715 |  | Max of V12 | int16 | R | 1
| 0x414C | 0x4151 | 16716 | 16721 | Time Stamp | int16 | R | 6
| 0x4152 |  | 16722 |  | Max of V23 | int16 | R | 1
| 0x4153 | 0x4158 | 16723 | 16728 | Time Stamp | int16 | R | 6
| 0x4159 |  | 16729 |  | Max of V31 | int16 | R | 1
| 0x415A | 0x415F | 16730 | 16735 | Time Stamp | int16 | R | 6
| 0x4160 |  | 16736 |  | Max of I1 | int16 | R | 1
| 0x4161 | 0x4166 | 16737 | 16742 | Time Stamp | int16 | R | 6
| 0x4167 |  | 16743 |  | Max of I2 | int16 | R | 1
| 0x4168 | 0x416D | 16744 | 16749 | Time Stamp | int16 | R | 6
| 0x416E |  | 16750 |  | Max of I3 | int16 | R | 1
| 0x416F | 0x4174 | 16751 | 16756 | Time Stamp | int16 | R | 6
| 0x4175 |  | 16757 |  | Max of System Power | int16 | R | 1
| 0x4176 | 0x417B | 16758 | 16763 | Time Stamp | int16 | R | 6
| 0x417C |  | 16764 |  | Max of Reactive Power | int16 | R | 1
| 0x417D | 0x4182 | 16765 | 16770 | Time Stamp | int16 | R | 6
| 0x4183 |  | 16771 |  | Max of Apparent Power | int16 | R | 1
| 0x4184 | 0x4189 | 16772 | 16777 | Time Stamp | int16 | R | 6
| 0x418A |  | 16778 |  | Max of Power Factor | int16 | R | 1
| 0x418B | 0x4190 | 16779 | 16784 | Time Stamp | int16 | R | 6
| 0x4191 |  | 16785 |  | Max of Frequency | int16 | R | 1
| 0x4192 | 0x4197 | 16786 | 16791 | Time Stamp | int16 | R | 6
| 0x4198 |  | 16792 |  | Max of Power Demand | int16 | R | 1
| 0x4199 | 0x419E | 16793 | 16798 | Time Stamp | int16 | R | 6
| 0x419F |  | 16799 |  | Max of Reactive power demand | int16 | R | 1
| 0x41A0 | 0x41A5 | 16800 | 16805 | Time Stamp | int16 | R | 6
| 0x41A6 |  | 16806 |  | Max of Apparent power demand | int16 | R | 1
| 0x41A7 | 0x41AC | 16807 | 16812 | Time Stamp | int16 | R | 6
| 0x41AD |  | 16813 |  | Max of Voltage unbalance | int16 | R | 1
| 0x41AE | 0x41B3 | 16814 | 16819 | Time Stamp | int16 | R | 6
| 0x41B4 |  | 16820 |  | Max of Current unbalance | int16 | R | 1
| 0x41B5 | 0x41BA | 16821 | 16826 | Time Stamp | int16 | R | 6
| 0x41BB |  | 16827 |  | Max of THD_V1(V12) | int16 | R | 1
| 0x41BC | 0x41C1 | 16828 | 16833 | Time Stamp | int16 | R | 6
| 0x41C2 |  | 16834 |  | Max of THD_V2(V31) | int16 | R | 1
| 0x41C3 | 0x41C8 | 16835 | 16840 | Time Stamp | int16 | R | 6
| 0x41C9 |  | 16841 |  | Max of THD_V3(V23) | int16 | R | 1
| 0x41CA | 0x41CF | 16842 | 16847 | Time Stamp | int16 | R | 6
| 0x41D0 |  | 16848 |  | Max of THD_I1 | int16 | R | 1
| 0x41D1 | 0x41D6 | 16849 | 16854 | Time Stamp | int16 | R | 6
| 0x41D7 |  | 16855 |  | Max of THD_I2 | int16 | R | 1
| 0x41D8 | 0x41DD | 16856 | 16861 | Time Stamp | int16 | R | 6
| 0x41DE |  | 16862 |  | Max of THD_I3 | int16 | R | 1
| 0x41DF | 0x41E4 | 16863 | 16868 | Time Stamp | int16 | R | 6
Min value record
| 0x41E5 |  | 16869 |  | Min of V1 | int16 | R | 1
| 0x41E6 | 0x41EB | 16870 | 16875 | Time Stamp | int16 | R | 6
| 0x41EC |  | 16876 |  | Min of V2 | int16 | R | 1
| 0x41ED | 0x41F2 | 16877 | 16882 | Time Stamp | int16 | R | 6
| 0x41F3 |  | 16883 |  | Min of V3 | int16 | R | 1
| 0x41F4 | 0x41F9 | 16884 | 16889 | Time Stamp | int16 | R | 6
| 0x41FA |  | 16890 |  | Min of V12 | int16 | R | 1
| 0x41FB | 0x4200 | 16891 | 16896 | Time Stamp | int16 | R | 6
| 0x4201 |  | 16897 |  | Min of V23 | int16 | R | 1
| 0x4202 | 0x4207 | 16898 | 16903 | Time Stamp | int16 | R | 6
| 0x4208 |  | 16904 |  | Min of V31 | int16 | R | 1
| 0x4209 | 0x420E | 16905 | 16910 | Time Stamp | int16 | R | 6
| 0x420F |  | 16911 |  | Min of I1 | int16 | R | 1
| 0x4210 | 0x4215 | 16912 | 16917 | Time Stamp | int16 | R | 6
| 0x4216 |  | 16918 |  | Min of I2 | int16 | R | 1
| 0x4217 | 0x421C | 16919 | 16924 | Time Stamp | int16 | R | 6
| 0x421D |  | 16925 |  | Min of I3 | int16 | R | 1
| 0x421E | 0x4223 | 16926 | 16931 | Time Stamp | int16 | R | 6
| 0x4224 |  | 16932 |  | Min of System Power | int16 | R | 1
| 0x4225 | 0x422A | 16933 | 16938 | Time Stamp | int16 | R | 6
| 0x422B |  | 16939 |  | Min of Reactive Power | int16 | R | 1
| 0x422C | 0x4231 | 16940 | 16945 | Time Stamp | int16 | R | 6
| 0x4232 |  | 16946 |  | Min of Apparent Power | int16 | R | 1
| 0x4233 | 0x4238 | 16947 | 16952 | Time Stamp | int16 | R | 6
| 0x4239 |  | 16953 |  | Min of Power Factor | int16 | R | 1
| 0x423A | 0x423F | 16954 | 16959 | Time Stamp | int16 | R | 6
| 0x4240 |  | 16960 |  | Min of Frequency | int16 | R | 1
| 0x4241 | 0x4246 | 16961 | 16966 | Time Stamp | int16 | R | 6
| 0x4247 |  | 16967 |  | Min of Power Demand | int16 | R | 1
| 0x4248 | 0x424D | 16968 | 16973 | Time Stamp | int16 | R | 6
| 0x424E |  | 16974 |  | Min of Reactive power demand | int16 | R | 1
| 0x424F | 0x4254 | 16975 | 16980 | Time Stamp | int16 | R | 6
| 0x4255 |  | 16981 |  | Min of Apparent power demand | int16 | R | 1
| 0x4256 | 0x425B | 16982 | 16987 | Time Stamp | int16 | R | 6
| 0x425C |  | 16988 |  | Min of Voltage unbalance | int16 | R | 1
| 0x425D | 0x4262 | 16989 | 16994 | Time Stamp | int16 | R | 6
| 0x4263 |  | 16995 |  | Min of Current unbalance | int16 | R | 1
| 0x4264 | 0x4269 | 16996 | 17001 | Time Stamp | int16 | R | 6
| 0x426A |  | 17002 |  | Min of THD_V1(V12) | int16 | R | 1
| 0x426B | 0x4270 | 17003 | 17008 | Time Stamp | int16 | R | 6
| 0x4271 |  | 17009 |  | Min of THD_V2(V31) | int16 | R | 1
| 0x4272 | 0x4277 | 17010 | 17015 | Time Stamp | int16 | R | 6
| 0x4278 |  | 17016 |  | Min of THD_V3(V23) | int16 | R | 1
| 0x4279 | 0x427E | 17017 | 17022 | Time Stamp | int16 | R | 6
| 0x427F |  | 17023 |  | Min of THD_I1 | int16 | R | 1
| 0x4280 | 0x4285 | 17024 | 17029 | Time Stamp | int16 | R | 6
| 0x4286 |  | 17030 |  | Min of THD_I2 | int16 | R | 1
| 0x4287 | 0x428C | 17031 | 17036 | Time Stamp | int16 | R | 6
| 0x428D |  | 17037 |  | Min of THD_I3 | int16 | R | 1
| 0x428E | 0x4293 | 17038 | 17043 | Time Stamp | int16 | R | 6
| 0x4606 |  | 17926 |  | Max of Phase A current demand | int16 | R | 1
| 0x4607 | 0x460C | 17927 | 17932 | Time Stamp | int16 | R | 6
| 0x460D |  | 17933 | 17933 | Max of Phase B current demand | int16 | R | 1
| 0x460E | 0x4613 | 17934 | 17939 | Time Stamp | int16 | R | 6
| 0x4614 |  | 17940 | 17940 | Max of Phase C current demand | int16 | R | 1
| 0x4615 | 0x461A | 17941 | 17946 | Time Stamp | int16 | R | 6

## Max,Min(float)
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Max value record
| 0x5000 |  | 20480 |  | Max of V1 | float32 | R | 2
| 0x5002 | 0x5007 | 20482 | 20487 | Time Stamp | int16 | R | 6
| 0x5008 |  | 20488 |  | Max of V2 | float32 | R | 2
| 0x500A | 0x500F | 20490 | 20495 | Time Stamp | int16 | R | 6
| 0x5010 |  | 20496 |  | Max of V3 | float32 | R | 2
| 0x5012 | 0x5017 | 20498 | 20503 | Time Stamp | int16 | R | 6
| 0x5018 |  | 20504 |  | Max of V12 | float32 | R | 2
| 0x501A | 0x501F | 20506 | 20511 | Time Stamp | int16 | R | 6
| 0x5020 |  | 20512 |  | Max of V23 | float32 | R | 2
| 0x5022 | 0x5027 | 20514 | 20519 | Time Stamp | int16 | R | 6
| 0x5028 |  | 20520 |  | Max of V31 | float32 | R | 2
| 0x502A | 0x502F | 20522 | 20527 | Time Stamp | int16 | R | 6
| 0x5030 |  | 20528 |  | Max of I1 | float32 | R | 2
| 0x5032 | 0x5037 | 20530 | 20535 | Time Stamp | int16 | R | 6
| 0x5038 |  | 20536 |  | Max of I2 | float32 | R | 2
| 0x503A | 0x503F | 20538 | 20543 | Time Stamp | int16 | R | 6
| 0x5040 |  | 20544 |  | Max of I3 | float32 | R | 2
| 0x5042 | 0x5047 | 20546 | 20551 | Time Stamp | int16 | R | 6
| 0x5048 |  | 20552 |  | Max of System Power | float32 | R | 2
| 0x504A | 0x504F | 20554 | 20559 | Time Stamp | int16 | R | 6
| 0x5050 |  | 20560 |  | Max of Reactive Power | float32 | R | 2
| 0x5052 | 0x5057 | 20562 | 20567 | Time Stamp | int16 | R | 6
| 0x5058 |  | 20568 |  | Max of Apparent Power | float32 | R | 2
| 0x505A | 0x505F | 20570 | 20575 | Time Stamp | int16 | R | 6
| 0x5060 |  | 20576 |  | Max of Power Factor | float32 | R | 2
| 0x5062 | 0x5067 | 20578 | 20583 | Time Stamp | int16 | R | 6
| 0x5068 |  | 20584 |  | Max of Frequency | float32 | R | 2
| 0x506A | 0x506F | 20586 | 20591 | Time Stamp | int16 | R | 6
| 0x5070 |  | 20592 |  | Max of Power Demand | float32 | R | 2
| 0x5072 | 0x5077 | 20594 | 20599 | Time Stamp | int16 | R | 6
| 0x5078 |  | 20600 |  | Max of Reactive power demand | float32 | R | 2
| 0x507A | 0x507F | 20602 | 20607 | Time Stamp | int16 | R | 6
| 0x5080 |  | 20608 |  | Max of Apparent power demand | float32 | R | 2
| 0x5082 | 0x5087 | 20610 | 20615 | Time Stamp | int16 | R | 6
| 0x5088 |  | 20616 |  | Max of Voltage unbalance | float32 | R | 2
| 0x508A | 0x508F | 20618 | 20623 | Time Stamp | int16 | R | 6
| 0x5090 |  | 20624 |  | Max of Current unbalance | float32 | R | 2
| 0x5092 | 0x5097 | 20626 | 20631 | Time Stamp | int16 | R | 6
| 0x5098 |  | 20632 |  | Max of THD_V1(V12) | float32 | R | 2
| 0x509A | 0x509F | 20634 | 20639 | Time Stamp | int16 | R | 6
| 0x50A0 |  | 20640 |  | Max of THD_V2(V31) | float32 | R | 2
| 0x50A2 | 0x50A7 | 20642 | 20647 | Time Stamp | int16 | R | 6
| 0x50A8 |  | 20648 |  | Max of THD_V3(V23) | float32 | R | 2
| 0x50AA | 0x50AF | 20650 | 20655 | Time Stamp | int16 | R | 6
| 0x50B0 |  | 20656 |  | Max of THD_I1 | float32 | R | 2
| 0x50B2 | 0x50B7 | 20658 | 20663 | Time Stamp | int16 | R | 6
| 0x50B8 |  | 20664 |  | Max of THD_I2 | float32 | R | 2
| 0x50BA | 0x50BF | 20666 | 20671 | Time Stamp | int16 | R | 6
| 0x50C0 |  | 20672 |  | Max of THD_I3 | float32 | R | 2
| 0x50C2 | 0x50C7 | 20674 | 20679 | Time Stamp | int16 | R | 6
| 0x50C8 |  | 20680 |  | Max of Phase A current demand | float32 | R | 2
| 0x50CA | 0x50CF | 20682 | 20687 | Time Stamp | int16 | R | 6
| 0x50D0 |  | 20688 | 20689 | Max of Phase B current demand | float32 | R | 2
| 0x50D2 | 0x50D7 | 20690 | 20695 | Time Stamp | int16 | R | 6
| 0x50D8 |  | 20696 | 20697 | Max of Phase C current demand | float32 | R | 2
| 0x50DA | 0x50DF | 20698 | 20703 | Time Stamp | int16 | R | 6
Min value record
| 0x50E0 |  | 20704 |  | Min of V1 | float32 | R | 2
| 0x50E2 | 0x50E7 | 20706 | 20711 | Time Stamp | int16 | R | 6
| 0x50E8 |  | 20712 |  | Min of V2 | float32 | R | 2
| 0x50EA | 0x50EF | 20714 | 20719 | Time Stamp | int16 | R | 6
| 0x50F0 |  | 20720 |  | Min of V3 | float32 | R | 2
| 0x50F2 | 0x50F7 | 20722 | 20727 | Time Stamp | int16 | R | 6
| 0x50F8 |  | 20728 |  | Min of V12 | float32 | R | 2
| 0x50FA | 0x50FF | 20730 | 20735 | Time Stamp | int16 | R | 6
| 0x5100 |  | 20736 |  | Min of V23 | float32 | R | 2
| 0x5102 | 0x5107 | 20738 | 20743 | Time Stamp | int16 | R | 6
| 0x5108 |  | 20744 |  | Min of V31 | float32 | R | 2
| 0x510A | 0x510F | 20746 | 20751 | Time Stamp | int16 | R | 6
| 0x5110 |  | 20752 |  | Min of I1 | float32 | R | 2
| 0x5112 | 0x5117 | 20754 | 20759 | Time Stamp | int16 | R | 6
| 0x5118 |  | 20760 |  | Min of I2 | float32 | R | 2
| 0x511A | 0x511F | 20762 | 20767 | Time Stamp | int16 | R | 6
| 0x5120 |  | 20768 |  | Min of I3 | float32 | R | 2
| 0x5122 | 0x5127 | 20770 | 20775 | Time Stamp | int16 | R | 6
| 0x5128 |  | 20776 |  | Min of System Power | float32 | R | 2
| 0x512A | 0x512F | 20778 | 20783 | Time Stamp | int16 | R | 6
| 0x5130 |  | 20784 |  | Min of Reactive Power | float32 | R | 2
| 0x5132 | 0x5137 | 20786 | 20791 | Time Stamp | int16 | R | 6
| 0x5138 |  | 20792 |  | Min of Apparent Power | float32 | R | 2
| 0x513A | 0x513F | 20794 | 20799 | Time Stamp | int16 | R | 6
| 0x5140 |  | 20800 |  | Min of Power Factor | float32 | R | 2
| 0x5142 | 0x5147 | 20802 | 20807 | Time Stamp | int16 | R | 6
| 0x5148 |  | 20808 |  | Min of Frequency | float32 | R | 2
| 0x514A | 0x514F | 20810 | 20815 | Time Stamp | int16 | R | 6
| 0x5150 |  | 20816 |  | Min of Power Demand | float32 | R | 2
| 0x5152 | 0x5157 | 20818 | 20823 | Time Stamp | int16 | R | 6
| 0x5158 |  | 20824 |  | Min of Reactive power demand | float32 | R | 2
| 0x515A | 0x515F | 20826 | 20831 | Time Stamp | int16 | R | 6
| 0x5160 |  | 20832 |  | Min of Apparent power demand | float32 | R | 2
| 0x5162 | 0x5167 | 20834 | 20839 | Time Stamp | int16 | R | 6
| 0x5168 |  | 20840 |  | Min of Voltage unbalance | float32 | R | 2
| 0x516A | 0x516F | 20842 | 20847 | Time Stamp | int16 | R | 6
| 0x5170 |  | 20848 |  | Min of Current unbalance | float32 | R | 2
| 0x5172 | 0x5177 | 20850 | 20855 | Time Stamp | int16 | R | 6
| 0x5178 |  | 20856 |  | Min of THD_V1(V12) | float32 | R | 2
| 0x517A | 0x517F | 20858 | 20863 | Time Stamp | int16 | R | 6
| 0x5180 |  | 20864 |  | Min of THD_V2(V31) | float32 | R | 2
| 0x5182 | 0x5187 | 20866 | 20871 | Time Stamp | int16 | R | 6
| 0x5188 |  | 20872 |  | Min of THD_V3(V23) | float32 | R | 2
| 0x518A | 0x518F | 20874 | 20879 | Time Stamp | int16 | R | 6
| 0x5190 |  | 20880 |  | Min of THD_I1 | float32 | R | 2
| 0x5192 | 0x5197 | 20882 | 20887 | Time Stamp | int16 | R | 6
| 0x5198 |  | 20888 |  | Min of THD_I2 | float32 | R | 2
| 0x519A | 0x519F | 20890 | 20895 | Time Stamp | int16 | R | 6
| 0x51A0 |  | 20896 |  | Min of THD_I3 | float32 | R | 2
| 0x51A2 | 0x51A7 | 20898 | 20903 | Time Stamp | int16 | R | 6
| 0x52E0 |  | 21216 |  | Max of Phase A P | float32 | R | 2
| 0x52E2 | 0x52E7 | 21218 | 21223 | Time Stamp | int16 | R | 6
| 0x52E8 |  | 21224 |  | Max of Phase B P | float32 | R | 2
| 0x52EA | 0x52EF | 21226 | 21231 | Time Stamp | int16 | R | 6
| 0x52F0 |  | 21232 |  | Max of Phase C P | float32 | R | 2
| 0x52F2 | 0x52F7 | 21234 | 21239 | Time Stamp | int16 | R | 6
| 0x52F8 |  | 21240 |  | Max of Phase N P | float32 | R | 2
| 0x52FA | 0x52FF | 21242 | 21247 | Time Stamp | int16 | R | 6
| 0x5300 |  | 21248 |  | Max of Phase A Q | float32 | R | 2
| 0x5302 | 0x5307 | 21250 | 21255 | Time Stamp | int16 | R | 6
| 0x5308 |  | 21256 |  | Max of Phase B Q | float32 | R | 2
| 0x530A | 0x530F | 21258 | 21263 | Time Stamp | int16 | R | 6
| 0x5310 |  | 21264 |  | Max of Phase C Q | float32 | R | 2
| 0x5312 | 0x5317 | 21266 | 21271 | Time Stamp | int16 | R | 6
| 0x5318 |  | 21272 |  | Max of Phase N Q | float32 | R | 2
| 0x531A | 0x531F | 21274 | 21279 | Time Stamp | int16 | R | 6
| 0x5320 |  | 21280 |  | Max of Phase A S | float32 | R | 2
| 0x5322 | 0x5327 | 21282 | 21287 | Time Stamp | int16 | R | 6
| 0x5328 |  | 21288 |  | Max of Phase B S | float32 | R | 2
| 0x532A | 0x532F | 21290 | 21295 | Time Stamp | int16 | R | 6
| 0x5330 |  | 21296 |  | Max of Phase C S | float32 | R | 2
| 0x5332 | 0x5337 | 21298 | 21303 | Time Stamp | int16 | R | 6
| 0x5338 |  | 21304 |  | Max of Phase N S | float32 | R | 2
| 0x533A | 0x533F | 21306 | 21311 | Time Stamp | int16 | R | 6
| 0x5340 |  | 21312 |  | Max of Phase A PF | float32 | R | 2
| 0x5342 | 0x5347 | 21314 | 21319 | Time Stamp | int16 | R | 6
| 0x5348 |  | 21320 |  | Max of Phase B PF | float32 | R | 2
| 0x534A | 0x534F | 21322 | 21327 | Time Stamp | int16 | R | 6
| 0x5350 |  | 21328 |  | Max of Phase C PF | float32 | R | 2
| 0x5352 | 0x5357 | 21330 | 21335 | Time Stamp | int16 | R | 6
| 0x5358 |  | 21336 |  | Max of Phase N PF | float32 | R | 2
| 0x535A | 0x535F | 21338 | 21343 | Time Stamp | int16 | R | 6
| 0x5360 |  | 21344 |  | Max of Phase A P demand | float32 | R | 2
| 0x5362 | 0x5367 | 21346 | 21351 | Time Stamp | int16 | R | 6
| 0x5368 |  | 21352 |  | Max of Phase B P Demand | float32 | R | 2
| 0x536A | 0x536F | 21354 | 21359 | Time Stamp | int16 | R | 6
| 0x5370 |  | 21360 |  | Max of Phase C P Demand | float32 | R | 2
| 0x5372 | 0x5377 | 21362 | 21367 | Time Stamp | int16 | R | 6
| 0x5378 |  | 21368 |  | Max of Phase N P Demand | float32 | R | 2
| 0x537A | 0x537F | 21370 | 21375 | Time Stamp | int16 | R | 6
| 0x5380 |  | 21376 |  | Max of Phase A Q demand | float32 | R | 2
| 0x5382 | 0x5387 | 21378 | 21383 | Time Stamp | int16 | R | 6
| 0x5388 |  | 21384 |  | Max of Phase B Q Demand | float32 | R | 2
| 0x538A | 0x538F | 21386 | 21391 | Time Stamp | int16 | R | 6
| 0x5390 |  | 21392 |  | Max of Phase C Q Demand | float32 | R | 2
| 0x5392 | 0x5397 | 21394 | 21399 | Time Stamp | int16 | R | 6
| 0x5398 |  | 21400 |  | Max of Phase N Q demand | float32 | R | 2
| 0x539A | 0x539F | 21402 | 21407 | Time Stamp | int16 | R | 6
| 0x53A0 |  | 21408 |  | Max of Phase A S Demand | float32 | R | 2
| 0x53A2 | 0x53A7 | 21410 | 21415 | Time Stamp | int16 | R | 6
| 0x53A8 |  | 21416 |  | Max of Phase B S Demand | float32 | R | 2
| 0x53AA | 0x53AF | 21418 | 21423 | Time Stamp | int16 | R | 6
| 0x53B0 |  | 21424 |  | Max of Phase C S demand | float32 | R | 2
| 0x53B2 | 0x53B7 | 21426 | 21431 | Time Stamp | int16 | R | 6
| 0x53B8 |  | 21432 |  | Max of Phase N S Demand | float32 | R | 2
| 0x53BA | 0x53BF | 21434 | 21439 | Time Stamp | int16 | R | 6
| 0x53C0 |  | 21440 |  | Max of Phase N I Demand | float32 | R | 2
| 0x53C2 | 0x53C7 | 21442 | 21447 | Time Stamp | int16 | R | 6
| 0x53C8 |  | 21448 |  | Max of Phase N I | float32 | R | 2
| 0x53CA | 0x53CF | 21450 | 21455 | Time Stamp | int16 | R | 6
| 0x53D0 |  | 21456 |  | Max of Summation 2 P | float32 | R | 2
| 0x53D2 | 0x53D7 | 21458 | 21463 | Time Stamp | int16 | R | 6
| 0x53D8 |  | 21464 |  | Max of Summation 2 Q | float32 | R | 2
| 0x53DA | 0x53DF | 21466 | 21471 | Time Stamp | int16 | R | 6
| 0x53E0 |  | 21472 |  | Max of Summation 2 S | float32 | R | 2
| 0x53E2 | 0x53E7 | 21474 | 21479 | Time Stamp | int16 | R | 6
| 0x53E8 |  | 21480 |  | Max of Summation 2 PF | float32 | R | 2
| 0x53EA | 0x53EF | 21482 | 21487 | Time Stamp | int16 | R | 6
| 0x53F0 |  | 21488 |  | Max of Summation 2 P demand | float32 | R | 2
| 0x53F2 | 0x53F7 | 21490 | 21495 | Time Stamp | int16 | R | 6
| 0x53F8 |  | 21496 |  | Max of Summation 2 Q Demand | float32 | R | 2
| 0x53FA | 0x53FF | 21498 | 21503 | Time Stamp | int16 | R | 6
| 0x5400 |  | 21504 |  | Max of Summation 2 S Demand | float32 | R | 2
| 0x5402 | 0x5407 | 21506 | 21511 | Time Stamp | int16 | R | 6
| 0x5408 |  | 21512 |  | Max of Summation 2 I | float32 | R | 2
| 0x540A | 0x540F | 21514 | 21519 | Time Stamp | int16 | R | 6
| 0x5410 |  | 21520 |  | Max of In THD | float32 | R | 2
| 0x5412 | 0x5417 | 21522 | 21527 | Time Stamp | int16 | R | 6
| 0x5418 |  | 21528 |  | Min of Phase A P | float32 | R | 2
| 0x541A | 0x541F | 21530 | 21535 | Time Stamp | int16 | R | 6
| 0x5420 |  | 21536 |  | Min of Phase B P | float32 | R | 2
| 0x5422 | 0x5427 | 21538 | 21543 | Time Stamp | int16 | R | 6
| 0x5428 |  | 21544 |  | Min of Phase C P | float32 | R | 2
| 0x542A | 0x542F | 21546 | 21551 | Time Stamp | int16 | R | 6
| 0x5430 |  | 21552 |  | Min of Phase N P | float32 | R | 2
| 0x5432 | 0x5437 | 21554 | 21559 | Time Stamp | int16 | R | 6
| 0x5438 |  | 21560 |  | Min of Phase A Q | float32 | R | 2
| 0x543A | 0x543F | 21562 | 21567 | Time Stamp | int16 | R | 6
| 0x5440 |  | 21568 |  | Min of Phase B Q | float32 | R | 2
| 0x5442 | 0x5447 | 21570 | 21575 | Time Stamp | int16 | R | 6
| 0x5448 |  | 21576 |  | Min of Phase C Q | float32 | R | 2
| 0x544A | 0x544F | 21578 | 21583 | Time Stamp | int16 | R | 6
| 0x5450 |  | 21584 |  | Min of Phase N Q | float32 | R | 2
| 0x5452 | 0x5457 | 21586 | 21591 | Time Stamp | int16 | R | 6
| 0x5458 |  | 21592 |  | Min of Phase A S | float32 | R | 2
| 0x545A | 0x545F | 21594 | 21599 | Time Stamp | int16 | R | 6
| 0x5460 |  | 21600 |  | Min of Phase B S | float32 | R | 2
| 0x5462 | 0x5467 | 21602 | 21607 | Time Stamp | int16 | R | 6
| 0x5468 |  | 21608 |  | Min of Phase C S | float32 | R | 2
| 0x546A | 0x546F | 21610 | 21615 | Time Stamp | int16 | R | 6
| 0x5470 |  | 21616 |  | Min of Phase N S | float32 | R | 2
| 0x5472 | 0x5477 | 21618 | 21623 | Time Stamp | int16 | R | 6
| 0x5478 |  | 21624 |  | Min of Phase A PF | float32 | R | 2
| 0x547A | 0x547F | 21626 | 21631 | Time Stamp | int16 | R | 6
| 0x5480 |  | 21632 |  | Min of Phase B PF | float32 | R | 2
| 0x5482 | 0x5487 | 21634 | 21639 | Time Stamp | int16 | R | 6
| 0x5488 |  | 21640 |  | Min of Phase C PF | float32 | R | 2
| 0x548A | 0x548F | 21642 | 21647 | Time Stamp | int16 | R | 6
| 0x5490 |  | 21648 |  | Min of Phase N PF | float32 | R | 2
| 0x5492 | 0x5497 | 21650 | 21655 | Time Stamp | int16 | R | 6
| 0x5498 |  | 21656 |  | Min of Phase A P demand | float32 | R | 2
| 0x549A | 0x549F | 21658 | 21663 | Time Stamp | int16 | R | 6
| 0x54A0 |  | 21664 |  | Min of Phase B P Demand | float32 | R | 2
| 0x54A2 | 0x54A7 | 21666 | 21671 | Time Stamp | int16 | R | 6
| 0x54A8 |  | 21672 |  | Min of Phase C P Demand | float32 | R | 2
| 0x54AA | 0x54AF | 21674 | 21679 | Time Stamp | int16 | R | 6
| 0x54B0 |  | 21680 |  | Min of Phase N P demand | float32 | R | 2
| 0x54B2 | 0x54B7 | 21682 | 21687 | Time Stamp | int16 | R | 6
| 0x54B8 |  | 21688 |  | Min of Phase A Q Demand | float32 | R | 2
| 0x54BA | 0x54BF | 21690 | 21695 | Time Stamp | int16 | R | 6
| 0x54C0 |  | 21696 |  | Min of Phase B Q Demand | float32 | R | 2
| 0x54C2 | 0x54C7 | 21698 | 21703 | Time Stamp | int16 | R | 6
| 0x54C8 |  | 21704 |  | Min of Phase C Q demand | float32 | R | 2
| 0x54CA | 0x54CF | 21706 | 21711 | Time Stamp | int16 | R | 6
| 0x54D0 |  | 21712 |  | Min of Phase N Q Demand | float32 | R | 2
| 0x54D2 | 0x54D7 | 21714 | 21719 | Time Stamp | int16 | R | 6
| 0x54D8 |  | 21720 |  | Min of Phase A S Demand | float32 | R | 2
| 0x54DA | 0x54DF | 21722 | 21727 | Time Stamp | int16 | R | 6
| 0x54E0 |  | 21728 |  | Min of Phase B S demand | float32 | R | 2
| 0x54E2 | 0x54E7 | 21730 | 21735 | Time Stamp | int16 | R | 6
| 0x54E8 |  | 21736 |  | Min of Phase C S Demand | float32 | R | 2
| 0x54EA | 0x54EF | 21738 | 21743 | Time Stamp | int16 | R | 6
| 0x54F0 |  | 21744 |  | Min of Phase N S Demand | float32 | R | 2
| 0x54F2 | 0x54F7 | 21746 | 21751 | Time Stamp | int16 | R | 6
| 0x54F8 |  | 21752 |  | Min of Phase N I | float32 | R | 2
| 0x54FA | 0x54FF | 21754 | 21759 | Time Stamp | int16 | R | 6
| 0x5500 |  | 21760 |  | Min of Summation 2 P | float32 | R | 2
| 0x5502 | 0x5507 | 21762 | 21767 | Time Stamp | int16 | R | 6
| 0x5508 |  | 21768 |  | Min of Summation 2 Q | float32 | R | 2
| 0x550A | 0x550F | 21770 | 21775 | Time Stamp | int16 | R | 6
| 0x5510 |  | 21776 |  | Min of Summation 2 S | float32 | R | 2
| 0x5512 | 0x5517 | 21778 | 21783 | Time Stamp | int16 | R | 6
| 0x5518 |  | 21784 |  | Min of Summation 2 PF | float32 | R | 2
| 0x551A | 0x551F | 21786 | 21791 | Time Stamp | int16 | R | 6
| 0x5520 |  | 21792 |  | Min of Summation 2 P demand | float32 | R | 2
| 0x5522 | 0x5527 | 21794 | 21799 | Time Stamp | int16 | R | 6
| 0x5528 |  | 21800 |  | Min of Summation 2 Q Demand | float32 | R | 2
| 0x552A | 0x552F | 21802 | 21807 | Time Stamp | int16 | R | 6
| 0x5530 |  | 21808 |  | Min of Summation 2 S Demand | float32 | R | 2
| 0x5532 | 0x5537 | 21810 | 21815 | Time Stamp | int16 | R | 6
| 0x5538 |  | 21816 |  | Min of Summation 2 I | float32 | R | 2
| 0x553A | 0x553F | 21818 | 21823 | Time Stamp | int16 | R | 6
| 0x5540 |  | 21824 |  | Min of In THD | float32 | R | 2
| 0x5542 | 0x5547 | 21826 | 21831 | Time Stamp | int16 | R | 6

## Alarm Records｜DI¦AO¦AI¦SOE
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Alarm Log
| 0x42A9 |  | 17065 |  | Alarm Log 1: Alarming Status | int16 | R | 1 | High Byte: Alarm ID Low Byte Bit0: Alarm Status; 1: On 0: Off Low Byte Bit1: if "AND" enabled
| 0x42AA |  | 17066 |  | Alarm Log 1: Alarming parameter code | int16 | R | 1 | 0~79
| 0x42AB |  | 17067 |  | Alarm Log 1: over/under limit value | int16 | R | 1 | Related to parameter chosen
| 0x42AC |  | 17068 |  | Alarm Log 1: timestamp: year | int16 | R | 1
| 0x42AD |  | 17069 |  | Alarm Log 1: timestamp: month | int16 | R | 1
| 0x42AE |  | 17070 |  | Alarm Log 1: timestamp: day | int16 | R | 1
| 0x42AF |  | 17071 |  | Alarm Log 1: timestamp: hour | int16 | R | 1
| 0x42B0 |  | 17072 |  | Alarm Log 1: timestamp: minute | int16 | R | 1
| 0x42B1 |  | 17073 |  | Alarm Log 1: timestamp: second | int16 | R | 1
| 0x42B2 |  | 17074 |  | Alarm Log 1: timestamp: ms | int16 | R | 1
| 0x42B3 | 0x42BC | 17075 | 17084 | Alarm Log 2 | int16 | R | 10
| 0x42BD | 0x42C6 | 17085 | 17094 | Alarm Log 3 | int16 | R | 10
| 0x42C7 | 0x42D0 | 17095 | 17104 | Alarm Log 4 | int16 | R | 10
| 0x42D1 | 0x42DA | 17105 | 17114 | Alarm Log 5 | int16 | R | 10
| 0x42DB | 0x42E4 | 17115 | 17124 | Alarm Log 6 | int16 | R | 10
| 0x42E5 | 0x42EE | 17125 | 17134 | Alarm Log 7 | int16 | R | 10
| 0x42EF | 0x42F8 | 17135 | 17144 | Alarm Log 8 | int16 | R | 10
| 0x42F9 | 0x4302 | 17145 | 17154 | Alarm Log 9 | int16 | R | 10
| 0x4303 | 0x430C | 17155 | 17164 | Alarm Log 10 | int16 | R | 10
| 0x430D | 0x4316 | 17165 | 17174 | Alarm Log 11 | int16 | R | 10
| 0x4317 | 0x4320 | 17175 | 17184 | Alarm Log 12 | int16 | R | 10
| 0x4321 | 0x432A | 17185 | 17194 | Alarm Log 13 | int16 | R | 10
| 0x432B | 0x4334 | 17195 | 17204 | Alarm Log 14 | int16 | R | 10
| 0x4335 | 0x433E | 17205 | 17214 | Alarm Log 15 | int16 | R | 10
| 0x433F | 0x4348 | 17215 | 17224 | Alarm Log 16 | int16 | R | 10
IO module DI pulse count
| 0x4349 | 0x434A | 17225 | 17226 | DI1 pulse count | uint32 | R | 2
| 0x434B | 0x434C | 17227 | 17228 | DI2 pulse count | uint32 | R | 2
| 0x434D | 0x434E | 17229 | 17230 | DI3 pulse count | uint32 | R | 2
| 0x434F | 0x4350 | 17231 | 17232 | DI4 pulse count | uint32 | R | 2
| 0x4351 | 0x4352 | 17233 | 17234 | DI5 pulse count | uint32 | R | 2
| 0x4353 | 0x4354 | 17235 | 17236 | DI6 pulse count | uint32 | R | 2
| 0x4355 | 0x4356 | 17237 | 17238 | DI7 pulse count | uint32 | R | 2
| 0x4357 | 0x4358 | 17239 | 17240 | DI8 pulse count | uint32 | R | 2
| 0x4359 | 0x435A | 17241 | 17242 | DI9 pulse count | uint32 | R | 2
| 0x435B | 0x435C | 17243 | 17244 | DI10 pulse count | uint32 | R | 2
| 0x435D | 0x435E | 17245 | 17246 | DI11 pulse count | uint32 | R | 2
| 0x435F | 0x4360 | 17247 | 17248 | DI12 pulse count | uint32 | R | 2
| 0x4361 | 0x4362 | 17249 | 17250 | DI13 pulse count | uint32 | R | 2
| 0x4363 | 0x4364 | 17251 | 17252 | DI14 pulse count | uint32 | R | 2
| 0x4365 | 0x4366 | 17253 | 17254 | DI15 pulse count | uint32 | R | 2
| 0x4367 | 0x4368 | 17255 | 17256 | DI16 pulse count | uint32 | R | 2
| 0x4369 | 0x436A | 17257 | 17258 | DI17 pulse count | uint32 | R | 2
| 0x436B | 0x436C | 17259 | 17260 | DI18 pulse count | uint32 | R | 2
| 0x436D | 0x436E | 17261 | 17262 | DI19 pulse count | uint32 | R | 2
| 0x436F | 0x4370 | 17263 | 17264 | DI20 pulse count | uint32 | R | 2
| 0x4371 | 0x4372 | 17265 | 17266 | DI21 pulse count | uint32 | R | 2
| 0x4373 | 0x4374 | 17267 | 17268 | DI22 pulse count | uint32 | R | 2
| 0x4375 | 0x4376 | 17269 | 17270 | DI23 pulse count | uint32 | R | 2
| 0x4377 | 0x4378 | 17271 | 17272 | DI24 pulse count | uint32 | R | 2
| 0x4379 | 0x437A | 17273 | 17274 | DI25 pulse count | uint32 | R | 2
| 0x437B | 0x437C | 17275 | 17276 | DI26 pulse count | uint32 | R | 2
| 0x437D | 0x437E | 17277 | 17278 | DI27 pulse count | uint32 | R | 2
| 0x437F | 0x4380 | 17279 | 17280 | DI28 pulse count | uint32 | R | 2
AO/AI analogic value
| 0x4381 |  | 17281 |  | AO1 output value | word | R | 1
| 0x4382 |  | 17282 |  | AO2 output value | word | R | 1
| 0x4383 |  | 17283 |  | AO3 output value | word | R | 1
| 0x4384 |  | 17284 |  | AO4 output value | word | R | 1
| 0x4385 |  | 17285 |  | AI1 sample value | word | R | 1
| 0x4386 |  | 17286 |  | AI2 sample value | word | R | 1
| 0x4387 |  | 17287 |  | AI3 sample value | word | R | 1
| 0x4388 |  | 17288 |  | AI4 sample value | word | R | 1
AO/AI real value
| 0x4389 | 0x438A | 17289 | 17290 | AO1 value | float32 | R | 2
| 0x438B | 0x438C | 17291 | 17292 | AO2 value | float32 | R | 2
| 0x438D | 0x438E | 17293 | 17294 | AO3 value | float32 | R | 2
| 0x438F | 0x4390 | 17295 | 17296 | AO4 value | float32 | R | 2
| 0x4391 | 0x4392 | 17297 | 17298 | AI1 value | float32 | R | 2
| 0x4393 | 0x4394 | 17299 | 17300 | AI2 value | float32 | R | 2
| 0x4395 | 0x4396 | 17301 | 17302 | AI3 value | float32 | R | 2
| 0x4397 | 0x4398 | 17303 | 17304 | AI4 value | float32 | R | 2
SOE Log
| 0x4399 |  | 17305 |  | SOE Log 1 timestamp - year | word | R | 1
| 0x439A |  | 17306 |  | SOE Log 1 timestamp - month | word | R | 1
| 0x439B |  | 17307 |  | SOE Log 1 timestamp - day | word | R | 1
| 0x439C |  | 17308 |  | SOE Log 1 timestamp - hour | word | R | 1
| 0x439D |  | 17309 |  | SOE Log 1 timestamp - minute | word | R | 1
| 0x439E |  | 17310 |  | SOE Log 1 timestamp - second | word | R | 1
| 0x439F |  | 17311 |  | SOE Log 1 timestamp - ms | word | R | 1
| 0x43A0 |  | 17312 |  | SOE Log 1 status | word | R | 1
| 0x43A1 | 0x43A8 | 17313 | 17320 | SOE Log 2 | word | R | 8
| 0x43A9 | 0x43B0 | 17321 | 17328 | SOE Log 3 | word | R | 8
| 0x43B1 | 0x43B8 | 17329 | 17336 | SOE Log 4 | word | R | 8
| 0x43B9 | 0x43C0 | 17337 | 17344 | SOE Log 5 | word | R | 8
| 0x43C1 | 0x43C8 | 17345 | 17352 | SOE Log 6 | word | R | 8
| 0x43C9 | 0x43D0 | 17353 | 17360 | SOE Log 7 | word | R | 8
| 0x43D1 | 0x43D8 | 17361 | 17368 | SOE Log 8 | word | R | 8
| 0x43D9 | 0x43E0 | 17369 | 17376 | SOE Log 9 | word | R | 8
| 0x43E1 | 0x43E8 | 17377 | 17384 | SOE Log 10 | word | R | 8
| 0x43E9 | 0x43F0 | 17385 | 17392 | SOE Log 11 | word | R | 8
| 0x43F1 | 0x43F8 | 17393 | 17400 | SOE Log 12 | word | R | 8
| 0x43F9 | 0x4400 | 17401 | 17408 | SOE Log 13 | word | R | 8
| 0x4401 | 0x4408 | 17409 | 17416 | SOE Log 14 | word | R | 8
| 0x4409 | 0x4410 | 17417 | 17424 | SOE Log 15 | word | R | 8
| 0x4411 | 0x4418 | 17425 | 17432 | SOE Log 16 | word | R | 8
| 0x4419 | 0x4420 | 17433 | 17440 | SOE Log 17 | word | R | 8
| 0x4421 | 0x4428 | 17441 | 17448 | SOE Log 18 | word | R | 8
| 0x4429 | 0x4430 | 17449 | 17456 | SOE Log 19 | word | R | 8
| 0x4431 | 0x4438 | 17457 | 17464 | SOE Log 20 | word | R | 8
| 0x4439 |  | 17465 | 17465 | SOE record from IO module number | word | R | 1
IO11- | 0x443A |  | 17466 | 17466 | bit0-bit6: DI1 -- DI6 | word | R | 1
IO21- | 0x443B |  | 17467 | 17467 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO31- | 0x443C |  | 17468 | 17468 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO12- | 0x443D |  | 17469 | 17469 | bit0-bit6: DI1 -- DI6 | word | R | 1
IO22- | 0x443E |  | 17470 | 17470 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO32- | 0x443F |  | 17471 | 17471 | bit0-bit4: DI1 -- DI4 | word | R | 1

## TOU Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Current Month Accumulative TOU Energy: 03H Read
| 0x7200 | 0x7201 | 29184 | 29185 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7202 | 0x7203 | 29186 | 29187 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7204 | 0x7205 | 29188 | 29189 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7206 | 0x7207 | 29190 | 29191 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7208 | 0x7209 | 29192 | 29193 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x720A | 0x720B | 29194 | 29195 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x720C | 0x720D | 29196 | 29197 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x720E | 0x720F | 29198 | 29199 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7210 | 0x7211 | 29200 | 29201 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7212 | 0x7213 | 29202 | 29203 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7214 | 0x7215 | 29204 | 29205 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7216 | 0x7217 | 29206 | 29207 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7218 | 0x7219 | 29208 | 29209 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x721A | 0x721B | 29210 | 29211 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x721C | 0x721D | 29212 | 29213 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x721E | 0x721F | 29214 | 29215 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7220 | 0x7221 | 29216 | 29217 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7222 | 0x7223 | 29218 | 29219 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7224 | 0x7225 | 29220 | 29221 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7226 | 0x7227 | 29222 | 29223 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7228 | 0x7229 | 29224 | 29225 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x722A | 0x722B | 29226 | 29227 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x722C | 0x722D | 29228 | 29229 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x722E | 0x722F | 29230 | 29231 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7230 | 0x7231 | 29232 | 29233 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Previous Month Accumulative TOU Energy: 03H Read
| 0x7232 | 0x7233 | 29234 | 29235 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7234 | 0x7235 | 29236 | 29237 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7236 | 0x7237 | 29238 | 29239 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7238 | 0x7239 | 29240 | 29241 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x723A | 0x723B | 29242 | 29243 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x723C | 0x723D | 29244 | 29245 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x723E | 0x723F | 29246 | 29247 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7240 | 0x7241 | 29248 | 29249 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7242 | 0x7243 | 29250 | 29251 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7244 | 0x7245 | 29252 | 29253 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7246 | 0x7247 | 29254 | 29255 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7248 | 0x7249 | 29256 | 29257 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x724A | 0x724B | 29258 | 29259 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x724C | 0x724D | 29260 | 29261 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x724E | 0x724F | 29262 | 29263 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7250 | 0x7251 | 29264 | 29265 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7252 | 0x7253 | 29266 | 29267 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7254 | 0x7255 | 29268 | 29269 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7256 | 0x7257 | 29270 | 29271 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7258 | 0x7259 | 29272 | 29273 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x725A | 0x725B | 29274 | 29275 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x725C | 0x725D | 29276 | 29277 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x725E | 0x725F | 29278 | 29279 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7260 | 0x7261 | 29280 | 29281 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7262 | 0x7263 | 29282 | 29283 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Current Month Incremental TOU Energy: 03H Read
| 0x7300 | 0x7301 | 29440 | 29441 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7302 | 0x7303 | 29442 | 29443 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7304 | 0x7305 | 29444 | 29445 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7306 | 0x7307 | 29446 | 29447 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7308 | 0x7309 | 29448 | 29449 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x730A | 0x730B | 29450 | 29451 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x730C | 0x730D | 29452 | 29453 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x730E | 0x730F | 29454 | 29455 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7310 | 0x7311 | 29456 | 29457 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7312 | 0x7313 | 29458 | 29459 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7314 | 0x7315 | 29460 | 29461 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7316 | 0x7317 | 29462 | 29463 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7318 | 0x7319 | 29464 | 29465 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x731A | 0x731B | 29466 | 29467 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x731C | 0x731D | 29468 | 29469 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x731E | 0x731F | 29470 | 29471 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7320 | 0x7321 | 29472 | 29473 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7322 | 0x7323 | 29474 | 29475 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7324 | 0x7325 | 29476 | 29477 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7326 | 0x7327 | 29478 | 29479 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7328 | 0x7329 | 29480 | 29481 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x732A | 0x732B | 29482 | 29483 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x732C | 0x732D | 29484 | 29485 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x732E | 0x732F | 29486 | 29487 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7330 | 0x7331 | 29488 | 29489 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Previous Month Incremental TOU Energy: 03H Read
| 0x7332 | 0x7333 | 29490 | 29491 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7334 | 0x7335 | 29492 | 29493 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7336 | 0x7337 | 29494 | 29495 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7338 | 0x7339 | 29496 | 29497 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x733A | 0x733B | 29498 | 29499 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x733C | 0x733D | 29500 | 29501 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x733E | 0x733F | 29502 | 29503 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7340 | 0x7341 | 29504 | 29505 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7342 | 0x7343 | 29506 | 29507 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7344 | 0x7345 | 29508 | 29509 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7346 | 0x7347 | 29510 | 29511 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7348 | 0x7349 | 29512 | 29513 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x734A | 0x734B | 29514 | 29515 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x734C | 0x734D | 29516 | 29517 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x734E | 0x734F | 29518 | 29519 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7350 | 0x7351 | 29520 | 29521 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7352 | 0x7353 | 29522 | 29523 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7354 | 0x7355 | 29524 | 29525 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7356 | 0x7357 | 29526 | 29527 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7358 | 0x7359 | 29528 | 29529 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x735A | 0x735B | 29530 | 29531 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x735C | 0x735D | 29532 | 29533 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x735E | 0x735F | 29534 | 29535 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7360 | 0x7361 | 29536 | 29537 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7362 | 0x7363 | 29538 | 29539 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Current Month TOU Max Demand
| 0x7500 | 0x7503 | 29952 | 29955 | sharp - max import active power demand and timestamp (format: max value; year month; date hour; minute second) | int16 | R | 4
| 0x7504 | 0x7507 | 29956 | 29959 | sharp - max export active power demand and timestamp | int16 | R | 4
| 0x7508 | 0x750B | 29960 | 29963 | sharp - max import reactive power demand and timestamp | int16 | R | 4
| 0x750C | 0x750F | 29964 | 29967 | sharp - max export reactive power demand and timestamp | int16 | R | 4
| 0x7510 | 0x7513 | 29968 | 29971 | sharp - max apparent power demand and timestamp | int16 | R | 4
| 0x7514 | 0x7517 | 29972 | 29975 | sharp - max Ia demand and timestamp | int16 | R | 4
| 0x7518 | 0x751B | 29976 | 29979 | sharp - max Ib demand and timestamp | int16 | R | 4
| 0x751C | 0x751F | 29980 | 29983 | sharp - max Ic demand and timestamp | int16 | R | 4
| 0x7520 | 0x7523 | 29984 | 29987 | peak - max import active power demand and timestamp | int16 | R | 4
| 0x7524 | 0x7527 | 29988 | 29991 | peak - max export active power demand and timestamp | int16 | R | 4
| 0x7528 | 0x752B | 29992 | 29995 | peak - max import reactive power demand and timestamp | int16 | R | 4
| 0x752C | 0x752F | 29996 | 29999 | peak - max export reactive power demand and timestamp | int16 | R | 4
| 0x7530 | 0x7533 | 30000 | 30003 | peak - max apparent power demand and timestamp | int16 | R | 4
| 0x7534 | 0x7537 | 30004 | 30007 | peak - max Ia demand and timestamp | int16 | R | 4
| 0x7538 | 0x753B | 30008 | 30011 | peak - max Ib demand and timestamp | int16 | R | 4
| 0x753C | 0x753F | 30012 | 30015 | peak - max Ic demand and timestamp | int16 | R | 4
| 0x7540 | 0x7543 | 30016 | 30019 | valley - max import active power demand and timestamp | int16 | R | 4
| 0x7544 | 0x7547 | 30020 | 30023 | valley - max export active power demand and timestamp | int16 | R | 4
| 0x7548 | 0x754B | 30024 | 30027 | valley - max import reactive power demand and timestamp | int16 | R | 4
| 0x754C | 0x754F | 30028 | 30031 | valley - max export reactive power demand and timestamp | int16 | R | 4
| 0x7550 | 0x7553 | 30032 | 30035 | valley - max apparent power demand and timestamp | int16 | R | 4
| 0x7554 | 0x7557 | 30036 | 30039 | valley - max Ia demand and timestamp | int16 | R | 4
| 0x7558 | 0x755B | 30040 | 30043 | valley - max Ib demand and timestamp | int16 | R | 4
| 0x755C | 0x755F | 30044 | 30047 | valley - max Ic demand and timestamp | int16 | R | 4
| 0x7560 | 0x7563 | 30048 | 30051 | normal - max import active power demand and timestamp | int16 | R | 4
| 0x7564 | 0x7567 | 30052 | 30055 | normal - max export active power demand and timestamp | int16 | R | 4
| 0x7568 | 0x756B | 30056 | 30059 | normal - max import reactive power demand and timestamp | int16 | R | 4
| 0x756C | 0x756F | 30060 | 30063 | normal - max export reactive power demand and timestamp | int16 | R | 4
| 0x7570 | 0x7573 | 30064 | 30067 | normal - max apparent power demand and timestamp | int16 | R | 4
| 0x7574 | 0x7577 | 30068 | 30071 | normal - max Ia demand and timestamp | int16 | R | 4
| 0x7578 | 0x757B | 30072 | 30075 | normal - max Ib demand and timestamp | int16 | R | 4
| 0x757C | 0x757F | 30076 | 30079 | normal - max Ic demand and timestamp | int16 | R | 4
| 0x7580 | 0x7583 | 30080 | 30083 | total - max import active power demand and timestamp | int16 | R | 4
| 0x7584 | 0x7587 | 30084 | 30087 | total - max export active power demand and timestamp | int16 | R | 4
| 0x7588 | 0x758B | 30088 | 30091 | total - max import reactive power demand and timestamp | int16 | R | 4
| 0x758C | 0x758F | 30092 | 30095 | total - max export reactive power demand and timestamp | int16 | R | 4
| 0x7590 | 0x7593 | 30096 | 30099 | total - max apparent power demand and timestamp | int16 | R | 4
| 0x7594 | 0x7597 | 30100 | 30103 | total - max Ia demand and timestamp | int16 | R | 4
| 0x7598 | 0x759B | 30104 | 30107 | total - max Ib demand and timestamp | int16 | R | 4
| 0x759C | 0x759F | 30108 | 30111 | total - max Ic demand and timestamp | int16 | R | 4
Previous Month TOU Max Demand
| 0x7600 | 0x7603 | 30208 | 30211 | sharp - max import active power demand and timestamp (format: max value; year month; date hour; minute second) | int16 | R | 4
| 0x7604 | 0x7607 | 30212 | 30215 | sharp - max export active power demand and timestamp | int16 | R | 4
| 0x7608 | 0x760B | 30216 | 30219 | sharp - max import reactive power demand and timestamp | int16 | R | 4
| 0x760C | 0x760F | 30220 | 30223 | sharp - max export reactive power demand and timestamp | int16 | R | 4
| 0x7610 | 0x7613 | 30224 | 30227 | sharp - max apparent power demand and timestamp | int16 | R | 4
| 0x7614 | 0x7617 | 30228 | 30231 | sharp - max Ia demand and timestamp | int16 | R | 4
| 0x7618 | 0x761B | 30232 | 30235 | sharp - max Ib demand and timestamp | int16 | R | 4
| 0x761C | 0x761F | 30236 | 30239 | sharp - max Ic demand and timestamp | int16 | R | 4
| 0x7620 | 0x7623 | 30240 | 30243 | peak - max import active power demand and timestamp | int16 | R | 4
| 0x7624 | 0x7627 | 30244 | 30247 | peak - max export active power demand and timestamp | int16 | R | 4
| 0x7628 | 0x762B | 30248 | 30251 | peak - max import reactive power demand and timestamp | int16 | R | 4
| 0x762C | 0x762F | 30252 | 30255 | peak - max export reactive power demand and timestamp | int16 | R | 4
| 0x7630 | 0x7633 | 30256 | 30259 | peak - max apparent power demand and timestamp | int16 | R | 4
| 0x7634 | 0x7637 | 30260 | 30263 | peak - max Ia demand and timestamp | int16 | R | 4
| 0x7638 | 0x763B | 30264 | 30267 | peak - max Ib demand and timestamp | int16 | R | 4
| 0x763C | 0x763F | 30268 | 30271 | peak - max Ic demand and timestamp | int16 | R | 4
| 0x7640 | 0x7643 | 30272 | 30275 | valley - max import active power demand and timestamp | int16 | R | 4
| 0x7644 | 0x7647 | 30276 | 30279 | valley - max export active power demand and timestamp | int16 | R | 4
| 0x7648 | 0x764B | 30280 | 30283 | valley - max import reactive power demand and timestamp | int16 | R | 4
| 0x764C | 0x764F | 30284 | 30287 | valley - max export reactive power demand and timestamp | int16 | R | 4
| 0x7650 | 0x7653 | 30288 | 30291 | valley - max apparent power demand and timestamp | int16 | R | 4
| 0x7654 | 0x7657 | 30292 | 30295 | valley - max Ia demand and timestamp | int16 | R | 4
| 0x7658 | 0x765B | 30296 | 30299 | valley - max Ib demand and timestamp | int16 | R | 4
| 0x765C | 0x765F | 30300 | 30303 | valley - max Ic demand and timestamp | int16 | R | 4
| 0x7660 | 0x7663 | 30304 | 30307 | normal - max import active power demand and timestamp | int16 | R | 4
| 0x7664 | 0x7667 | 30308 | 30311 | normal - max export active power demand and timestamp | int16 | R | 4
| 0x7668 | 0x766B | 30312 | 30315 | normal - max import reactive power demand and timestamp | int16 | R | 4
| 0x766C | 0x766F | 30316 | 30319 | normal - max export reactive power demand and timestamp | int16 | R | 4
| 0x7670 | 0x7673 | 30320 | 30323 | normal - max apparent power demand and timestamp | int16 | R | 4
| 0x7674 | 0x7677 | 30324 | 30327 | normal - max Ia demand and timestamp | int16 | R | 4
| 0x7678 | 0x767B | 30328 | 30331 | normal - max Ib demand and timestamp | int16 | R | 4
| 0x767C | 0x767F | 30332 | 30335 | normal - max Ic demand and timestamp | int16 | R | 4
| 0x7680 | 0x7683 | 30336 | 30339 | total - max import active power demand and timestamp | int16 | R | 4
| 0x7684 | 0x7687 | 30340 | 30343 | total - max export active power demand and timestamp | int16 | R | 4
| 0x7688 | 0x768B | 30344 | 30347 | total - max import reactive power demand and timestamp | int16 | R | 4
| 0x768C | 0x768F | 30348 | 30351 | total - max export reactive power demand and timestamp | int16 | R | 4
| 0x7690 | 0x7693 | 30352 | 30355 | total - max apparent power demand and timestamp | int16 | R | 4
| 0x7694 | 0x7697 | 30356 | 30359 | total - max Ia demand and timestamp | int16 | R | 4
| 0x7698 | 0x769B | 30360 | 30363 | total - max Ib demand and timestamp | int16 | R | 4
| 0x769C | 0x769F | 30364 | 30367 | total - max Ic demand and timestamp | int16 | R | 4

## SunSpec
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
SunSpec System Information Address Table
| 0xC350 | 0xC351 | 50000 | 50001 | SunSpec_ID | Uint16 | R | 2 | 0x53756e53 |  | Y
| 0xC352 | 0xC352 | 50002 | 50002 | ID | Uint16 | R | 1 | 1 |  | Y
| 0xC353 | 0xC353 | 50003 | 50003 | Lenth | Uint16 | R | 1 | 65 |  | Y
| 0xC354 | 0xC363 | 50004 | 50019 | Manufacturer | string | R | 16 | Well known value registered with SunSpec for compliance | ACCUENERGY 41 43 43 55 45 4E 45 52 47 59 | Y
| 0xC364 | 0xC373 | 50020 | 50035 | Model | string | R | 16 | Manufacturer specific value (32 chars) | Acuvim II 41 63 75 76 69 6D 20 49 49 | Y
| 0xC374 | 0xC37B | 50036 | 50043 | Options | string | R | 8 | Manufacturer specific value (16 chars) | Acuvim IIX 41 63 75 76 69 6D 20 49 49 00（II）/52（IIR）/45(IIE)/57(IIW)/42 4E(IIBN) MK II(4D 4B 20 49 49) | Y | 0xF050 product model ID
| 0xC37C | 0xC383 | 50044 | 50051 | Version | string | R | 8 | Manufacturer specific value (16 chars) | H: 2.32 S: 3.91 48 3A 32 2E 33 32 20 53 3A 33 2E 39 31 20 20 20 | Y
| 0xC384 | 0xC393 | 50052 | 50067 | Serial Number | string | R | 16 | Manufacturer specific value (32 chars) |  | Y
| 0xC394 | 0xC394 | 50068 | 50068 | Device Address | uint16 | R | 1 | Modbus device address |  | Y
SunSpec Measured Data Address Table (Continued)
| 0xC395 | 0xC395 | 50069 | 50069 | ID | Uint16 | R | 1 | Meter (Single Phase)single phase (AN or AB) meter --201 split single phase (ABN) meter –202 wye-connect three phase (abcn) meter-203 delta-connect three phase (abc) meter --204 |  | Y
| 0xC396 | 0xC396 | 50070 | 50070 | Lenth | Uint16 | R | 1 | 105 |  | Y
| 0xC397 | 0xC397 | 50071 | 50071 | Amps(average): Sunspec; Amps(average): AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC398 | 0xC398 | 50072 | 50072 | Amps Phase A: Sunspec; Phase A Current: AcuvimII | int16 | R | 1 | 0~9999 A | Change to 0~32767 | Y
| 0xC399 | 0xC399 | 50073 | 50073 | Amps Phase B: Sunspec; Phase B Current: AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC39A | 0xC39A | 50074 | 50074 | Amps Phase C: Sunspec; Phase C Current: AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC39B | 0xC39B | 50075 | 50075 | Current scale factor: Sunspec; CT Ratio: Acuvim II | sunssf | R | 1 | - 3 ~ + 2(used as exponent of a power of 10) |  | Y
| 0xC39C | 0xC39C | 50076 | 50076 | Voltage LN (average): Sunspec; Phase Average Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39D | 0xC39D | 50077 | 50077 | Phase Voltage AN: Sunspec; Phase A Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39E | 0xC39E | 50078 | 50078 | Phase Voltage BN: Sunspec; Phase B Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39F | 0xC39F | 50079 | 50079 | Phase Voltage CN: Sunspec; Phase C Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A0 | 0xC3A0 | 50080 | 50080 | Voltage LL (average): Sunspec; Line Average Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A1 | 0xC3A1 | 50081 | 50081 | Phase Voltage AB: Sunspec; Line AB Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A2 | 0xC3A2 | 50082 | 50082 | Phase Voltage BC: Sunspec; Line BC Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A3 | 0xC3A3 | 50083 | 50083 | Phase Voltage CA: Sunspec; Line CA Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A4 | 0xC3A4 | 50084 | 50084 | Voltage scale factor: Sunspec | sunssf | R | 1 | - 2 ~ 4(used as exponent of a power of 10) |  | Y
| 0xC3A5 | 0xC3A5 | 50085 | 50085 | Frequency | int16 | R | 1 | 45Hz-65Hz |  | Y
| 0xC3A6 | 0xC3A6 | 50086 | 50086 | Frequency scale factor | sunssf | R | 1 | -2(used as exponent of a power of 10) |  | Y
| 0xC3A7 | 0xC3A7 | 50087 | 50087 | Total Real Power: Sunspec; Total Active Power: Acuvim II | int16 | R | 1 | 0~9999 W | 'Change to -32768~32767 | Y
| 0xC3A8 | 0xC3A8 | 50088 | 50088 | Watts phase A: Sunspec; Phase A Active Power: Acuvim II | int16 | R | 1 | 0~9999 W | P | Y
| 0xC3A9 | 0xC3A9 | 50089 | 50089 | Watts phase B: Sunspec; Phase B Active Power: Acuvim II | int16 | R | 1 | 0~9999 W |  | Y
| 0xC3AA | 0xC3AA | 50090 | 50090 | Watts phase C: Sunspec; Phase C Active Power: Acuvim II | int16 | R | 1 | 0~9999 W |  | Y
| 0xC3AB | 0xC3AB | 50091 | 50091 | Real Power scale factor: Sunspec | sunssf | R | 1 | -1~ 4(used as exponent of a power of 10) |  | Y
| 0xC3AC | 0xC3AC | 50092 | 50092 | Total Apparent Power VA: Sunspec; Total Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA | S | Y
| 0xC3AD | 0xC3AD | 50093 | 50093 | VA phase A: Sunspec; Phase A Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3AE | 0xC3AE | 50094 | 50094 | VA phase B: Sunspec; Phase B Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3AF | 0xC3AF | 50095 | 50095 | VA phaseCA: Sunspec; Phase C Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3B0 | 0xC3B0 | 50096 | 50096 | Apparent Power scale factor: Sunspec; | sunssf | R | 1 | - 1 ~ 4(used as exponent of a power of 10) | -1~8 | Y
| 0xC3B1 | 0xC3B1 | 50097 | 50097 | Reactive Power VAR: Sunspec; Total Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var |  | Y
| 0xC3B2 | 0xC3B2 | 50098 | 50098 | VAR phase A: Sunspec; Phase A Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var | -32768~32767 | Y
| 0xC3B3 | 0xC3B3 | 50099 | 50099 | VAR phase B: Sunspec; Phase B Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var | Q | Y
| 0xC3B4 | 0xC3B4 | 50100 | 50100 | VAR phase C: Sunspec; Phase C Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var |  | Y
| 0xC3B5 | 0xC3B5 | 50101 | 50101 | Reactive Power scale factor: Sunspec | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10) | -1~8 | Y
| 0xC3B6 | 0xC3B6 | 50102 | 50102 | Power Factor | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B7 | 0xC3B7 | 50103 | 50103 | PF phase A | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B8 | 0xC3B8 | 50104 | 50104 | PF phase B | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B9 | 0xC3B9 | 50105 | 50105 | PF phase C | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3BA | 0xC3BA | 50106 | 50106 | Power Factor scale factor: Sunspec | sunssf | R | 1 | -3(used as exponent of a power of 10) |  | Y
| 0xC3BB | 0xC3BC | 50107 | 50108 | Total Real Energy Exported: Sunspec Total Active Energy Exported: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh（unit: W） | EP Export/Output | Y
| 0xC3BD | 0xC3BE | 50109 | 50110 | Total Watt-hours Exported in phase A: Sunspec; Total Active Energy Exported in Phase A: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3BF | 0xC3C0 | 50111 | 50112 | Total Watt-hours Exported in phase B: Sunspec; Total Active Energy Exported in PhaseB: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C1 | 0xC3C2 | 50113 | 50114 | Total Watt-hours Exported in phase C: Sunspec; Total Active Energy Exported in Phase C: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C3 | 0xC3C4 | 50115 | 50116 | Total Real Energy Imported: Sunspec; Total Active Energy Imported: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh | EP Import/Input | Y
| 0xC3C5 | 0xC3C6 | 50117 | 50118 | Total Watt-hours Imported phase A: Sunspec; Total Active Energy Imported in Phase A: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C7 | 0xC3C8 | 50119 | 50120 | Total Watt-hours Imported phase B: Sunspec; Total Active Energy Imported in Phase B: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C9 | 0xC3CA | 50121 | 50122 | Total Watt-hours Imported phase C: Sunspec; Total Active Energy Imported in Phase C: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3CB | 0xC3CB | 50123 | 50123 | TotWh_SF: Sunspec | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10) |  | Y
| 0xC3CC | 0xC3CD | 50124 | 50125 | Total VA-hours Exported: Sunspec; | acc32 | R/W | 2 | P < 0 | ES Export/Output
| 0xC3CE | 0xC3CF | 50126 | 50127 | Total VA-hours Exported in phase A: Sunspec; | acc32 | R/W | 2
| 0xC3D0 | 0xC3D1 | 50128 | 50129 | Total VA-hours Exported in phase B: Sunspec; | acc32 | R/W | 2
| 0xC3D2 | 0xC3D3 | 50130 | 50131 | Total VA-hours Exported in phase C: Sunspec; | acc32 | R/W | 2
| 0xC3D4 | 0xC3D5 | 50132 | 50133 | Total VA-hours Imported: Sunspec; | acc32 | R/W | 2 |  | ES Import/Input
| 0xC3D6 | 0xC3D7 | 50134 | 50135 | Total VA-hours Imported in phase A: Sunspec; | acc32 | R/W | 2
| 0xC3D8 | 0xC3D9 | 50136 | 50137 | Total VA-hours Imported in phase B: Sunspec; | acc32 | R/W | 2
| 0xC3DA | 0xC3DB | 50138 | 50139 | Total VA-hours Imported in phase C: Sunspec; | acc32 | R/W | 2
| 0xC3DC | 0xC3DC | 50140 | 50140 | TotVAh_SF: Sunspec | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10) |  | Y
| 0xC3DD | 0xC3DE | 50141 | 50142 | Total VAr-hours Imported Q1: Sunspec | acc32 | R/W | 2 |  | EQ
| 0xC3DF | 0xC3E0 | 50143 | 50144 | Total VAr-hours Imported Q1 phase A: Sunspec | acc32 | R/W | 2
| 0xC3E1 | 0xC3E2 | 50145 | 50146 | Total VAr-hours Imported Q1 phase B: Sunspec | acc32 | R/W | 2
| 0xC3E3 | 0xC3E4 | 50147 | 50148 | Total VAr-hours Imported Q1 phase C: Sunspec | acc32 | R/W | 2
| 0xC3E5 | 0xC3E6 | 50149 | 50150 | Total VAr-hours Imported Q2: Sunspec | acc32 | R/W | 2
| 0xC3E7 | 0xC3E8 | 50151 | 50152 | Total VAr-hours Imported Q2 phase A: Sunspec | acc32 | R/W | 2
| 0xC3E9 | 0xC3EA | 50153 | 50154 | Total VAr-hours Imported Q2 phase B: Sunspec | acc32 | R/W | 2
| 0xC3EB | 0xC3EC | 50155 | 50156 | Total VAr-hours Imported Q2 phase C: Sunspec | acc32 | R/W | 2
| 0xC3ED | 0xC3EE | 50157 | 50158 | Total VAr-hours Exported Q3: Sunspec | acc32 | R/W | 2
| 0xC3EF | 0xC3F0 | 50159 | 50160 | Total VAr-hours Exported Q3 phase A: Sunspec | acc32 | R/W | 2
| 0xC3F1 | 0xC3F2 | 50161 | 50162 | Total VAr-hours Exported Q3 phase B: Sunspec | acc32 | R/W | 2
| 0xC3F3 | 0xC3F4 | 50163 | 50164 | Total VAr-hours Exported Q3 phase C: Sunspec | acc32 | R/W | 2
| 0xC3F5 | 0xC3F6 | 50165 | 50166 | Total VAr-hours Exported Q4: Sunspec | acc32 | R/W | 2
| 0xC3F7 | 0xC3F8 | 50167 | 50168 | Total VAr-hours Exported Q4 phase A: Sunspec | acc32 | R/W | 2
| 0xC3F9 | 0xC3FA | 50169 | 50170 | Total VAr-hours Exported Q4 phase B: Sunspec | acc32 | R/W | 2
| 0xC3FB | 0xC3FC | 50171 | 50172 | Total VAr-hours Exported Q4 phase C: Sunspec | acc32 | R/W | 2
| 0xC3FD | 0xC3FD | 50173 | 50173 | TotVArh_SF: Sunspec; | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10)
| 0xC3FE | 0xC3FF | 50174 | 50175 | Meter Event Flags | bitfield32 | R | 2 | 0
| 0xC400 | 0xC400 | 50176 | 50176 | SunSpec_end_ID: Sunspec | Uint16 |  | 1 | 0xFFFF
| 0xC401 | 0xC401 | 50177 | 50177 | SunSpec_end_lenth: Sunspec | Uint16 |  | 1 | 0x0000