## Version
Version | Changes | Date
v1.00 | Initial Version | 2024-01-01
v1.01 | Dual Source, Max/Min (Float) added | 2025-02-07
v1.02 | Class S | 2025-02-27
v1.03 | TDD, Predictive Demand | 2025-09-16
v1.05 | Data Log settings, status and readings | 2025-11-17
v1.06 | Residual Current | 2025-12-02
v1.07 | Updated decimal addressing error for Nueutral current selection and frequency avg filter registers | 2026-01-08

## Parameter & Status Settings
System Settings: 03H Read, 10H Write
Address(H) | Address(D) | Parameter | Range | Default | Data Type | Access Property
0FFDH | 4093 | Frequency | 0: 50Hz 1: 60Hz 2: 400Hz | 0 | Word | R/W
0FFEH | 4094 | Protocol 1 | 0: Modbus 2: BACnet MSTP | 0 | Word | R/W
0FFFH | 4095 | Parity 1 | 0:Even 1: Odd 2: Non2 3: Non1 | 3 | Word | R/W
1000H | 4096 | Password | 0-9999 | 0 | Word | R/W
1001H | 4097 | Communication Address 1 | 1-247 (Modbus) 0-127 (BACnet) | 1 | Word | R/W
1002H | 4098 | Baud Rate | 2400-115200 | 19200 | Word | R/W
1003H | 4099 | Voltage Input Wiring Type | 0: 3LN 1: 2LN 2: 2LL 3: 3LL 4: 1LL | 0 | Word | R/W
1004H | 4100 | Current Input Wiring Type | 0:3CT 1: 1CT 2: 2CT | 0 | Word | R/W
1005H | 4101 | PT1(High 16 bit) | 50.0-500000.0 | 0 | Word | R/W
1006H | 4102 | PT1(Low 16 bit) |  | 220 | Word | R/W
1007H | 4103 | PT2 | 50.0-400.0 | 220 | Word | R/W
1008H | 4104 | CT1 | 1-50000 | 5 (5A Model) 1 (mV Model) | Word | R/W
1009H | 4105 | CT2 | 1: 1A (5A Model) 5: 5A (5A Model) 333: 333mV (mV Model) 100: RCT (mV Model) | 5 (5A Model) 333 (mV Model) | Word | R/W
100AH | 4106 | kWh Pulse Constant | 1-60000 | 5000 | Word | R/W
100BH | 4107 | kvarh Pulse Constant | 1-60000 | 5000 | Word | R/W
100CH | 4108 | LCD Backlight Time | 0-120 | 1 | Word | R/W
100DH | 4109 | Demand Sliding Window Time | 1-30 | 15 | Word | R/W
100EH | 4110 | Demand Calculation Mode | 0: Fixed 1: Sliding 2: Thermal 3: Rolling | 1 | Word | R/W
100FH | 4111 | Clear Demand | 1: Clear Demand 0: No Clear | 0 | Word | R/W
1010H | 4112 | Max/Min Clear | 1: Clear Max/Min 0: No Clear | 0 | Word | R/W
1011H | 4113 | Run Time Clear | 1: Clear Run Time 0: No Clear | 0 | Word | R/W
1012H | 4114 | Current I1 Direction | 0: Positive 1: Negative | 0 | Word | R/W
1013H | 4115 | Current I2 Direction | 0: Positive 1: Negative | 0 | Word | R/W
1014H | 4116 | Current I3 Direction | 0: Positive 1: Negative | 0 | Word | R/W
1015H | 4117 | VAR/PF Convention | 0: IEC 1: IEEE | 0 | Word | R/W
1016H | 4118 | Clear Energy | 1: Clear Energy 0: No Clear | 0 | Word | R/W
1017H | 4119 | Energy Calculation Mode | 0: Fundamental 1: Full-wave | 1 | Word | R/W
1018H | 4120 | Reactive Power Measurement Mode | 0: Real 1: General | 0 | Word | R/W
1019H | 4121 | Energy Display Mode | 0: Primary 1: Secondary 2: Primary (0.001 kWh) | 0 | Word | R/W
101AH | 4122 | Reset Ethernet Module | 0: None 1: Reset 2: Default | 0 | Word | R/W
101BH | 4123 | Enable SOE | 0: None 1: AXM-IO11 2: AXM-IO21 3: AXM-IO31 4: AXM-IO12 5: AXM-IO22 6: AXM-IO32 | 0 | Word | R/W
101CH | 4124 | Clear Pulse Counter | 0: None 1: AXM-IO11 2: AXM-IO21 3: AXM-IO31 4: AXM-IO12 5: AXM-IO22 6: AXM-IO32 | 0 | Word | R/W
101DH | 4125 | Basic Parameter Mode | 0: Secondary 1: Primary | 0 | Word | R/W
101EH | 4126 | Non Standard Seal Options | Bit0: First Communication Parameters Bit1: Second Communication Parameters Bit2: Clear Run Time Bit3: DI Pulse Count Bit4: TOU | 0 | Word | R/W
101FH | 4127 | Sealed State | 10: Sealed 0: Open | 1 | Word | R
1020H | 4128 | Demand Calculation Slip Time | 1-30 | 1 | Word | R/W
1021H | 4129 | Clear Alarm Records | 1: Clear Alarm 0: No Clear | 0 | Word | R/W
1022H | 4130 | CT41 | 1-50000 | 1 | Word | R/W
1023H | 4131 | CT42 | 1: 1A (5A Model) 5: 5A (5A Model) 333: 333mV (mV Model) 100: RCT (mV Model) | 5 (5A Model) 333 (mV Model) | Word | R/W
1024H-1025H | 4132-4133 | Reserved | - | - | - | -
1026H | 4134 | Restore Factory Settings | 1: Restore Factory Setting 0: No Restore | 0 | Word | R/W
1027H | 4135 | Neutral Current Mode | 1: Measured 0: Calculated | 0 | Word | R/W
1028H-102BH | 4136-4139 | Reserved | - | - | Word | R/W
102CH | 4140 | Load Percentage Power Rating | 1-14400 W | 1 | Word | R/W
102DH | 4141 | Load Percentage Property | 0: Current 1: Power | 0 | Word | R/W
102EH | 4142 | System Status | Bit0: New Alarm Bit1: New SOE Record | 0 | Word | R
102FH | 4143 | Baud Rate 2 | 2400-115200 |  | Word | R/W
1030H | 4144 | Parity 2 | 0: Even 1: Odd 2: Non2 3: Non1 | 3 | Word | R/W
1031H | 4145 | Address 2 | 1-247 | 1 | Word | R/W
1032H | 4146 | Alarm Record Number | 0: No Alarming Record 1-16: Last Alarm Record | 0 | Word | R
1033H | 4147 | SOE Record Number | 0: No SOE Record 1-20: Last SOE Record | 0 | Word | R
1034H | 4148 | Run Time (High) | 0-999999999 |  | Word | R/W
1035H | 4149 | Run Time (Low)
1036H | 4150 | IO Module Connection Status | Bit0: AXM-IO1-1 Bit1: AXM-IO1-2 Bit2: AXM-IO2-1 Bit3: AXM-IO2-2 Bit4: AXM-IO3-1 Bit5: AXM-IO3-2 0: Disconnected 1:Connected | 0 | Word | R
1037H | 4151 | Reserved | - | - | - | -
1038H | 4152 | Protocol 2 | 0: Other 4: WEB2 | 0
1039H | 4153 | 10 Year Holiday Setting Enable | 1: Enable 0: Disable | 0 | Word | R/W
103AH | 4154 | Clear Sharp Tariff | 10: Clear Tariff 0: No Clear | 0 | Word | R/W
103BH | 4155 | Clear Peak Tariff | 10: Clear Tariff 0: No Clear | 0 | Word | R/W
103CH | 4156 | Clear Valley Tariff | 10: Clear Tariff 0: No Clear | 0 | Word | R/W
103DH | 4157 | Clear Normal Tariff | 10: Clear Tariff 0: No Clear | 0 | Word | R/W
103EH | 4158 | Clear Total TOU Energy | 10: Clear Tariff 0: No Clear | 0 | Word | R/W
10F4H | 4340 | Phase A Current Phase Selection | 0: Not Used 1: Phase A Current 2: Phase B Current 3: Phase C Current 4: Neutal Current | 0 | Word | R/W
10F5H | 4341 | Phase B Current Phase Selection | 0: Not Used 1: Phase A Current 2: Phase B Current 3: Phase C Current 4: Neutal Current | 0 | Word | R/W
10F6H | 4342 | Phase C Current Phase Selection | 0: Not Used 1: Phase A Current 2: Phase B Current 3: Phase C Current 4: Neutal Current | 0 | Word | R/W
10F7H | 4343 | Neutral Current Phase Selection | 0: Not Used 1: Phase A Current 2: Phase B Current 3: Phase C Current 4: Neutal Current | 0 | Word | R/W
10F8H | 4344 | Frequency Average Filter: Update Rate | 1-4 cycles | 1 | Word | R/W
10F9H | 4345 | Frequency Average Filter: Window Size | 1-50 | 4 | Word | R/W
143AH | 5178 | Load Run Time High Byte | 0-999999999 |  | Word | R/W
143BH | 5179 | Load Run Time Low Byte

## Basic Real-time (FLOAT)
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  |  | Primary Mode | Secondary Mode
4000H-4001H | 16384-16385 | F | Frequency | F=Rx | F=Rx | Hz | Float | R
4002H-4003H | 16386-16387 | Ua | Phase A Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4004H-4005H | 16388-16389 | Ub | Phase B Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4006H-4007H | 16390-16391 | Uc | Phase C Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4008H-4009H | 16392-16393 | Uavg | Average Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
400AH-400BH | 16394-16395 | Uab | Line Voltage AB | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
400CH-400DH | 16396-16397 | Ubc | Line Voltage BC | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
400EH-400FH | 16398-16399 | Uca | Line Voltage CA | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4010H-4011H | 16400-16401 | Ulavg | Average line voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4012H-4013H | 16402-16403 | Ia | Phase A current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4014H-4015H | 16404-16405 | Ib | Phase B Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4016H-4017H | 16406-16407 | Ic | Phase C Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4018H-4019H | 16408-16409 | Iavg | Average Phase Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
401AH-401BH | 16410-16411 | In | Neutral Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
401CH-401DH | 16412-16413 | Pa | Phase A Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
401EH-401FH | 16414-16415 | Pb | Phase B Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4020H-4021H | 16416-16417 | Pc | Phase C Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4022H-4023H | 16418-16419 | Psum | Total System Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4024H-4025H | 16420-16421 | Qa | Phase A Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
4026H-4027H | 16422-16423 | Qb | Phase B Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
4028H-4029H | 16424-16425 | Qc | Phase C Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
402AH-402BH | 16426-16427 | Qsum | Total Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
402CH-402DH | 16428-16429 | Sa | Phase A Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
402EH-402FH | 16430-16431 | Sb | Phase B Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
4030H-4031H | 16432-16433 | Sc | Phase C Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
4032H-4033H | 16434-16435 | Ssum | Total Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
4034H-4035H | 16436-16437 | Pfa | Phase A Power Factor | PF=Rx | PF=Rx | No Unit | Float | R
4036H-4037H | 16438-16439 | PFb | Phase B Power Factor | PF=Rx | PF=Rx | No Unit | Float | R
4038H-4039H | 16440-16441 | PFc | Phase C Power Factor | PF=Rx | PF=Rx | No Unit | Float | R
403AH-403BH | 16442-16443 | Pfsum | Total Power Factor | PF=Rx | PF=Rx | No Unit | Float | R
403CH-403DH | 16444-16445 | U_unbl | Voltage Unbalance | U=Rx*100% | U=Rx*100% | % | Float | R
403EH-403FH | 16446-16447 | I_unbl | Current Unbalance | I=Rx*100% | I=Rx*100% | % | Float | R
4040H-4041H | 16448-16449 | L/C/R | Load Characteristic | 76.0[L], 67.0[C], 82.0[R] | 76.0[L], 67.0[C], 82.0[R] |  | Float | R
4042H-4043H | 16450-16451 | P_Dmd | Active Power Demand | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4044H-4045H | 16452-16453 | Q_Dmd | Reactive Power Demand | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
4046H-4047H | 16454-16455 | S_Dmd | Apparent Power Demand | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
4600H-4601H | 17920-17921 | Ia_Dmd | Phase A Current Demand | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4602H-4603H | 17922-17923 | Ib_Dmd | Phase B Current Demand | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4604H-4605H | 17924-17925 | Ic_Dmd | Phase C Current Demand | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
304AH-304BH | 12362-12363 | P_Dmd_Pred | Predictive Demand P | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
304CH-304DH | 12364-12365 | Q_Dmd_Pred | Predictive Demand Q | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
304EH-304FH | 12366-12367 | S_Dmd_Pred | Predictive Demand S | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
495FH-4960H | 18783-18784 | I_res | Residual Current | I =Rx | I=Rx*(CT1/CT2) | A | Float | R

## Basic Real-time (INT)
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Relationship | Property | Data Type | Access Property
3200H | 12800 | F | Frequency | F=Rx/100 | Hz | Int16 | R
3201H | 12801 | U1 | Phase 1 voltage | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3202H | 12802 | U2 | Phase 2 voltage | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3203H | 12803 | U3 | Phase 3 voltage | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3204H | 12804 | Uavg | Average phase voltage | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3205H | 12805 | U12 | Line voltage 1-2 | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3206H | 12806 | U23 | Line voltage 2-3 | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3207H | 12807 | U31 | Line voltage 3-1 | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3208H | 12808 | Ulavg | Average line voltage | U=Rx*(PT1/PT2)/10 | V | Int16 | R
3209H | 12809 | IL1 | Total phase A current | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
320AH | 12810 | IL2 | Total phase B current | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
320BH | 12811 | IL3 | Total phase C current | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
320CH | 12812 | Iavg | Average phase current | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
320DH | 12813 | In | Neutral current | I=Rx*(CT1/CT2) | A | Int16 | R
320EH | 12814 | Pa | Phase A power | P=Rx*(PT1/PT2)*(CT1/CT2) | W | Int16 | R
320FH | 12815 | Pb | Phase B power | P=Rx*(PT1/PT2)*(CT1/CT2) | W | Int16 | R
3210H | 12816 | Pc | Phase C power | P=Rx*(PT1/PT2)*(CT1/CT2) | W | Int16 | R
3211H | 12817 | Psum | Total system power | P=Rx*(PT1/PT2)*(CT1/CT2) | W | Int16 | R
3212H | 12818 | Qa | Phase A reactive power | Q=Rx*(PT1/PT2)*(CT1/CT2) | var | Int16 | R
3213H | 12819 | Qb | Phase B reactive power | Q=Rx*(PT1/PT2)*(CT1/CT2) | var | Int16 | R
3214H | 12820 | Qc | Phase C reactive power | Q=Rx*(PT1/PT2)*(CT1/CT2) | var | Int16 | R
3215H | 12821 | Qsum | Total reactive power | Q=Rx*(PT1/PT2)*(CT1/CT2) | var | Int16 | R
3216H | 12822 | Sa | Phase A apparent power | S=Rx*(PT1/PT2)*(CT1/CT2) | VA | Int16 | R
3217H | 12823 | Sb | Phase B apparent power | S=Rx*(PT1/PT2)*(CT1/CT2) | VA | Int16 | R
3218H | 12824 | Sc | Phase C apparent power | S=Rx*(PT1/PT2)*(CT1/CT2) | VA | Int16 | R
3219H | 12825 | Ssum | Total apparent power | S=Rx*(PT1/PT2)*(CT1/CT2) | VA | Int16 | R
321AH | 12826 | Pfa | Phase A power factor | PF=Rx/1000 | No Unit | Int16 | R
321BH | 12827 | PFb | Phase B power factor | PF=Rx/1000 | No Unit | Int16 | R
321CH | 12828 | PFc | Phase C power factor | PF=Rx/1000 | No Unit | Int16 | R
321DH | 12829 | Pfsum | Total power factor | PF=Rx/1000 | No Unit | Int16 | R
321EH | 12830 | U_unbl | Voltage unbalance | U=Rx*100%/10 | % | Int16 | R
321FH | 12831 | I_unbl | Current unbalance | I=Rx*100%/10 | % | Int16 | R
3220H | 12832 | L/C/R | Load Characteristic | 76.0(L) 67.0(C) 82.0(R) |  | Int16 | R
3221H | 12833 | P_Dmd | Power demand | P=Rx*(PT1/PT2)*(CT1/CT2) | W | Int16 | R
3222H | 12834 | Q_Dmd | Reactive power demand | Q=Rx*(PT1/PT2)*(CT1/CT2) | var | Int16 | R
3223H | 12835 | S_Dmd | Apparent power demand | S=Rx*(PT1/PT2)*(CT1/CT2) | VA | Int16 | R
3224H | 12836 | I1_Dmd | Phase A current demand | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
3225H | 12837 | I2_Dmd | Phase B current Demand | I=Rx*(CT1/CT2)/1000 | A | Int16 | R
3226H | 12838 | I3_Dmd | Phase C current demand | I=Rx*(CT1/CT2)/1000 | A | Int16 | R

## 100ms High Speed Metering
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  |  | Primary Mode | Secondary Mode
3000H-3001H | 12288-12289 | F | Frequency | F=Rx | F=Rx | Hz | Float | R
3002H-3003H | 12290-12291 | Ua | Phase A Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3004H-3005H | 12292-12293 | Ub | Phase B Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3006H-3007H | 12294-12295 | Uc | Phase C Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3008H-3009H | 12296-12297 | Uavg | Average Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
300AH-300BH | 12298-12299 | Uab | Line Voltage AB | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
300CH-300DH | 12300-12301 | Ubc | Line Voltage BC | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
300EH-300FH | 12302-12303 | Uca | Line Voltage CA | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3010H-3011H | 12304-12305 | Ulavg | Average Line-Line Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3012H-3013H | 12306-12307 | Ia | Phase A Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
3014H-3015H | 12308-12309 | Ib | Phase B Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
3016H-3017H | 12310-12311 | Ic | Phase C Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
3018H-3019H | 12312-12313 | Iavg | Average Phase Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
301AH-301BH | 12314-12315 | In | Neutral Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
301CH-301DH | 12316-12317 | Pa | Phase A Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
301EH-301FH | 12318-12319 | Pb | Phase B Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
3020H-3021H | 12320-12321 | Pc | Phase C Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
3022H-3023H | 12322-12323 | Psum | Total System Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
3024H-3025H | 12324-12325 | Qa | Phase A Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
3026H-3027H | 12326-12327 | Qb | Phase B Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
3028H-3029H | 12328-12329 | Qc | Phase C Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
302AH-302BH | 12330-12331 | Qsum | Total Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
302CH-302DH | 12332-12333 | Sa | Phase A Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
302EH-302FH | 12334-12335 | Sb | Phase B Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
3030H-3031H | 12336-12337 | Sc | Phase C Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
3032H-3033H | 12338-12339 | Ssum | Total Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
3034H-3035H | 12340-12341 | Pfa | Phase A Power Factor | PF=Rx | PF=Rx |  | Float | R
3036H-3037H | 12342-12343 | PFb | Phase B Power Factor | PF=Rx | PF=Rx |  | Float | R
3038H-3039H | 12344-12345 | PFc | Phase C Power Factor | PF=Rx | PF=Rx |  | Float | R
303AH-303BH | 12346-12347 | PFsum | Total Power Factor | PF=Rx | PF=Rx |  | Float | R

## 20ms High Speed Metering
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  |  | Primary Mode | Secondary Mode
3400H-3401H | 13312-13313 | Ua | Phase A Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3402H-3403H | 13314-13315 | Ub | Phase B Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3404H-3405H | 13316-13317 | Uc | Phase C Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3406H-3407H | 13318-13319 | Ia | Phase A Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
3408H-3409H | 13320-13321 | Ib | Phase B Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
340AH-340BH | 13322-13323 | Ic | Phase C Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
340CH-340DH | 13324-13325 | Pa | Phase A Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
340EH-340FH | 13326-13327 | Pb | Phase B Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
3410H-3411H | 13328-13329 | Pc | Phase C Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
3412H-3413H | 13330-13331 | Unavg | Average Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3414H-3415H | 13332-13333 | Iavg | Average Phase Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
3416H-3417H | 13334-13335 | Ulavg | Average Line-Line Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
3418H-3419H | 13336-13337 | Psum | Total Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
341AH-341BH | 13338-13339 | Qsum | Total Reactive Power | Q=Rx/1000 | Q=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kvar | Float | R
341CH-341DH | 13340-13341 | F | Frequency | F=Rx | F=Rx | Hz | Float | R

## Moving Average Parameters
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  | Primary Mode | Secondary Mode
493DH-493EH | 18749-18750 | Phase A Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
493FH-4940H | 18751-18752 | Phase B Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4941H-4942H | 18753-18754 | Phase C Line-Neutral Voltage | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4943H-4944H | 18755-18756 | Line Voltage AB | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4945H-4946H | 18757-18758 | Line Voltage BC | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4947H-4948H | 18759-18760 | Line Voltage CA | U=Rx | U=Rx*(PT1/PT2) | V | Float | R
4949H-494AH | 18761-18762 | Phase A Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
494BH-494CH | 18763-18764 | Phase B Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
494DH-494EH | 18765-18766 | Phase C Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
494FH-4950H | 18767-18768 | Neutral Current | I=Rx | I=Rx*(CT1/CT2) | A | Float | R
4951H-4952H | 18769-18770 | Phase A Active Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4953H-4954H | 18771-18772 | Phase B Active Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4955H-4956H | 18773-18774 | Phase C Active Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R
4957H-4958H | 18775-18776 | Phase A Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
4959H-495AH | 18777-18778 | Phase B Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
495BH-495CH | 18779-18780 | Phase C Apparent Power | S=Rx/1000 | S=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kVA | Float | R
495DH-495EH | 18781-18782 | Total System Active Power | P=Rx/1000 | P=[Rx*(PT1/PT2)*(CT1/CT2)]/1000 | kW | Float | R

## Energy
Energy Measurements: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Relationship |  | Range | Property | Data Type | Access Property
|  |  |  | Primary Mode | Secondary Mode
4048H-4049H | 16456-16457 | Ep_Imp | Consumed Energy | Ep_Imp=Rx/10 | Ep_Imp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
404AH-404BH | 16458-16459 | Ep_Exp | Generated Energy | Ep_Exp=Rx/10 | Ep_Exp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
404CH-404DH | 16460-16461 | Eq_Imp | Consumed Reactive Energy | Eq_Imp=Rx/10 | Eq_Imp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
404EH-404FH | 16462-16463 | Eq_Exp | Generated Reactive Energy | Eq_Exp=Rx/10 | Eq_Exp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4050H-4051H | 16464-16465 | Ep_Sum | Total Energy | Ep_sum=Rx/10 | Ep_sum=Rx/1000 | 0~999999999 | kWh | Dword | R/W
4052H-4053H | 16466-16467 | Ep_Net | Net Energy | Ep_net=Rx/10 | Ep_net=Rx/1000 | ±999999999 | kWh | Dword | R/W
4054H-4055H | 16468-16469 | Eq_Sum | Total Reactive Energy | Eq_sum=Rx/10 | Eq_sum=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4056H-4057H | 16470-16471 | Eq_Net | Net Reactive Energy | Eq_net=Rx/10 | Eq_net=Rx/1000 | ±999999999 | kvarh | Dword | R/W
4058H-4059H | 16472-16473 | Es | Apparent Energy | Es=Rx/10 | Es=Rx/1000 | 0~999999999 | kVAh | Dword | R/W
4620H-4621H | 17952-17953 | Epa_Imp | Phase A Consumed Energy | Epa_Imp=Rx/10 | Epa_Imp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
4622H-4623H | 17954-17955 | Epa_Exp | Phase A Generated Energy | Epa_Exp=Rx/10 | Epa_Exp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
4624H-4625H | 17956-17957 | Epb_Imp | Phase B Consumed Energy | Epb_Imp=Rx/10 | Epb_Imp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
4626H-4627H | 17958-17959 | Epb_Exp | Phase B Generated Energy | Epb_Exp=Rx/10 | Epb_Exp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
4628H-4629H | 17960-17961 | Epc_Imp | Phase C Consumed Energy | Epc_Imp=Rx/10 | Epc_Imp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
462AH-462BH | 17962-17963 | Epc_Exp | Phase C Generated Energy | Epc_Exp=Rx/10 | Epc_Imp=Rx/1000 | 0~999999999 | kWh | Dword | R/W
462CH-462DH | 17964-17965 | Eqa_Imp | Phase A Consumed Reactive Energy | Eqa_Imp=Rx/10 | Eqa_Imp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
462EH-462FH | 17966-17967 | Eqa_Exp | Phase A Generated Reactive Energy | Eqa_Exp=Rx/10 | Eqa_Exp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4630H-4631H | 17968-17969 | Eqb_Imp | Phase B Consumed Reactive Energy | Eqb_Imp=Rx/10 | Eqb_Imp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4632H-4633H | 17970-17971 | Eqb_Exp | Phase B Generated Reactive Energy | Eqb_Exp=Rx/10 | Eqb_Exp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4634H-4635H | 17972-17973 | Eqc_Imp | Phase C Consumed Reactive Energy | Eqc_Imp=Rx/10 | Eqc_Imp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4636H-4637H | 17974-17975 | Eqc_Exp | Phase C Generated Reactive Energy | Eqc_Exp=Rx/10 | Eqc_Exp=Rx/1000 | 0~999999999 | kvarh | Dword | R/W
4638H-4639H | 17976-17977 | Esa | Phase A Apparent Energy | Esa=Rx/10 | Esa=Rx/1000 | 0~999999999 | kVAh | Dword | R/W
463AH-463BH | 17978-17979 | Esb | Phase B Apparent Energy | Esb=Rx/10 | Esb=Rx/1000 | 0~999999999 | kVAh | Dword | R/W
463CH-463DH | 17980-17981 | Esc | Phase C Apparent Energy | Esc=Rx/10 | Esc=Rx/1000 | 0~999999999 | kVAh | Dword | R/W

## TOU Energy
Current Month Accumulation TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Property | Data Type | Access Property
Sharp
7200H-7201H | 29184-29185 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7202H-7203H | 29186-29187 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7204H-7205H | 29188-29189 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7206H-7207H | 29190-29191 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7208H-7209H | 29192-29193 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Peak
720AH-720BH | 29194-29195 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
720CH-720DH | 29196-29197 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
720EH-720FH | 29198-29199 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7210H-7211H | 29200-29201 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7212H-7213H | 29202-29203 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Valley
7214H-7215H | 29204-29205 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7216H-7217H | 29206-29207 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7218H-7219H | 29208-29209 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
721AH-721BH | 29210-29211 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
721CH-721DH | 29212-29213 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Normal
721EH-721FH | 29214-29215 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7220H-7221H | 29216-29217 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7222H-7223H | 29218-29219 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7224H-7225H | 29220-29221 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7226H-7227H | 29222-29223 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Total
7228H-7229H | 29224-29225 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
722AH-722BH | 29226-29227 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
722CH-722DH | 29228-29229 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
722EH-722FH | 29230-29231 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7230H-7231H | 29232-29233 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Prior Month Accumulation TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Property | Data Type | Access Property
Sharp
7232H-7233H | 29234-29235 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7234H-7235H | 29236-29237 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7236H-7237H | 29238-29239 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7238H-7239H | 29240-29241 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
723AH-723BH | 29242-29243 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Peak
723CH-723DH | 29244-29245 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
723EH-723FH | 29246-29247 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7240H-7241H | 29248-29249 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7242H-7243H | 29250-29251 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7244H-7245H | 29252-29253 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Valley
7246H-7247H | 29254-29255 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7248H-7249H | 29256-29257 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
724AH-724BH | 29258-29259 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
724CH-724DH | 29260-29261 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
724EH-724FH | 29262-29263 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Normal
7250H-7251H | 29264-29265 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7252H-7253H | 29266-29267 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7254H-7255H | 29268-29269 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7256H-7257H | 29270-29271 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7258H-7259H | 29272-29273 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Total
725AH-725BH | 29274-29275 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
725CH-725DH | 29276-29277 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
725EH-725FH | 29278-29279 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7260H-7261H | 29280-29281 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7262H-7263H | 29282-29283 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Current Month(Incremental) TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Property | Data Type | Access Property
Sharp
7300H-7301H | 29440-29441 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7302H-7303H | 29442-29443 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7304H-7305H | 29444-29445 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7306H-7307H | 29446-29447 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7308H-7309H | 29448-29449 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Peak
730AH-730BH | 29450-29451 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
730CH-730DH | 29452-29453 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
730EH-730FH | 29454-29455 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7310H-7311H | 29456-29457 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7312H-7313H | 29458-29459 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Valley
7314H-7315H | 29460-29461 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7316H-7317H | 29462-29463 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7318H-7319H | 29464-29465 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
731AH-731BH | 29466-29467 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
731CH-731DH | 29468-29469 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Normal
731EH-731FH | 29470-29471 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7320H-7321H | 29472-29473 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7322H-7323H | 29474-29475 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7324H-7325H | 29476-29477 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7326H-7327H | 29478-29479 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Total
7328H-7329H | 29480-29481 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
732AH-732BH | 29482-29483 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
732CH-732DH | 29484-29485 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
732EH-732FH | 29486-29487 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7330H-7331H | 29488-29489 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Prior Month(Incremental) TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Property | Data Type | Access Property
Sharp
7332H-7333H | 29490-29491 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7334H-7335H | 29492-29493 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7336H-7337H | 29494-29495 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7338H-7339H | 29496-29497 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
733AH-733BH | 29498-29499 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Peak
733CH-733DH | 29500-29501 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
733EH-733FH | 29502-29503 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7340H-7341H | 29504-29505 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7342H-7343H | 29506-29507 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7344H-7345H | 29508-29509 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Valley
7346H-7347H | 29510-29511 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7348H-7349H | 29512-29513 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
734AH-734BH | 29514-29515 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
734CH-734DH | 29516-29517 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
734EH-734FH | 29518-29519 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Normal
7350H-7351H | 29520-29521 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
7352H-7353H | 29522-29523 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
7354H-7355H | 29524-29525 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7356H-7357H | 29526-29527 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7358H-7359H | 29528-29529 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Total
735AH-735BH | 29530-29531 | Ep_Imp | Consumed Energy | 0~999999999 | kWh | Dword | R/W
735CH-735DH | 29532-29533 | Ep_Exp | Generated Energy | 0~999999999 | kWh | Dword | R/W
735EH-735FH | 29534-29535 | Eq_Imp | Consumed Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7360H-7361H | 29536-29537 | Eq_Exp | Generated Reactive Energy | 0~999999999 | kvarh | Dword | R/W
7362H-7363H | 29538-29539 | Es | Apparent Energy | 0~999999999 | kVA | Dword | R/W
Current Month Maximum Demand TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Relationship | Range | Data Type | Access Property
Sharp
7500H | 29952 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7501H-7503H | 29953-29955 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7504H | 29956 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7505H-7507H | 29957-29959 |  | Time Stamp | YY/MM/DD/HH/Min/Sec |  |  |  | Relationship= Rx*(CT1/CT2)*(PT1/PT2)/1000
7508H | 29960 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7509H-750BH | 29961-29963 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
750CH | 29964 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
750DH-750FH | 29965-29967 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7510H | 29968 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7511H-7513H | 29969-29971 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7514H | 29972 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7515H-7517H | 29973-29975 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7518H | 29976 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7519H-751BH | 29977-29979 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
751CH | 29980 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
751DH-751FH | 29981-29983 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Peak
7520H | 29984 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7521H-7523H | 29985-29987 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7524H | 29988 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7525H-7527H | 29989-29991 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7528H | 29992 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7529H-752BH | 29993-29995 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
752CH | 29996 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
752DH-752FH | 29997-29999 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7530H | 30000 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7351H-7533H | 30001-30003 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7534H | 30004 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7535H-7537H | 30005-30007 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7538H | 30008 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7539H-753BH | 30009-30011 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
753CH | 30012 | Ic | Max Phase C Current Demand |  | -32768~32767 | Int | R
753DH-753FH | 30013-30015 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Valley
7540H | 30016 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7541H-7543H | 30017-30019 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7544H | 30020 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7545H-7547H | 30021-30023 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7548H | 30024 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7549H-754BH | 30025-30026 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
754CH | 30027 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
754DH-754FH | 30028-30031 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7550H | 30032 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7551H-7553H | 30033-30035 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7554H | 30036 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7555H-7557H | 30037-30039 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7558H | 30040 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7559H-755BH | 30041-30043 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
755CH | 30044 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
755DH-755FH | 30045-30047 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Normal
7560H | 30048 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7561H-7563H | 30049-30051 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7564H | 30052 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7565H-7567H | 30053-30055 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7568H | 30056 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7569H-756BH | 30057-30059 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
756CH | 30060 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
756DH-756FH | 30061-30063 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7570H | 30064 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7571H-7573H | 30065-30067 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7574H | 30068 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7575H-7577H | 30069-30071 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7578H | 30072 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7579H-757BH | 30073-30075 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
757CH | 30076 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
757DH-757FH | 30077-30079 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Total
7580H | 30080 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7581H-7583H | 30081-30083 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7584H | 30084 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7585H-7587H | 30085-30087 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7588H | 30088 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7589H-758BH | 30089-30091 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
758CH | 30092 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
758DH-758FH | 30093-30095 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7590H | 30096 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7591H-7593H | 30097-30099 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7594H | 30100 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7595H-7597H | 30101-30103 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7598H | 30104 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7599H-759BH | 30105-30107 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
759CH | 30108 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
759DH-759FH | 30109-30111 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Previous Month Maximum Demand TOU Energy: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Relationship | Range | Data Type | Access Property
Sharp
7600H | 30208 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7601H-7603H | 30209-30211 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7604H | 30212 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7605H-7607H | 30213-30215 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7608H | 30216 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7609H-760BH | 30217-30219 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
760CH | 30220 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
760DH-760FH | 30221-30223 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7610H | 30224 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7611H-7613H | 30225-30227 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7614H-7617H | 30228 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7615H-7617H | 30229-30231 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7618H | 30232 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7619H-761BH | 30233-30235 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
761CH | 30236 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
761DH-761FH | 30237-30239 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Peak
7620H | 30240 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7621H-7623H | 30241-30243 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7624H | 30244 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7625H-7627H | 30245-30247 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7628H | 30248 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7629H-762BH | 30249-30251 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
762CH | 30252 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
762DH-762FH | 30253-30255 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7630H | 30256 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7651H-7633H | 30257-30259 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7634H | 30260 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7635H-7637H | 30261-30263 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7638H | 30264 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7639H-763BH | 30265-30267 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
763CH | 30268 | Ic | Max Phase C Current Demand |  | -32768~32767 | Int | R
763DH-763FH | 30269-30271 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Valley
7610H | 30272 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7641H-7643H | 30273-30275 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7644H | 30276 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7645H-7647H | 30277-30279 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7648H | 30280 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7649H-764BH | 30281-30283 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
764CH | 30284 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
764DH-764FH | 30285-30287 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7650H | 30288 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7651H-7653H | 30289-30291 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7654H | 30292 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7655H-7657H | 30293-30295 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7658H | 30296 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7659H-765BH | 30297-30299 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
765CH | 30300 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
765DH-765FH | 30301-30303 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Normal
7660H | 30304 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7661H-7663H | 30305-30307 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7664H | 30308 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7665H-7667H | 30309-30311 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7668H | 30312 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7669H-766BH | 30313-30315 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
766CH | 30316 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
766DH-766FH | 30317-30319 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7670H | 30320 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7671H-7673H | 30321-30323 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7674H | 30324 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7675H-7677H | 30325-30327 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7678H | 30328 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7679H-767BH | 30329-30331 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
767CH | 30332 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
767DH-767FH | 30333-30335 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
Total
7680H | 30336 | Ep_Imp | Max Import Power Demand | Rx/10 | -32768~32767 | Int | R
7681H-7683H | 30337-30339 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7684H | 30340 | Ep_Exp | Max Export Power Demand | Rx/10 | -32768~32767 | Int | R
7685H-7687H | 30341-30343 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7688H | 30344 | Eq_Imp | Max Import Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
7689H-768BH | 30345-30347 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
768CH | 30348 | Eq_Exp | Max Export Reactive Power Demand | Rx/10 | -32768~32767 | Int | R
768DH-768FH | 30349-30351 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7690H | 30352 | Es | Max Apparent Power Demadn | Rx/10 | -32768~32767 | Int | R
7691H-7693H | 30353-30355 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7694H | 30356 | Ia | Max Phase A Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7695H-7697H | 30357-30359 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
7698H | 30360 | Ib | Max Phase B Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
7699H-769BH | 30361-30363 |  | Time Stamp | YY/MM/DD/HH/Min/Sec
769CH | 30364 | Ic | Max Phase C Current Demand | Rx*(CT1/CT2)/1000 | -32768~32767 | Int | R
769DH-769FH | 30365-30367 |  | Time Stamp | YY/MM/DD/HH/Min/Sec

## Dual Source Energy
Dual Source Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
1680H | 5760 | Dual Source Enable/Disable | 1: Enable 0: Disable | Word | R/W
1681H | 5761 | Energy Selection 1 | 0: Not Selected 1: Active Energy 2: Phase A Active Energy 3: Phase B Active Energy 4: Phase C Active Energy 5: Reactive Energy 6: Phase A Reactve Energy 7: Phase B Reactive Energy 8: Phase C Reactive Energy 9: Apparent Energy 10: Phase A Apparent Energy 11: Phase B Apparent Energy 12: Phase C Apparent Energy | Word | R/W
1682H | 5762 | Energy Selection 2 | 0: Not Selected 1: Active Energy 2: Phase A Active Energy 3: Phase B Active Energy 4: Phase C Active Energy 5: Reactive Energy 6: Phase A Reactve Energy 7: Phase B Reactive Energy 8: Phase C Reactive Energy 9: Apparent Energy 10: Phase A Apparent Energy 11: Phase B Apparent Energy 12: Phase C Apparent Energy | Word | R/W
1683H | 5763 | Energy Selection 3 | 0: Not Selected 1: Active Energy 2: Phase A Active Energy 3: Phase B Active Energy 4: Phase C Active Energy 5: Reactive Energy 6: Phase A Reactve Energy 7: Phase B Reactive Energy 8: Phase C Reactive Energy 9: Apparent Energy 10: Phase A Apparent Energy 11: Phase B Apparent Energy 12: Phase C Apparent Energy | Word | R/W
1684H | 5764 | Control Mode | 0: Communication 1-28: DI1-DI28 | Word | R/W
1685H | 5765 | Direction | 0: Grid 1: Generator | Word | R/W
1686H | 5766 | Clear Dual Source Energy | 0: No Clear 1: Clear | Word | R/W
1687H | 5767 | Clear Dual Source Swithching Record | 0: No Clear 1: Clear | Word | R/W
Dual Source Settings: 03H Read
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
4930H-4931H | 18736-18737 | Energy 1 - Grid Direction | 0-999,999,999 kWh | UINT32 | R
4932H-4933H | 18738-18739 | Energy 1 - Generator Direction | 0-999,999,999 kWh | UINT32 | R
4934H-4935H | 18740-18741 | Energy 2 - Grid Direction | 0-999,999,999 kvarh | UINT32 | R
4936H-4937H | 18742-18743 | Energy 2 - Generator Direction | 0-999,999,999 kvarh | UINT32 | R
4938H-4939H | 18744-18745 | Energy 3 - Grid Direction | 0-999,999,999 kVAh | UINT32 | R
493AH-493BH | 18746-18747 | Energy 3 - Generator Direction | 0-999,999,999 kVAh | UINT32 | R
Dual Source Settings: 03H Read
Address (Hex) | Address (Dec) | Parameter | Data Type | Access Property
6D00H | 27904 | Number of records to read | Word | R
6D01H | 27905 | ID of current switching record | Word | R
6D02H | 27906 | The length of bytes that can be read by the current window | Word | R
6D03H | 27907 | 1st switch record - timestamp year & month | Word | R
6D04H | 27908 | 1st switch record - timestamp day & hour | Word | R
6D05H | 27909 | 1st switch record - timestamp minute & second | Word | R
6D06H | 27910 | 1st switch record - switch command source | Word | R
6D07H | 27911 | 1st switch record - swith command | Word | R
6D08H-6D09H | 27912-27913 | 1st switch record - Energy 1 - Grid Direction | Word | R
6D0AH-6D0BH | 27914-27915 | 1st switch record - Energy 1 - Generator Direction | Word | R
6D0CH-6D0DH | 27916-27917 | 1st switch record - Energy 2 - Grid Direction | Word | R
6D0EH-6D0FH | 27918-27919 | 1st switch record - Energy 2 - Generator Direction | Word | R
6D10H-6D11H | 27920-27921 | 1st switch record - Energy 3 - Grid Direction | Word | R
6D12H-6D13H | 27922-27923 | 1st switch record - Energy 3 - Generator Direction | Word | R
6D14H-6D24H | 27924-27940 | 2nd switch record data | Word | R
6D25H-6D35H | 27941-27957 | 3rd switch record data | Word | R
6D36H-6D46H | 27958-27974 | 4th switch record data | Word | R
6D47H-6D57H | 27975-27991 | 5th switch record data | Word | R

## THD
Power Quality: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
405AH | 16474 | THD_Va(Vab) | THD=Rx/100 | % | ≥0 | Word | R
405BH | 16475 | THD_Vb(Vca) | THD=Rx/100 | % | ≥0 | Word | R
405CH | 16476 | THD_Vc(Vbc) | THD=Rx/100 | % | ≥0 | Word | R
405DH | 16477 | THD_avg | THD=Rx/100 | % | ≥0 | Word | R
405EH | 16478 | THD_Ia | THD=Rx/100 | % | ≥0 | Word | R
405FH | 16479 | THD_Ib | THD=Rx/100 | % | ≥0 | Word | R
4060H | 16480 | THD_Ic | THD=Rx/100 | % | ≥0 | Word | R
4061H | 16481 | THD_Iavg | THD=Rx/100 | % | ≥0 | Word | R
412BH | 16683 | TDD_I1 | TDD=Rx/100 | % | ≥0 | Word | R
412CH | 16684 | TDD_I2 | TDD=Rx/100 | % | ≥0 | Word | R
412DH | 16685 | TDD_I3 | TDD=Rx/100 | % | ≥0 | Word | R
412EH | 16686 | TDD_Iavg | TDD=Rx/100 | % | ≥0 | Word | R

## Voltage Harmonics
Voltage Harmonics, Even & Odd Harmonics, Crest Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Va/Vab Harmonics
4062H | 16482 | Va(Vab) 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4063H | 16483 | Va(Vab) 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4064H | 16484 | Va(Vab) 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4065H | 16485 | Va(Vab) 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4066H | 16486 | Va(Vab) 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4067H | 16487 | Va(Vab) 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4068H | 16488 | Va(Vab) 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4069H | 16489 | Va(Vab) 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406AH | 16490 | Va(Vab) 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406BH | 16491 | Va(Vab) 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406CH | 16492 | Va(Vab) 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406DH | 16493 | Va(Vab) 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406EH | 16494 | Va(Vab) 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
406FH | 16495 | Va(Vab) 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4070H | 16496 | Va(Vab) 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4071H | 16497 | Va(Vab) 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4072H | 16498 | Va(Vab) 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4073H | 16499 | Va(Vab) 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4074H | 16500 | Va(Vab) 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4075H | 16501 | Va(Vab) 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4076H | 16502 | Va(Vab) 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4077H | 16503 | Va(Vab) 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4078H | 16504 | Va(Vab) 24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4079H | 16505 | Va(Vab) 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407AH | 16506 | Va(Vab) 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407BH | 16507 | Va(Vab) 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407CH | 16508 | Va(Vab) 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407DH | 16509 | Va(Vab) 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407EH | 16510 | Va(Vab) 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
407FH | 16511 | Va(Vab) 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4500H | 17664 | Va(Vab) 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4501H | 17665 | Va(Vab) 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4502H | 17666 | Va(Vab) 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4503H | 17667 | Va(Vab) 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4504H | 17668 | Va(Vab) 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4505H | 17669 | Va(Vab) 37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4506H | 17670 | Va(Vab) 38th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4507H | 17671 | Va(Vab) 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4508H | 17672 | Va(Vab) 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4509H | 17673 | Va(Vab) 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450AH | 17674 | Va(Vab) 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450BH | 17675 | Va(Vab) 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450CH | 17676 | Va(Vab) 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450DH | 17677 | Va(Vab) 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450EH | 17678 | Va(Vab) 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
450FH | 17679 | Va(Vab) 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4510H | 17680 | Va(Vab) 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4511H | 17681 | Va(Vab) 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4512H | 17682 | Va(Vab) 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4513H | 17683 | Va(Vab) 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4514H | 17684 | Va(Vab) 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4515H | 17685 | Va(Vab) 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4516H | 17686 | Va(Vab) 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4517H | 17687 | Va(Vab) 55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4518H | 17688 | Va(Vab) 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4519H | 17689 | Va(Vab) 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451AH | 17690 | Va(Vab) 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451BH | 17691 | Va(Vab) 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451CH | 17692 | Va(Vab) 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451DH | 17693 | Va(Vab) 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451EH | 17694 | Va(Vab) 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
451FH | 17695 | Va(Vab) 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4080H | 16512 | Odd THD_Va(Vab) | THD=Rx/100 | % | ≥0 | Word | R
4081H | 16513 | Even THD_Va(Vab) | THD=Rx/100 | % | ≥0 | Word | R
4082H | 16514 | Crest Factor Va(Vab) | CF=Rx/100 | % | 0~65535 | Word | R
4083H | 16515 | THFF_Va(Vab) | THFF=Rx/100 | % | ≥0 | Word | R
Voltage Harmonics, Even & Odd Harmonics, Crest Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Vb/Vca Harmonics
4084H | 16516 | V2(V31) 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4085H | 16517 | V2(V31) 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4086H | 16518 | V2(V31) 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4087H | 16519 | V2(V31) 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4088H | 16520 | V2(V31) 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4089H | 16521 | V2(V31) 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408AH | 16522 | V2(V31) 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408BH | 16523 | V2(V31) 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408CH | 16524 | V2(V31) 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408DH | 16525 | V2(V31) 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408EH | 16526 | V2(V31) 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
408FH | 16527 | V2(V31) 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4090H | 16528 | V2(V31) 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4091H | 16529 | V2(V31) 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4092H | 16530 | V2(V31) 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4093H | 16531 | V2(V31) 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4094H | 16532 | V2(V31) 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4095H | 16533 | V2(V31) 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4096H | 16534 | V2(V31) 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4097H | 16535 | V2(V31) 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4098H | 16536 | V2(V31) 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4099H | 16537 | V2(V31) 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409AH | 16538 | V2(V31)24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409BH | 16539 | V2(V31) 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409CH | 16540 | V2(V31) 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409DH | 16541 | V2(V31) 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409EH | 16542 | V2(V31) 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
409FH | 16543 | V2(V31) 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A0H | 16544 | V2(V31) 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A1H | 16545 | V2(V31) 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4520H | 17696 | V2(V31) 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4521H | 17697 | V2(V31) 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4522H | 17698 | V2(V31) 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4523H | 17699 | V2(V31) 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4524H | 17700 | V2(V31) 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4525H | 17701 | V2(V31)37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4526H | 17702 | V2(V31) 38th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4527H | 17703 | V2(V31) 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4528H | 17704 | V2(V31) 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4529H | 17705 | V2(V31) 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452AH | 17706 | V2(V31) 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452BH | 17707 | V2(V31) 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452CH | 17708 | V2(V31) 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452DH | 17709 | V2(V31) 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452EH | 17710 | V2(V31) 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
452FH | 17711 | V2(V31) 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4530H | 17712 | V2(V31) 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4531H | 17713 | V2(V31) 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4532H | 17714 | V2(V31) 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4323H | 17187 | V2(V31) 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4534H | 17716 | V2(V31) 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4535H | 17717 | V2(V31) 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4536H | 17718 | V2(V31) 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4537H | 17719 | V2(V31)55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4538H | 17720 | V2(V31) 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4539H | 17721 | V2(V31) 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453AH | 17722 | V2(V31) 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453BH | 17723 | V2(V31) 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453CH | 17724 | V2(V31) 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453DH | 17725 | V2(V31) 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453EH | 17726 | V2(V31) 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
453FH | 17727 | V2(V31) 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A2H | 16546 | Odd THD_V2(V31) | THD=Rx/100 | % | ≥0 | Word | R
40A3H | 16547 | Even THD_V2(V31) | THD=Rx/100 | % | ≥0 | Word | R
40A4H | 16548 | Crest Factor V2(V31) | CF=Rx/100 | % | 0~65535 | Word | R
40A5H | 16549 | THFF_V2(V31) | THFF=Rx/100 | % | ≥0 | Word | R
Voltage Harmonics, Even & Odd Harmonics, Crest Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Vc/Vbc Harmonics
40A6H | 16550 | V3(V23) 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A7H | 16551 | V3(V23) 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A8H | 16552 | V3(V23) 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40A9H | 16553 | V3(V23) 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40AAH | 16554 | V3(V23) 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40ABH | 16555 | V3(V23) 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40ACH | 16556 | V3(V23) 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40ADH | 16557 | V3(V23) 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40AEH | 16558 | V3(V23) 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40AFH | 16559 | V3(V23) 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B0H | 16560 | V3(V23) 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B1H | 16561 | V3(V23) 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B2H | 16562 | V3(V23) 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B3H | 16563 | V3(V23) 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B4H | 16564 | V3(V23) 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B5H | 16565 | V3(V23) 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B6H | 16566 | V3(V23) 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B7H | 16567 | V3(V23) 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B8H | 16568 | V3(V23) 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40B9H | 16569 | V3(V23) 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BAH | 16570 | V3(V23) 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BBH | 16571 | V3(V23) 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BCH | 16572 | V3(V23) 24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BDH | 16573 | V3(V23) 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BEH | 16574 | V3(V23) 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40BFH | 16575 | V3(V23) 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C0H | 16576 | V3(V23) 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C1H | 16577 | V3(V23) 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C2H | 16578 | V3(V23) 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C3H | 16579 | V3(V23) 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4540H | 17728 | V3(V23) 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4541H | 17729 | V3(V23) 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4542H | 17730 | V3(V23) 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4543H | 17731 | V3(V23) 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4544H | 17732 | V3(V23) 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4545H | 17733 | V3(V23) 37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4546H | 17734 | V3(V23) 38th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4547H | 17735 | V3(V23) 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4548H | 17736 | V3(V23) 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4549H | 17737 | V3(V23) 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454AH | 17738 | V3(V23) 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454BH | 17739 | V3(V23) 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454CH | 17740 | V3(V23) 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454DH | 17741 | V3(V23) 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454EH | 17742 | V3(V23) 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
454FH | 17743 | V3(V23) 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4550H | 17744 | V3(V23) 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4551H | 17745 | V3(V23) 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4552H | 17746 | V3(V23) 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4553H | 17747 | V3(V23) 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4554H | 17748 | V3(V23) 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4555H | 17749 | V3(V23) 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4556H | 17750 | V3(V23) 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4557H | 17751 | V3(V23) 55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4558H | 17752 | V3(V23) 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4559H | 17753 | V3(V23) 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455AH | 17754 | V3(V23) 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455BH | 17755 | V3(V23) 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455CH | 17756 | V3(V23) 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455DH | 17757 | V3(V23) 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455EH | 17758 | V3(V23) 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
455FH | 17759 | V3(V23) 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C4H | 16580 | Odd THD_V3(V23) | THD=Rx/100 | % | ≥0 | Word | R
40C5H | 16581 | Even THD_V3(V23) | THD=Rx/100 | % | ≥0 | Word | R
40C6H | 16582 | Crest Factor V3(V23) | CF=Rx/100 | % | 0~65535 | Word | R
40C7H | 16583 | THFF_V3(V23) | THFF=Rx/100 | % | ≥0 | Word | R

## Current Harmonics
Current Harmonics, Even & Odd Harmonics, K Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ia Harmonics
40C8H | 16584 | I1 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40C9H | 16585 | I1 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CAH | 16586 | I1 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CBH | 16587 | I1 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CCH | 16588 | I1 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CDH | 16589 | I1 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CEH | 16590 | I1 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40CFH | 16591 | I1 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D0H | 16592 | I1 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D1H | 16593 | I1 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D2H | 16594 | I1 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D3H | 16595 | I1 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D4H | 16596 | I1 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D5H | 16597 | I1 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D6H | 16598 | I2 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D7H | 16599 | I1 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D8H | 16600 | I1 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40D9H | 16601 | I1 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DAH | 16602 | I1 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DBH | 16603 | I1 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DCH | 16604 | I1 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DDH | 16605 | I1 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DEH | 16606 | I1 24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40DFH | 16607 | I1 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E0H | 16608 | I1 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E1H | 16609 | I1 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E2H | 16610 | I1 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E3H | 16611 | I1 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E4H | 16612 | I1 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E5H | 16613 | I1 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4560H | 17760 | I1 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4561H | 17761 | I1 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4562H | 17762 | I1 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4563H | 17763 | I1 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4564H | 17764 | I1 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4565H | 17765 | I1 37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4566H | 17766 | I138th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4567H | 17767 | I1 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4568H | 17768 | I1 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4569H | 17769 | I1 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456AH | 17770 | I1 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456BH | 17771 | I1 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456CH | 17772 | I1 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456DH | 17773 | I1 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456EH | 17774 | I1 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
456FH | 17775 | I1 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4570H | 17776 | I1 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4571H | 17777 | I1 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4572H | 17778 | I1 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4573H | 17779 | I1 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4574H | 17780 | I1 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4575H | 17781 | I1 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4576H | 17782 | I1 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4577H | 17783 | I1 55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4578H | 17784 | I1 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4579H | 17785 | I1 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457AH | 17786 | I1 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457BH | 17787 | I1 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457CH | 17788 | I1 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457DH | 17789 | I1 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457EH | 17790 | I1 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
457FH | 17791 | I1 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40E6H | 16614 | Odd THD_I1 | THD=Rx/100 | % | ≥0 | Word | R
40E7H | 16615 | Even THD_I1 | THD=Rx/100 | % | ≥0 | Word | R
40E8H | 16616 | K Factor of I1 | CF=Rx/100 | % | 0~65535 | Word | R
Current Harmonics, Even & Odd Harmonics, K Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ib Harmonics
40E9H | 16617 | I2 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40EAH | 16618 | I2 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40EBH | 16619 | I2 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40ECH | 16620 | I2 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40EDH | 16621 | I2 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40EEH | 16622 | I2 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40EFH | 16623 | I2 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F0H | 16624 | I2 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F1H | 16625 | I2 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F2H | 16626 | I2 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F3H | 16627 | I2 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F4H | 16628 | I2 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F5H | 16629 | I2 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F6H | 16630 | I2 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F7H | 16631 | I2 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F8H | 16632 | I2 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40F9H | 16633 | I2 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FAH | 16634 | I2 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FBH | 16635 | I2 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FCH | 16636 | I2 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FDH | 16637 | I2 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FEH | 16638 | I2 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
40FFH | 16639 | I2 24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4100H | 16640 | I2 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4101H | 16641 | I2 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4102H | 16642 | I2 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4103H | 16643 | I2 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4104H | 16644 | I2 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4105H | 16645 | I2 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4106H | 16646 | I2 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4580H | 17792 | I2 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4581H | 17793 | I2 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4582H | 17794 | I2 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4583H | 17795 | I2 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4584H | 17796 | I2 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4585H | 17797 | I2 37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4586H | 17798 | I2 38th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4587H | 17799 | I2 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4588H | 17800 | I2 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4589H | 17801 | I2 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458AH | 17802 | I2 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458BH | 17803 | I2 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458CH | 17804 | I2 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458DH | 17805 | I2 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458EH | 17806 | I2 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
458FH | 17807 | I2 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4590H | 17808 | I2 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4591H | 17809 | I2 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4592H | 17810 | I2 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4593H | 17811 | I2 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4594H | 17812 | I2 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4595H | 17813 | I2 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4596H | 17814 | I2 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4597H | 17815 | I2 55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4598H | 17816 | I2 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4599H | 17817 | I2 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459AH | 17818 | I2 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459BH | 17819 | I2 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459CH | 17820 | I2 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459DH | 17821 | I2 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459EH | 17822 | I2 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
459FH | 17823 | I2 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4107H | 16647 | Odd THD_I2 | THD=Rx/100 | % | ≥0 | Word | R
4108H | 16648 | Even THD_I2 | THD=Rx/100 | % | ≥0 | Word | R
4109H | 16649 | K Factor of I2 | CF=Rx/100 | % | 0~65535 | Word | R
Current Harmonics, Even & Odd Harmonics, K Factor: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ic Harmonics
410AH | 16650 | I3 2nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
410BH | 16651 | I3 3rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
410CH | 16652 | I3 4th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
410DH | 16653 | I3 5th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
410EH | 16654 | I3 6th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
410FH | 16655 | I3 7th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4110H | 16656 | I3 8th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4111H | 16657 | I3 9th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4112H | 16658 | I3 10th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4113H | 16659 | I3 11th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4114H | 16660 | I3 12th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4115H | 16661 | I3 13th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4116H | 16662 | I3 14th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4117H | 16663 | I3 15th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4118H | 16664 | I3 16th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4119H | 16665 | I3 17th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411AH | 16666 | I3 18th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411BH | 16667 | I3 19th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411CH | 16668 | I3 20th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411DH | 16669 | I3 21st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411EH | 16670 | I3 22nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
411FH | 16671 | I3 23rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4120H | 16672 | I3 24th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4121H | 16673 | I3 25th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4122H | 16674 | I3 26th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4123H | 16675 | I3 27th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4124H | 16676 | I3 28th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4125H | 16677 | I3 29th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4126H | 16678 | I3 30th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4127H | 16679 | I3 31st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A0H | 17824 | I3 32nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A1H | 17825 | I3 33rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A2H | 17826 | I3 34th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A3H | 17827 | I3 35th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A4H | 17828 | I3 36th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A5H | 17829 | I3 37th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A6H | 17830 | I3 38th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A7H | 17831 | I3 39th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A8H | 17832 | I3 40th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45A9H | 17833 | I3 41st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45AAH | 17834 | I3 42nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45ABH | 17835 | I3 43rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45ACH | 17836 | I3 44th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45ADH | 17837 | I3 45th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45AEH | 17838 | I3 46th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45AFH | 17839 | I3 47th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B0H | 17840 | I3 48th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B1H | 17841 | I3 49th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B2H | 17842 | I3 50th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B3H | 17843 | I3 51st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B4H | 17844 | I3 52nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B5H | 17845 | I3 53rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B6H | 17846 | I3 54th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B7H | 17847 | I3 55th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B8H | 17848 | I3 56th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45B9H | 17849 | I3 57th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BAH | 17850 | I3 58th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BBH | 17851 | I3 59th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BCH | 17852 | I3 60th Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BDH | 17853 | I3 61st Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BEH | 17854 | I3 62nd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
45BFH | 17855 | I3 63rd Harmonic | THD=Rx/100 | % | ≥0 | Word | R
4128H | 16680 | Odd THD_I3 | THD=Rx/100 | % | ≥0 | Word | R
4129H | 16681 | Even THD_I3 | THD=Rx/100 | % | ≥0 | Word | R
412AH | 16682 | K Factor of I3 | CF=Rx/100 | % | 0~65535 | Word | R

## Voltage Amplitude & Phase
Voltage Harmonic Amplitude: 03H Read | [7 empty] | Voltage Harmonic Phase Angle: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Va/Vab Harmonic Amplitude | [7 empty] | Va/Vab Harmonic Phase Angle
6E00H | 28160 | V1(V12) 2nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F74H | 28532 | V1(V12) 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E01H | 28161 | V1(V12) 3rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F75H | 28533 | V1(V12) 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E02H | 28162 | V1(V12) 4th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F76H | 28534 | V1(V12) 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E03H | 28163 | V1(V12) 5th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F77H | 28535 | V1(V12) 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E04H | 28164 | V1(V12) 6th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F78H | 28536 | V1(V12) 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E05H | 28165 | V1(V12) 7th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F79H | 28537 | V1(V12) 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E06H | 28166 | V1(V12) 8th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7AH | 28538 | V1(V12) 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E07H | 28167 | V1(V12) 9th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7BH | 28539 | V1(V12) 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E08H | 28168 | V1(V12) 10th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7CH | 28540 | V1(V12) 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E09H | 28169 | V1(V12) 11th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7DH | 28541 | V1(V12) 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0AH | 28170 | V1(V12) 12th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7EH | 28542 | V1(V12) 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0BH | 28171 | V1(V12) 13th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F7FH | 28543 | V1(V12) 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0CH | 28172 | V1(V12) 14th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F80H | 28544 | V1(V12) 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0DH | 28173 | V1(V12) 15th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F81H | 28545 | V1(V12) 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0EH | 28174 | V1(V12) 16th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F82H | 28546 | V1(V12) 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E0FH | 28175 | V1(V12) 17th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F83H | 28547 | V1(V12) 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E10H | 28176 | V1(V12) 18th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F84H | 28548 | V1(V12) 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E11H | 28177 | V1(V12) 19th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F85H | 28549 | V1(V12) 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E12H | 28178 | V1(V12) 20th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F86H | 28550 | V1(V12) 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E13H | 28179 | V1(V12) 21st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F87H | 28551 | V1(V12) 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E14H | 28180 | V1(V12) 22nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F88H | 28552 | V1(V12) 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E15H | 28181 | V1(V12) 23rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F89H | 28553 | V1(V12) 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E16H | 28182 | V1(V12) 24th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8AH | 28554 | V1(V12) 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E17H | 28183 | V1(V12) 25th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8BH | 28555 | V1(V12) 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E18H | 28184 | V1(V12) 26th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8CH | 28556 | V1(V12) 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E19H | 28185 | V1(V12) 27th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8DH | 28557 | V1(V12) 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1AH | 28186 | V1(V12) 28th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8EH | 28558 | V1(V12) 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1BH | 28187 | V1(V12) 29th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F8FH | 28559 | V1(V12) 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1CH | 28188 | V1(V12) 30th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F90H | 28560 | V1(V12) 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1DH | 28189 | V1(V12) 31st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F91H | 28561 | V1(V12) 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1EH | 28190 | V1(V12) 32nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F92H | 28562 | V1(V12) 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E1FH | 28191 | V1(V12) 33rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F93H | 28563 | V1(V12) 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E20H | 28192 | V1(V12) 34th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F94H | 28564 | V1(V12) 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E21H | 28193 | V1(V12) 35th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F95H | 28565 | V1(V12) 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E22H | 28194 | V1(V12) 36th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F96H | 28566 | V1(V12) 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E23H | 28195 | V1(V12) 37th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F97H | 28567 | V1(V12) 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E24H | 28196 | V1(V12) 38th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F98H | 28568 | V1(V12) 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E25H | 28197 | V1(V12) 39th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F99H | 28569 | V1(V12) 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E26H | 28198 | V1(V12) 40th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9AH | 28570 | V1(V12) 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E27H | 28199 | V1(V12) 41st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9BH | 28571 | V1(V12) 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E28H | 28200 | V1(V12) 42nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9CH | 28572 | V1(V12) 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E29H | 28201 | V1(V12) 43rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9DH | 28573 | V1(V12) 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2AH | 28202 | V1(V12) 44th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9EH | 28574 | V1(V12) 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2BH | 28203 | V1(V12) 45th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6F9FH | 28575 | V1(V12) 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2CH | 28204 | V1(V12) 46th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA0H | 28576 | V1(V12) 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2DH | 28205 | V1(V12) 47th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA1H | 28577 | V1(V12) 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2EH | 28206 | V1(V12) 48th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA2H | 28578 | V1(V12) 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E2FH | 28207 | V1(V12) 49th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA3H | 28579 | V1(V12) 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E30H | 28208 | V1(V12) 50th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA4H | 28580 | V1(V12) 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E31H | 28209 | V1(V12) 51st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA5H | 28581 | V1(V12) 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E32H | 28210 | V1(V12) 52nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA6H | 28582 | V1(V12) 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E33H | 28211 | V1(V12) 53rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA7H | 28583 | V1(V12) 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E34H | 28212 | V1(V12) 54th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA8H | 28584 | V1(V12) 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E35H | 28213 | V1(V12) 55th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FA9H | 28585 | V1(V12) 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E36H | 28214 | V1(V12) 56th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FAAH | 28586 | V1(V12) 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E37H | 28215 | V1(V12) 57th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FABH | 28587 | V1(V12) 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E38H | 28216 | V1(V12) 58th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FACH | 28588 | V1(V12) 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E39H | 28217 | V1(V12) 59th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FADH | 28589 | V1(V12) 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E3AH | 28218 | V1(V12) 60th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FAEH | 28590 | V1(V12) 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E3BH | 28219 | V1(V12) 61st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FAFH | 28591 | V1(V12) 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E3CH | 28220 | V1(V12) 62nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB0H | 28592 | V1(V12) 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E3DH | 28221 | V1(V12) 63rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB1H | 28593 | V1(V12) 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
Voltage Harmonic Amplitude: 03H Read | [7 empty] | Voltage Harmonic Phase Angle: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Vb/Vca Harmonic Amplitude | [7 empty] | Vb/Vca Harmonic Amplitude
6E3EH | 28222 | V2(V31) 2nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB2H | 28594 | V2(V31) 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E3FH | 28223 | V2(V31) 3rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB3H | 28595 | V2(V31) 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E40H | 28224 | V2(V31) 4th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB4H | 28596 | V2(V31) 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E41H | 28225 | V2(V31) 5th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB5H | 28597 | V2(V31) 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E42H | 28226 | V2(V31) 6th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB6H | 28598 | V2(V31) 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E43H | 28227 | V2(V31) 7th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB7H | 28599 | V2(V31) 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E44H | 28228 | V2(V31) 8th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB8H | 28600 | V2(V31) 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E45H | 28229 | V2(V31) 9th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FB9H | 28601 | V2(V31) 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E46H | 28230 | V2(V31) 10th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBAH | 28602 | V2(V31) 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E47H | 28231 | V2(V31) 11th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBBH | 28603 | V2(V31) 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E48H | 28232 | V2(V31) 12th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBCH | 28604 | V2(V31) 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E49H | 28233 | V2(V31) 13th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBDH | 28605 | V2(V31) 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4AH | 28234 | V2(V31) 14th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBEH | 28606 | V2(V31) 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4BH | 28235 | V2(V31) 15th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FBFH | 28607 | V2(V31) 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4CH | 28236 | V2(V31) 16th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC0H | 28608 | V2(V31) 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4DH | 28237 | V2(V31) 17th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC1H | 28609 | V2(V31) 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4EH | 28238 | V2(V31) 18th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC2H | 28610 | V2(V31) 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E4FH | 28239 | V2(V31) 19th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC3H | 28611 | V2(V31) 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E50H | 28240 | V2(V31) 20th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC4H | 28612 | V2(V31) 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E51H | 28241 | V2(V31) 21st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC5H | 28613 | V2(V31) 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E52H | 28242 | V2(V31) 22nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC6H | 28614 | V2(V31) 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E53H | 28243 | V2(V31) 23rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC7H | 28615 | V2(V31) 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E54H | 28244 | V2(V31) 24th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC8H | 28616 | V2(V31) 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E55H | 28245 | V2(V31) 25th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FC9H | 28617 | V2(V31) 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E56H | 28246 | V2(V31) 26th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCAH | 28618 | V2(V31) 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E57H | 28247 | V2(V31) 27th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCBH | 28619 | V2(V31) 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E58H | 28248 | V2(V31) 28th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCCH | 28620 | V2(V31) 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E59H | 28249 | V2(V31) 29th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCDH | 28621 | V2(V31) 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5AH | 28250 | V2(V31) 30th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCEH | 28622 | V2(V31) 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5BH | 28251 | V2(V31) 31st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FCFH | 28623 | V2(V31) 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5CH | 28252 | V2(V31) 32nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD0H | 28624 | V2(V31) 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5DH | 28253 | V2(V31) 33rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD1H | 28625 | V2(V31) 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5EH | 28254 | V2(V31) 34th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD2H | 28626 | V2(V31) 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E5FH | 28255 | V2(V31) 35th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD3H | 28627 | V2(V31) 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E60H | 28256 | V2(V31) 36th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD4H | 28628 | V2(V31) 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E61H | 28257 | V2(V31) 37th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD5H | 28629 | V2(V31) 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E62H | 28258 | V2(V31) 38th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD6H | 28630 | V2(V31) 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E63H | 28259 | V2(V31) 39th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD7H | 28631 | V2(V31) 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E64H | 28260 | V2(V31) 40th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD8H | 28632 | V2(V31) 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E65H | 28261 | V2(V31) 41st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FD9H | 28633 | V2(V31) 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E66H | 28262 | V2(V31) 42nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDAH | 28634 | V2(V31) 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E67H | 28263 | V2(V31) 43rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDBH | 28635 | V2(V31) 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E68H | 28264 | V2(V31) 44th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDCH | 28636 | V2(V31) 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E69H | 28265 | V2(V31) 45th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDDH | 28637 | V2(V31) 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6AH | 28266 | V2(V31) 46th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDEH | 28638 | V2(V31) 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6BH | 28267 | V2(V31) 47th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FDFH | 28639 | V2(V31) 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6CH | 28268 | V2(V31) 48th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE0H | 28640 | V2(V31) 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6DH | 28269 | V2(V31) 49th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE1H | 28641 | V2(V31) 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6EH | 28270 | V2(V31) 50th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE2H | 28642 | V2(V31) 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E6FH | 28271 | V2(V31) 51st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE3H | 28643 | V2(V31) 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E70H | 28272 | V2(V31) 52nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE4H | 28644 | V2(V31) 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E71H | 28273 | V2(V31) 53rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE5H | 28645 | V2(V31) 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E72H | 28274 | V2(V31) 54th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE6H | 28646 | V2(V31) 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E73H | 28275 | V2(V31) 55th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE7H | 28647 | V2(V31) 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E74H | 28276 | V2(V31) 56th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE8H | 28648 | V2(V31) 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E75H | 28277 | V2(V31) 57th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FE9H | 28649 | V2(V31) 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E76H | 28278 | V2(V31) 58th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FEAH | 28650 | V2(V31) 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E77H | 28279 | V2(V31) 59th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FEBH | 28651 | V2(V31) 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E78H | 28280 | V2(V31) 60th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FECH | 28652 | V2(V31) 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E79H | 28281 | V2(V31) 61st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FEDH | 28653 | V2(V31) 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E7AH | 28282 | V2(V31) 62nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FEEH | 28654 | V2(V31) 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E7BH | 28283 | V2(V31) 63rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FEFH | 28655 | V2(V31) 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
Voltage Harmonic Amplitude: 03H Read | [7 empty] | Voltage Harmonic Phase Angle: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Vc/Vbc Harmonic Amplitude | [7 empty] | Vc/Vbc Harmonic Phase Angle
6E7CH | 28284 | V3(V23) 2nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF0H | 28656 | V3(V23) 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E7DH | 28285 | V3(V23) 3rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF1H | 28657 | V3(V23) 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E7EH | 28286 | V3(V23) 4th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF2H | 28658 | V3(V23) 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E7FH | 28287 | V3(V23) 5th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF3H | 28659 | V3(V23) 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E80H | 28288 | V3(V23) 6th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF4H | 28660 | V3(V23) 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E81H | 28289 | V3(V23) 7th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF5H | 28661 | V3(V23) 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E82H | 28290 | V3(V23) 8th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF6H | 28662 | V3(V23) 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E83H | 28291 | V3(V23) 9th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF7H | 28663 | V3(V23) 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E84H | 28292 | V3(V23) 10th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF8H | 28664 | V3(V23) 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E85H | 28293 | V3(V23) 11th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FF9H | 28665 | V3(V23) 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E86H | 28294 | V3(V23) 12th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFAH | 28666 | V3(V23) 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E87H | 28295 | V3(V23) 13th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFBH | 28667 | V3(V23) 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E88H | 28296 | V3(V23) 14th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFCH | 28668 | V3(V23) 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E89H | 28297 | V3(V23) 15th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFDH | 28669 | V3(V23) 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8AH | 28298 | V3(V23) 16th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFEH | 28670 | V3(V23) 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8BH | 28299 | V3(V23) 17th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 6FFFH | 28671 | V3(V23) 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8CH | 28300 | V3(V23) 18th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7000H | 28672 | V3(V23) 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8DH | 28301 | V3(V23) 19th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7001H | 28673 | V3(V23) 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8EH | 28302 | V3(V23) 20th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7002H | 28674 | V3(V23) 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E8FH | 28303 | V3(V23) 21st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7003H | 28675 | V3(V23) 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E90H | 28304 | V3(V23) 22nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7004H | 28676 | V3(V23) 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E91H | 28305 | V3(V23) 23rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7005H | 28677 | V3(V23) 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E92H | 28306 | V3(V23) 24th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7006H | 28678 | V3(V23) 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E93H | 28307 | V3(V23) 25th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7007H | 28679 | V3(V23) 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E94H | 28308 | V3(V23) 26th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7008H | 28680 | V3(V23) 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E95H | 28309 | V3(V23) 27th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7009H | 28681 | V3(V23) 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E96H | 28310 | V3(V23) 28th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700AH | 28682 | V3(V23) 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E97H | 28311 | V3(V23) 29th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700BH | 28683 | V3(V23) 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E98H | 28312 | V3(V23) 30th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700CH | 28684 | V3(V23) 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E99H | 28313 | V3(V23) 31st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700DH | 28685 | V3(V23) 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9AH | 28314 | V3(V23) 32nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700EH | 28686 | V3(V23) 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9BH | 28315 | V3(V23) 33rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 700FH | 28687 | V3(V23) 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9CH | 28316 | V3(V23) 34th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7010H | 28688 | V3(V23) 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9DH | 28317 | V3(V23) 35th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7011H | 28689 | V3(V23) 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9EH | 28318 | V3(V23) 36th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7012H | 28690 | V3(V23) 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6E9FH | 28319 | V3(V23) 37th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7013H | 28691 | V3(V23) 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA0H | 28320 | V3(V23) 38th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7014H | 28692 | V3(V23) 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA1H | 28321 | V3(V23) 39th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7015H | 28693 | V3(V23) 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA2H | 28322 | V3(V23) 40th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7016H | 28694 | V3(V23) 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA3H | 28323 | V3(V23) 41st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7017H | 28695 | V3(V23) 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA4H | 28324 | V3(V23) 42nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7018H | 28696 | V3(V23) 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA5H | 28325 | V3(V23) 43rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7019H | 28697 | V3(V23) 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA6H | 28326 | V3(V23) 44th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701AH | 28698 | V3(V23) 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA7H | 28327 | V3(V23) 45th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701BH | 28699 | V3(V23) 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA8H | 28328 | V3(V23) 46th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701CH | 28700 | V3(V23) 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EA9H | 28329 | V3(V23) 47th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701DH | 28701 | V3(V23) 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EAAH | 28330 | V3(V23) 48th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701EH | 28702 | V3(V23) 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EABH | 28331 | V3(V23) 49th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 701FH | 28703 | V3(V23) 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EACH | 28332 | V3(V23) 50th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7020H | 28704 | V3(V23) 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EADH | 28333 | V3(V23) 51st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7021H | 28705 | V3(V23) 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EAEH | 28334 | V3(V23) 52nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7022H | 28706 | V3(V23) 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EAFH | 28335 | V3(V23) 53rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7023H | 28707 | V3(V23) 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB0H | 28336 | V3(V23) 54th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7024H | 28708 | V3(V23) 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB1H | 28337 | V3(V23) 55th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7025H | 28709 | V3(V23) 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB2H | 28338 | V3(V23) 56th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7026H | 28710 | V3(V23) 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB3H | 28339 | V3(V23) 57th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7027H | 28711 | V3(V23) 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB4H | 28340 | V3(V23) 58th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7028H | 28712 | V3(V23) 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB5H | 28341 | V3(V23) 59th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 7029H | 28713 | V3(V23) 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB6H | 28342 | V3(V23) 60th Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 702AH | 28714 | V3(V23) 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB7H | 28343 | V3(V23) 61st Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 702BH | 28715 | V3(V23) 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB8H | 28344 | V3(V23) 62nd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 702CH | 28716 | V3(V23) 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EB9H | 28345 | V3(V23) 63rd Harmonic Amplitude | V=Rx/10 | V | ≥0 | Word | R | 702DH | 28717 | V3(V23) 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R

## Current Amplitude & Phase
Current Harmonic Amplitude: 03H Read | [7 empty] | Current Harmonic Phase Angle: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ia Harmonic Amplitude | [7 empty] | Ia Harmonic Phase Angle
6EBAH | 28346 | I1 2nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 702EH | 28718 | I1 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EBBH | 28347 | I1 3rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 702FH | 28719 | I1 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EBCH | 28348 | I1 4th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7030H | 28720 | I1 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EBDH | 28349 | I1 5th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7031H | 28721 | I1 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EBEH | 28350 | I1 6th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7032H | 28722 | I1 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EBFH | 28351 | I1 7th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7033H | 28723 | I1 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC0H | 28352 | I1 8th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7034H | 28724 | I1 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC1H | 28353 | I1 9th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7035H | 28725 | I1 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC2H | 28354 | I1 10th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7036H | 28726 | I1 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC3H | 28355 | I1 11th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7037H | 28727 | I1 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC4H | 28356 | I1 12th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7038H | 28728 | I1 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC5H | 28357 | I1 13th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7039H | 28729 | I1 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC6H | 28358 | I1 14th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703AH | 28730 | I1 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC7H | 28359 | I1 15th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703BH | 28731 | I1 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC8H | 28360 | I1 16th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703CH | 28732 | I1 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EC9H | 28361 | I1 17th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703DH | 28733 | I1 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECAH | 28362 | I1 18th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703EH | 28734 | I1 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECBH | 28363 | I1 19th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 703FH | 28735 | I1 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECCH | 28364 | I1 20th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7040H | 28736 | I1 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECDH | 28365 | I1 21st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7041H | 28737 | I1 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECEH | 28366 | I1 22nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7042H | 28738 | I1 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ECFH | 28367 | I1 23rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7043H | 28739 | I1 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED0H | 28368 | I1 24th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7044H | 28740 | I1 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED1H | 28369 | I1 25th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7045H | 28741 | I1 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED2H | 28370 | I1 26th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7046H | 28742 | I1 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED3H | 28371 | I1 27th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7047H | 28743 | I1 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED4H | 28372 | I1 28th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7048H | 28744 | I1 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED5H | 28373 | I1 29th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7049H | 28745 | I1 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED6H | 28374 | I1 30th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704AH | 28746 | I1 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED7H | 28375 | I1 31st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704BH | 28747 | I1 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED8H | 28376 | I1 32nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704CH | 28748 | I1 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6ED9H | 28377 | I1 33rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704DH | 28749 | I1 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDAH | 28378 | I1 34th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704EH | 28750 | I1 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDBH | 28379 | I1 35th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 704FH | 28751 | I1 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDCH | 28380 | I1 36th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7050H | 28752 | I1 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDDH | 28381 | I1 37th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7051H | 28753 | I1 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDEH | 28382 | I1 38th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7052H | 28754 | I1 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EDFH | 28383 | I1 39th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7053H | 28755 | I1 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE0H | 28384 | I1 40th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7054H | 28756 | I1 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE1H | 28385 | I1 41st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7055H | 28757 | I1 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE2H | 28386 | I1 42nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7056H | 28758 | I1 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE3H | 28387 | I1 43rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7057H | 28759 | I1 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE4H | 28388 | I1 44th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7058H | 28760 | I1 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE5H | 28389 | I1 45th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7059H | 28761 | I1 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE6H | 28390 | I1 46th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705AH | 28762 | I1 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE7H | 28391 | I1 47th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705BH | 28763 | I1 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE8H | 28392 | I1 48th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705CH | 28764 | I1 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EE9H | 28393 | I1 49th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705DH | 28765 | I1 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EEAH | 28394 | I1 50th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705EH | 28766 | I1 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EEBH | 28395 | I1 51st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 705FH | 28767 | I1 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EECH | 28396 | I1 52nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7060H | 28768 | I1 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EEDH | 28397 | I1 53rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7061H | 28769 | I1 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EEEH | 28398 | I1 54th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7062H | 28770 | I1 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EEFH | 28399 | I1 55th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7063H | 28771 | I1 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF0H | 28400 | I1 56th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7064H | 28772 | I1 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF1H | 28401 | I1 57th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7065H | 28773 | I1 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF2H | 28402 | I1 58th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7066H | 28774 | I1 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF3H | 28403 | I1 59th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7067H | 28775 | I1 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF4H | 28404 | I1 60th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7068H | 28776 | I1 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF5H | 28405 | I1 61st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7069H | 28777 | I1 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF6H | 28406 | I1 62nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706AH | 28778 | I1 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF7H | 28407 | I1 63rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706BH | 28779 | I1 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
Current Harmonic Amplitude: 03H Read | [7 empty] | Voltage Harmonic Amplitude & Phase: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ib Harmonic Amplitude | [7 empty] | Ib Harmonic Phase Angle
6EF8H | 28408 | I2 2nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706CH | 28780 | I2 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EF9H | 28409 | I2 3rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706DH | 28781 | I2 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFAH | 28410 | I2 4th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706EH | 28782 | I2 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFBH | 28411 | I2 5th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 706FH | 28783 | I2 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFCH | 28412 | I2 6th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7070H | 28784 | I2 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFDH | 28413 | I2 7th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7071H | 28785 | I2 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFEH | 28414 | I2 8th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7072H | 28786 | I2 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6EFFH | 28415 | I2 9th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7073H | 28787 | I2 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F00H | 28416 | I2 10th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7074H | 28788 | I2 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F01H | 28417 | I2 11th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7075H | 28789 | I2 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F02H | 28418 | I2 12th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7076H | 28790 | I2 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F03H | 28419 | I2 13th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7077H | 28791 | I2 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F04H | 28420 | I2 14th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7078H | 28792 | I2 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F05H | 28421 | I2 15th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7079H | 28793 | I2 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F06H | 28422 | I2 16th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707AH | 28794 | I2 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F07H | 28423 | I2 17th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707BH | 28795 | I2 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F08H | 28424 | I2 18th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707CH | 28796 | I2 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F09H | 28425 | I2 19th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707DH | 28797 | I2 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0AH | 28426 | I2 20th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707EH | 28798 | I2 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0BH | 28427 | I2 21st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 707FH | 28799 | I2 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0CH | 28428 | I2 22nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7080H | 28800 | I2 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0DH | 28429 | I2 23rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7081H | 28801 | I2 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0EH | 28430 | I2 24th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7082H | 28802 | I2 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F0FH | 28431 | I2 25th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7083H | 28803 | I2 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F10H | 28432 | I2 26th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7084H | 28804 | I2 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F11H | 28433 | I2 27th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7085H | 28805 | I2 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F12H | 28434 | I2 28th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7086H | 28806 | I2 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F13H | 28435 | I2 29th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7087H | 28807 | I2 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F14H | 28436 | I2 30th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7088H | 28808 | I2 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F15H | 28437 | I2 31st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7089H | 28809 | I2 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F16H | 28438 | I2 32nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708AH | 28810 | I2 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F17H | 28439 | I2 33rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708BH | 28811 | I2 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F18H | 28440 | I2 34th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708CH | 28812 | I2 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F19H | 28441 | I2 35th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708DH | 28813 | I2 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1AH | 28442 | I2 36th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708EH | 28814 | I2 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1BH | 28443 | I2 37th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 708FH | 28815 | I2 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1CH | 28444 | I2 38th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7090H | 28816 | I2 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1DH | 28445 | I2 39th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7091H | 28817 | I2 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1EH | 28446 | I2 40th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7092H | 28818 | I2 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F1FH | 28447 | I2 41st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7093H | 28819 | I2 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F20H | 28448 | I2 42nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7094H | 28820 | I2 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F21H | 28449 | I2 43rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7095H | 28821 | I2 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F22H | 28450 | I2 44th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7096H | 28822 | I2 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F23H | 28451 | I2 45th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7097H | 28823 | I2 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F24H | 28452 | I2 46th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7098H | 28824 | I2 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F25H | 28453 | I2 47th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 7099H | 28825 | I2 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F26H | 28454 | I2 48th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709AH | 28826 | I2 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F27H | 28455 | I2 49th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709BH | 28827 | I2 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F28H | 28456 | I2 50th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709CH | 28828 | I2 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F29H | 28457 | I2 51st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709DH | 28829 | I2 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2AH | 28458 | I2 52nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709EH | 28830 | I2 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2BH | 28459 | I2 53rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 709FH | 28831 | I2 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2CH | 28460 | I2 54th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A0H | 28832 | I2 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2DH | 28461 | I2 55th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A1H | 28833 | I2 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2EH | 28462 | I2 56th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A2H | 28834 | I2 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F2FH | 28463 | I2 57th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A3H | 28835 | I2 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F30H | 28464 | I2 58th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A4H | 28836 | I2 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F31H | 28465 | I2 59th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A5H | 28837 | I2 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F32H | 28466 | I2 60th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A6H | 28838 | I2 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F33H | 28467 | I2 61st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A7H | 28839 | I2 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F34H | 28468 | I2 62nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A8H | 28840 | I2 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F35H | 28469 | I2 63rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70A9H | 28841 | I2 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
Current Harmonic Amplitude: 03H Read | [7 empty] | Current Harmonic Phase Angle: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property | Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
Ic Harmonic Amplitude | [7 empty] | Ic Harmonic Phase Angle
6F36H | 28470 | I3 2nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70AAH | 28842 | I3 2nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F37H | 28471 | I3 3rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70ABH | 28843 | I3 3rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F38H | 28472 | I3 4th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70ACH | 28844 | I3 4th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F39H | 28473 | I3 5th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70ADH | 28845 | I3 5th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3AH | 28474 | I3 6th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70AEH | 28846 | I3 6th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3BH | 28475 | I3 7th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70AFH | 28847 | I3 7th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3CH | 28476 | I3 8th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B0H | 28848 | I3 8th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3DH | 28477 | I3 9th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B1H | 28849 | I3 9th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3EH | 28478 | I3 10th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B2H | 28850 | I3 10th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F3FH | 28479 | I3 11th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B3H | 28851 | I3 11th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F40H | 28480 | I3 12th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B4H | 28852 | I3 12th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F41H | 28481 | I3 13th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B5H | 28853 | I3 13th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F42H | 28482 | I3 14th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B6H | 28854 | I3 14th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F43H | 28483 | I3 15th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B7H | 28855 | I3 15th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F44H | 28484 | I3 16th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B8H | 28856 | I3 16th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F45H | 28485 | I3 17th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70B9H | 28857 | I3 17th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F46H | 28486 | I3 18th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BAH | 28858 | I3 18th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F47H | 28487 | I3 19th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BBH | 28859 | I3 19th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F48H | 28488 | I3 20th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BCH | 28860 | I3 20th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F49H | 28489 | I3 21st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BDH | 28861 | I3 21st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4AH | 28490 | I3 22nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BEH | 28862 | I3 22nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4BH | 28491 | I3 23rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70BFH | 28863 | I3 23rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4CH | 28492 | I3 24th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C0H | 28864 | I3 24th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4DH | 28493 | I3 25th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C1H | 28865 | I3 25th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4EH | 28494 | I3 26th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C2H | 28866 | I3 26th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F4FH | 28495 | I3 27th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C3H | 28867 | I3 27th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F50H | 28496 | I3 28th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C4H | 28868 | I3 28th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F51H | 28497 | I3 29th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C5H | 28869 | I3 29th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F52H | 28498 | I3 30th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C6H | 28870 | I3 30th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F53H | 28499 | I3 31st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C7H | 28871 | I3 31st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F54H | 28500 | I3 32nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C8H | 28872 | I3 32nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F55H | 28501 | I3 33rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70C9H | 28873 | I3 33rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F56H | 28502 | I3 34th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CAH | 28874 | I3 34th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F57H | 28503 | I3 35th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CBH | 28875 | I3 35th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F58H | 28504 | I3 36th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CCH | 28876 | I3 36th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F59H | 28505 | I3 37th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CDH | 28877 | I3 37th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5AH | 28506 | I3 38th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CEH | 28878 | I3 38th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5BH | 28507 | I3 39th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70CFH | 28879 | I3 39th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5CH | 28508 | I3 40th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D0H | 28880 | I3 40th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5DH | 28509 | I3 41st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D1H | 28881 | I3 41st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5EH | 28510 | I3 42nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D2H | 28882 | I3 42nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F5FH | 28511 | I3 43rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D3H | 28883 | I3 43rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F60H | 28512 | I3 44th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D4H | 28884 | I3 44th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F61H | 28513 | I3 45th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D5H | 28885 | I3 45th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F62H | 28514 | I3 46th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D6H | 28886 | I3 46th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F63H | 28515 | I3 47th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D7H | 28887 | I3 47th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F64H | 28516 | I3 48th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D8H | 28888 | I3 48th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F65H | 28517 | I3 49th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70D9H | 28889 | I3 49th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F66H | 28518 | I3 50th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DAH | 28890 | I3 50th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F67H | 28519 | I3 51st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DBH | 28891 | I3 51st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F68H | 28520 | I3 52nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DCH | 28892 | I3 52nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F69H | 28521 | I3 53rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DDH | 28893 | I3 53rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6AH | 28522 | I3 54th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DEH | 28894 | I3 54th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6BH | 28523 | I3 55th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70DFH | 28895 | I3 55th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6CH | 28524 | I3 56th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E0H | 28896 | I3 56th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6DH | 28525 | I3 57th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E1H | 28897 | I3 57th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6EH | 28526 | I3 58th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E2H | 28898 | I3 58th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F6FH | 28527 | I3 59th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E3H | 28899 | I3 59th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F70H | 28528 | I3 60th Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E4H | 28900 | I3 60th Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F71H | 28529 | I3 61st Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E5H | 28901 | I3 61st Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F72H | 28530 | I3 62nd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E6H | 28902 | I3 62nd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R
6F73H | 28531 | I3 63rd Harmonic Amplitude | I=Rx/10 | A | ≥0 | Word | R | 70E7H | 28903 | I3 63rd Harmonic Phase Angle | Phase Angle=Rx/10 | Degrees ° | ≥0 | Word | R

## Phase Angles
Phase Angles: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
42A0H | 17056 | Phase Angle of V2 to V1 | V2=Rx/10 | Degrees | 0-360.0 | Word | R
42A1H | 17057 | Phase Angle of V3 to V1 | V3=Rx/10 | Degrees | 0-360.0 | Word | R
42A2H | 17058 | Phase Angle of I1 to V1 | I1=Rx/10 | Degrees | 0-360.0 | Word | R
42A3H | 17059 | Phase Angle of I2 to V1 | I2=Rx/10 | Degrees | 0-360.0 | Word | R
42A4H | 17060 | Phase Angle of I3 to V1 | I3=Rx/10 | Degrees | 0-360.0 | Word | R

## Sequence
Sequence Components: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
4294H | 17044 | Positive Sequence Real part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
4295H | 17045 | Postive Sequence Complex part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
4296H | 17046 | Negative Sequence Real part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
4297H | 17047 | Negative Sequence Complex part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
4298H | 17048 | Zero Sequence Real part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
4299H | 17049 | Zero Sequence Complex part of V1 | THD=Rx/100 | % | -32768~32767 | Word | R
429AH | 17050 | Positive Sequence Real part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R
429BH | 17051 | Postive Sequence Complex part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R
429CH | 17052 | Negative Sequence Real part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R
429DH | 17053 | Negative Sequence Complex part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R
429EH | 17054 | Zero Sequence Real part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R
429FH | 17055 | Zero Sequence Complex part of I1 | THD=Rx/100 | % | -32768~32767 | Word | R

## MAX-MIN (INT)
MAX: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
4136H | 16694 | Va Max | Rx/10 | V | -32768~32767 | Word | R
4137H-413CH | 16695-16700 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R | NOTE: Values in terms of Secondary side
413DH | 16701 | Vb Max | Rx/10 | V | -32768~32767 | Word | R
413EH-4143H | 16702-16707 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4144H | 16708 | V3 Max | Rx/10 | V | -32768~32767 | Word | R
4145H-414AH | 16709-16714 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
414BH | 16715 | Vab Max | Rx/10 | V | -32768~32767 | Word | R
414CH-4151H | 16716-16721 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4152H | 16722 | Vbc Max | Rx/10 | V | -32768~32767 | Word | R
4153H-4158H | 16723-16728 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4159H | 16729 | Vca Max | Rx/10 | V | -32768~32767 | Word | R
415AH-415FH | 16730-16765 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4160H | 16736 | Ia Max | Rx/10 | A | -32768~32767 | Word | R
4161H-4166H | 16737-16742 | Time Stamp |  |  |  | Word | R
4167H | 16743 | Ib Max | Rx/10 | A | -32768~32767 | Word | R
4168H-416DH | 16744-16749 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
416EH | 16750 | Ic Max | Rx/10 | A | -32768~32767 | Word | R
416FH-4174H | 16751-16756 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4175H | 16757 | Total Power Max | Rx/10 | kW | -32768~32767 | Word | R
4176H-417BH | 16758-16763 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
417CH | 16764 | Total Reactive Power Max | Rx/10 | kvar | -32768~32767 | Word | R
417DH-4182H | 16765-16770 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4183H | 16771 | Total Apparent Power Max | Rx/10 | kVA | -32768~32767 | Word | R
4184H-4189H | 16772-16777 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
418AH | 16778 | Power Factor Max | Rx/1000 |  | -32768~32767 | Word | R
418BH-4190H | 16779-16784 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4191H | 16785 | Frequency Max | Rx/1000 | Hz | -32768~32767 | Word | R
4192H-4197H | 16786-16791 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4198H | 16792 | Power Demand Max | Rx/10 | kW | -32768~32767 | Word | R
4199H-419EH | 16793-16793 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
419FH | 16799 | Reactive Power Demand Max | Rx/10 | kvar | -32768~32767 | Word | R
41A0H-41A5H | 16800-16805 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41A6H | 16806 | Apparent Demand Max | Rx/10 | kVA | -32768~32767 | Word | R
41A7H-41ACH | 16807-16812 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4606H | 17926 | Phase A Current Demand Max | Rx/10 | A | -32768~32767 | Word | R
4607H-460CH | 17927-17932 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
460DH | 17933 | Phase B Current Demand Max | Rx/10 | A | -32768~32767 | Word | R
460EH-4613HH | 17934-17939 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
4614H | 17940 | Phase C Current Demand Max | Rx/10 | A | -32768~32767 | Word | R
4615H-461AH | 17941-17946 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41ADH | 16813 | Voltage Unbalance Max | Rx/10 | % | -32768~32767 | Word | R
41AEH-41B3H | 16814-16819 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41B4H | 16820 | Current Unbalance Max | Rx/10 | % | -32768~32767 | Word | R
41B5H-41BAH | 16821-16826 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41BBH | 16827 | THD_Va(Vab) Max | Rx/100 | % | -32768~32767 | Word | R
41BCH-41C1H | 16828-16833 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41C2H | 16834 | THD_Vb(Vca) Max | Rx/100 | % | -32768~32767 | Word | R
41C3H-41C8H | 16835-16840 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41C9H | 16841 | THD_Vc(Vbc) Max | Rx/100 | % | -32768~32767 | Word | R
41CAH-41CFH | 16842-16847 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41D0H | 16848 | THD_Ia Max | Rx/100 | % | -32768~32767 | Word | R
41D1H-41D6H | 16849-16854 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41D7H | 16855 | THD_Ib Max | Rx/100 | % | -32768~32767 | Word | R
41D8H-41DDH | 16856-16861 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
41DEH | 16862 | THD_Ic Max | Rx/100 | % | -32768~32767 | Word | R
41DFH-41E4H | 16863-16868 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | Word | R
MIN: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Property | Range | Data Type | Access Property
41E5H | 16869 | Va Min | Rx/10 | V | -32768~32767 | int | R
41E6H-41EBH | 16870-16875 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
41ECH | 16876 | Vb Min | Rx/10 | V | -32768~32767 | int | R
41EDH-41F2H | 16877-16882 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
41F3H | 16883 | Vc Min | Rx/10 | V | -32768~32767 | int | R
41F4H-41F9H | 16884-16889 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
41FAH | 16890 | Vab Min | Rx/10 | V | -32768~32767 | int | R
41FBH-4200H | 16891-16896 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4201H | 16897 | Vbc Min | Rx/10 | V | -32768~32767 | int | R
4202H-4207H | 16898-16903 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4208H | 16904 | Vca Min | Rx/10 | V | -32768~32767 | int | R
4209H-420EH | 16905-16910 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
420FH | 16911 | Ia Min | Rx/10 | A | -32768~32767 | int | R
4210H-4215H | 16912-16917 | Time Stamp |  |  |  | int | R
4216H | 16918 | Ib Min | Rx/10 | A | -32768~32767 | int | R
4217H-421CH | 16919-16924 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
421DH | 16925 | Ic Min | Rx/10 |  | -32768~32767 | int | R
421EH-4223H | 16926-16931 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4224H | 16932 | Total Power Min | Rx/10 | kW | -32768~32767 | int | R
4225H-422AH | 16933-16938 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
422BH | 16939 | Total Reactive Power Min | Rx/10 | kvar | -32768~32767 | int | R
422CH-4231H | 16940-16945 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4232H | 16946 | Total Apparent Power Min | Rx/10 | kVA | -32768~32767 | int | R
4233H-4238H | 16947-16952 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4239H | 16953 | Power Factor Min | Rx/1000 |  | -32768~32767 | int | R
423AH-423FH | 16954-16959 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4240H | 16960 | Fequency Min | Rx/1000 | Hz | -32768~32767 | int | R
4241H-4246H | 16961-16966 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4247H | 16967 | Power Demand Min | Rx/10 | kW | -32768~32767 | int | R
4248H-424DH | 16968-16973 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
424EH | 16974 | Reactive Power Demand Min | Rx/10 | kvar | -32768~32767 | int | R
424FH-4254H | 16975-16980 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4255H | 16981 | Apparent Power Demand Min | Rx/10 | kVA | -32768~32767 | int | R
4256H-425BH | 16982-16987 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
425CH | 16988 | Voltage Unbalance Min | Rx/10 | % | -32768~32767 | int | R
425DH-4262H | 16989-16994 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4263H | 16995 | Current Unbalance Min | Rx/10 | % | -32768~32767 | int | R
4264H-4269H | 16996-17001 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
426AH | 17002 | THD_Va(Vab) Min | Rx/100 | % | -32768~32767 | int | R
426BH-4270H | 17003-17008 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4271H | 17009 | THD_Vb(Vca) Min | Rx/100 | % | '-32768~32767 | int | R
4272H-4277H | 17010-17015 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4278H | 17016 | THD_Vc(Vbc) Min | Rx/100 | % | '-32768~32767 | int | R
4279H-427EH | 17017-17022 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
427FH | 17023 | THD_Ia Min | Rx/100 | % | '-32768~32767 | int | R
4280H-4285H | 17024-17029 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
4286H | 17030 | THD_Ib Min | Rx/100 | % | '-32768~32767 | int | R
4287H-428CH | 17031-17036 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R
428DH | 17037 | THD_Ic Min | Rx/100 | % | '-32768~32767 | int | R
428EH-4293H | 17038-17043 | Time Stamp | YYYY:MM:DD:hh:mm:ss |  |  | int | R

## MAX-MIN (FLOAT)
MAX: 03H Read
Address (Hex) | Address (Dec) | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  | Primary | Secondary
5000H-5001H | 20480-20481 | Va Max | Va=Rx | Va=Rx*(PT1/PT2) | V | Float | R
5002H-5007H | 20482-20487 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5008H-5009H | 20488-20489 | Vb Max | Vb=Rx | Vb=Rx*(PT1/PT2) | V | Float | R
500AH-500FH | 20490-20495 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5010H-5011H | 20496-20497 | Vc Max | Vc=Rx | Vc=Rx*(PT1/PT2) | V | Float | R
5012H-5017H | 20498-20503 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5018H-5019H | 20504-20505 | Vab Max | Vab=Rx | Vab=Rx*(PT1/PT2) | V | Float | R
501AH-501FH | 20506-20511 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5020H-5021H | 20512-20513 | Vbc Max | Vbc=Rx | Vbc=Rx*(PT1/PT2) | V | Float | R
5022H-5027H | 20514-20519 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5028H-5029H | 20520-20521 | Vca Max | Vca=Rx | Vca=Rx*(PT1/PT2) | V | Float | R
502AH-502FH | 20522-20527 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5030H-5031H | 20528-20529 | Ia Max | Ia=Rx | Ia=Rx*(CT1/CT2) | A | Float | R
5032H-5037H | 20530-20535 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5038H-5039H | 20536-20537 | Ib Max | Ib=Rx | Ib=Rx*(CT1/CT2) | A | Float | R
503AH-503FH | 20538-20543 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5040H-5041H | 20544-20545 | Ic Max | Ic=Rx | Ic=Rx*(CT1/CT2) | A | Float | R
5042H-5047H | 20546-20551 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5048H-5049H | 20552-20553 | Total Power Max | P=Rx/1000 | P=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kW | Float | R
504AH-504FH | 20554-20559 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5050H-5051H | 20560-20561 | Total Reactive Power Max | Q=Rx/1000 | Q=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kvar | Float | R
5052H-5057H | 20562-20567 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5058H-5059H | 20568-20569 | Total Apparent Power Max | S=Rx/1000 | S=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kVA | Float | R
505AH-505FH | 20570-20575 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5060H-5061H | 20576-20577 | Power Factor Max | PF=Rx | PF=Rx |  | Float | R
5062H-5067H | 20578-20583 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5068H-5069H | 20584-20585 | Frequency Max | F=Rx | F=Rx | Hz | Float | R
506AH-506FH | 20586-20591 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5070H-5071H | 20592-20593 | Power Demand Max | P=Rx/1000 | P=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kW | Float | R
5072H-5073H | 20594-20595 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5078H-5079H | 20600-20601 | Reactive Power Demand Max | Q=Rx/1000 | Q=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kvar | Float | R
507AH-507FH | 20602-20607 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5080H-5081H | 20608-20609 | Apparent Demand Max | S=Rx/1000 | S=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kVA | Float | R
5082H-5087H | 20610-20615 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5088H-5089H | 20616-20617 | Voltage Unbalance Max | Vunb=Rx*100% | Vunb=Rx*100% | % | Float | R
508AH-508FH | 20618-20623 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5090H-5091H | 20624-20625 | Current Unbalance Max | Iunb=Rx*100% | Iunb=Rx*100% | % | Float | R
5092H-5097H | 20626-20631 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5098H-5099H | 20632-20633 | THD_Va(Vab) Max | THD_Va(Vab) = Rx*100% | THD_Va(Vab) = Rx*100% | % | Float | R
509AH-509FH | 20634-20639 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50A0H-50A1H | 20640-20641 | THD_Vb(Vca) Max | THD_Vb(Vca)=Rx*100% | THD_Vb(Vca)=Rx*100% | % | Float | R
50A2H-50A7H | 20642-20647 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50A8H-50A9H | 20648-20649 | THD_Vc(Vbc) Max | THD_Vc(Vbc)=Rx*100% | THD_Vc(bc)=Rx*100% | % | Float | R
50AAH-50AFH | 20650-20655 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50B0H-50B1H | 20656-20657 | THD_Ia Max | THD_Ia=Rx*100% | THD_Ia=Rx*100% | % | Float | R
50B2H-50B7H | 20658-20663 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50B8H-50B9H | 20664-20665 | THD_Ib Max | THD_Ib=Rx*100% | THD_Ib=Rx*100% | % | Float | R
50BAH-50BFH | 20666-20671 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50C0H-50C1H | 20672-20673 | THD_Ic Max | THD_Ic=Rx*100% | THD_Ic=Rx*100% | % | Float | R
50C2H-50C7H | 20674-20679 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50C8H-50C9H | 20680-20681 | Ia Current Demand Max | Ia=Rx | Ia=Rx*(CT1/CT2) | A | Float | R
50CAH-50CFH | 20682-20687 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50D0H-50D1H | 20688-20689 | Ib Current Demand Max | Ib=Rx | Ib=Rx*(CT1/CT2) | A | Float | R
50D2H-50D7H | 20690-20695 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50D8H-50D9H | 20696-20697 | Ic Current Demand Max | Ic=Rx | Ic=Rx*(CT1/CT2) | A | Float | R
50DAH-50DFH | 20698-20703 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
MIN: 03H Read
Address (Hex) | Address (Dec) | Parameter | Parameter Mode |  | Property | Data Type | Access Property
|  |  | Primary | Secondary
50E0H-50E1H | 20704-20705 | Va Min | Va=Rx | Va=Rx*(PT1/PT2) | V | Float | R
50E2H-50E7H | 20706-20711 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50E8H-50E9H | 20712-20713 | Vb Min | Vb=Rx | Vb=Rx*(PT1/PT2) | V | Float | R
50EAH-50EFH | 20714-20719 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50F0H-50F1H | 20720-20721 | Vc Min | Vc=Rx | Vc=Rx*(PT1/PT2) | V | Float | R
50F2H-50F7H | 20722-20727 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
50F8H-50F9H | 20728-20729 | Vab Min | Vab=Rx | Vab=Rx*(PT1/PT2) | V | Float | R
50FAH-50FFH | 20730-20735 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5100H-5101H | 20736-20737 | Vbc Min | Vbc=Rx | Vbc=Rx*(PT1/PT2) | V | Float | R
5102H-5107H | 20738-20743 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5108H-5109H | 20744-20745 | Vca Min | Vca=Rx | Vca=Rx*(PT1/PT2) | V | Float | R
510AH-510FH | 20746-20751 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5110H-5111H | 20752-20753 | Ia Min | Ia=Rx | Ia=Rx*(CT1/CT2) | A | Float | R
5112H-5117H | 20754-20759 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5118H-5119H | 20760-20761 | Ib Min | Ib=Rx | Ib=Rx*(CT1/CT2) | A | Float | R
511AH-511FH | 20762-20767 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5120H-5121H | 20768-20769 | Ic Min | Ic=Rx | Ic=Rx*(CT1/CT2) | A | Float | R
5122H-5127H | 20770-20775 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5128H-5129H | 20776-20777 | Total Power Min | P=Rx/1000 | P=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kW | Float | R
512AH-512FH | 20778-20783 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5130H-5131H | 20784-20785 | Total Reactive Power Min | Q=Rx/1000 | Q=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kvar | Float | R
5132H-5137H | 20786-20791 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5138H-5139H | 20792-20793 | Total Apparent Power Min | S=Rx/1000 | S=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kVA | Float | R
513AH-513FH | 20794-20799 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5140H-5141H | 20800-20801 | Power Factor Min | PF=Rx | PF=Rx |  | Float | R
5142H-5147H | 20802-20807 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5148H-5149H | 20808-20809 | Frequency Min | F=Rx | F=Rx | Hz | Float | R
514AH-514FH | 20810-20815 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5150H-5151H | 20816-20817 | Power Demand Min | P=Rx/1000 | P=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kW | Float | R
5152H-5157H | 20818-20823 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5158H-5159H | 20824-20825 | Reactive Power Demand Min | Q=Rx/1000 | Q=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kvar | Float | R
515AH-515FH | 20826-20831 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5160H-5161H | 20832-20833 | Apparent Demand Min | S=Rx/1000 | S=[Rx*(CT1/CT2)*(PT1/PT2)]/1000 | kVA | Float | R
5162H-5167H | 20834-20839 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5168H-5169H | 20840-20841 | Voltage Unbalance Min | Vunb=Rx*100% | Vunb=Rx*100% | % | Float | R
516AH-516FH | 20842-20847 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5170H-5171H | 20848-20849 | Current Unbalance Min | Iunb=Rx*100% | Iunb=Rx*100% | % | Float | R
5172H-5177H | 20850-20855 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5178H-5179H | 20856-20857 | THD_Va(Vab) Min | THD_Va(Vab) = Rx*100% | THD_Va(Vab) = Rx*100% | % | Float | R
517AH-517FH | 20858-20863 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5180H-5181H | 20864-20865 | THD_Vb(Vca) Min | THD_Vb(Vca)=Rx*100% | THD_Vb(Vca)=Rx*100% | % | Float | R
5182H-5187H | 20866-20871 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5188H-5189H | 20872-20873 | THD_Vc(Vbc) Min | THD_Vc(Vbc)=Rx*100% | THD_Vc(bc)=Rx*100% | % | Float | R
518AH-518FH | 20874-20879 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5190H-5191H | 20880-20881 | THD_Ia Min | THD_Ia=Rx*100% | THD_Ia=Rx*100% | % | Float | R
5192H-5197H | 20882-20887 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
5198H-5199H | 20888-20889 | THD_Ib Min | THD_Ib=Rx*100% | THD_Ib=Rx*100% | % | Float | R
519AH-519FH | 20890-20895 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
51A0H-51A1H | 20896-20897 | THD_Ic Min | THD_Ic=Rx*100% | THD_Ic=Rx*100% | % | Float | R
51A2H-51A7H | 20898-20903 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
51A8H-51A9H | 20904-20905 | Ia Current Demand Min | Ia=Rx | Ia=Rx*(CT1/CT2) | A | Float | R
51AAH-51AFH | 20906-20911 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
51B0H-51B1H | 20912-20913 | Ib Current Demand Min | Ib=Rx | Ib=Rx*(CT1/CT2) | A | Float | R
51B2H-51B7H | 20914-20919 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R
51B8H-51B9H | 20920-20921 | Ic Current Demand Min | Ic=Rx | Ic=Rx*(CT1/CT2) | A | Float | R
51BAH-51BFH | 20922-20927 | Time Stamp | Time Stamp = Rx | Time Stamp = Rx | YYYY:MM:DD:hh:mm:ss | Word | R

## Clock
Clock Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
103FH | 4159 | Week | 0-6 | Word | R/W
1040H | 4160 | Year | 2000-2099 | Word | R/W
1041H | 4161 | Month | 1-12 | Word | R/W
1042H | 4162 | Day | 1-31 | Word | R/W
1043H | 4163 | Hour | 0-23 | Word | R/W
1044H | 4164 | Minute | 0-59 | Word | R/W
1045H | 4165 | Second | 0-59 | Word | R/W

## IO Module Settings
03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
AXM-IO1-1
109EH | 4254 | DI1-DI6 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: DI4 Bit4: DI5 Bit5: DI6; 0: Status 1: Pulse Counter | 0 | R/W | Word
109FH | 4255 | DI Pulse Constant | 1~65535 | 0 | R/W | Word
10A0H | 4256 | RO Type Mode | 0: Control 1: Alarm | 0 | R/W | Word
10A1H | 4257 | RO Control Mode | 0: Latch 1: Momentary | 0 | R/W | Word
10A2H | 4258 | Pulse Width | 50-300ms | 50 | R/W | Word
AXM-IO2-1
10A3H | 4259 | DI1-DI4 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: D4 0: Status 1: Pulse Counter | 0 | R/W | Word
10A4H | 4260 | DI Pulse Constant | 1-65535 | 0 | R/W | Word
10A5H | 4261 | DO Mode | 0: Pulse Output 1: Alarm output | 0 | R/W | Word
10A6H | 4262 | DO Pulse width | 20-100ms | 20 | R/W | Word
10A7H | 4063 | DO1 Output | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP | 0 | R/W | Word
10A8H | 4064 | DO2 Output | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP | 0 | R/W | Word
10A9H | 4265 | AO Type | 0: 0-20mA 1: 4-20mA 2: 0-5V 3: 1-5V | 1 or 2 | R/W | Word
AXM-IO3-1
10AAH | 4266 | DI11~DI14 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: D4 0: Status 1: Pulse Counter | 0 | R/W | Word
10ABH | 4267 | DI Pulse Constant | 1-65535 | 0 | R/W | Word
10ACH | 4268 | RO Type Mode | 0: Control 1: Alarm | 0 | R/W | Word
10ADH | 4269 | RO Control Mode | 0: Latch 1: Momentary | 0 | R/W | Word
10AEH | 4270 | Pulse Width | 50-300ms | 50 | R/W | Word
10AFH | 4271 | AI Type | 0: 0-20mA 1: 4-20mA 2: 0-5V 3: 1-5V | 1 or 2 | R/W | Word
AXM-IO1-2
10B0H | 4272 | DI15~20 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: DI4 Bit4: DI5 Bit5: DI6; 0: Status 1: Pulse Counter | 0 | R/W | Word
10B1H | 4273 | DI Pulse Constant | 1~65535 | 0 | R/W | Word
10B2H | 4274 | RO Type Mode | 0: Control 1: Alarm | 0 | R/W | Word
10B3H | 4275 | RO Control Mode | 0: Latch 1: Momentary | 0 | R/W | Word
10B4H | 4276 | Pulse Width | 50-300ms | 50 | R/W | Word
AXM-IO2-2
10B5H | 4277 | DI21~DI24 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: D4 0: Status 1: Pulse Counter | 0 | R/W | Word
10B6H | 4278 | DI Pulse Constant | 1-65535 | 0 | R/W | Word
10B7H | 4279 | DO Mode | 0: Pulse Output 1: Alarm output | 0 | R/W | Word
10B8H | 4280 | DO Pulse width | 20-100ms | 20 | R/W | Word
10B9H | 4281 | DO1 Output | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP | 0 | R/W | Word
10BAH | 4282 | DO2 Output | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP | 0 | R/W | Word
10BBH | 4283 | AO Type | 0: 0-20mA 1: 4-20mA 2: 0-5V 3: 1-5V | 1 or 2 | R/W | Word
AXM-IO3-2
10BCH | 4284 | DI25~DI28 Type | Bit0: DI1 Bit1: DI2 Bit2: DI3 Bit3: D4 0: Status 1: Pulse Counter | 0 | R/W | Word
10BDH | 4285 | DI Pulse Constant | 1-65535 | 0 | R/W | Word
10BEH | 4286 | RO Type Mode | 0: Control 1: Alarm | 0 | R/W | Word
10BFH | 4287 | RO Control Mode | 0: Latch 1: Momentary | 0 | R/W | Word
10C0H | 4288 | Pulse Width | 50-300ms | 50 | R/W | Word
10C1H | 4289 | AI Type | 0: 0-20mA 1: 4-20mA 2: 0-5V 3: 1-5V | 1 or 2 | R/W | Word

## Analog Output Parameter Setting
03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
AO Parameter Selection
AXM-IO2-1
10C2H | 4290 | AO1 Parameter Selection | Refer to following table | 0 | R/W | Word | AO Parameter Selection
10C3H | 4291 | AO2 Parameter Selection | Refer to following table | 0 | R/W | Word | Setting Value | Parameter | Symbol
AXM-IO2-2 | [6 empty] | 0 | Frequency | F
10C4H | 4292 | AO3 Parameter Selection | Refer to following table | 0 | R/W | Word | 1 | Phase A Line-Neutral Voltage | Ua
10C5H | 4293 | AO4 Parameter Selection | Refer to following table | 0 | R/W | Word | 2 | Phase B Line-Neutral Voltage | Ub
[7 empty] | 3 | Phase C Line-Neutral Voltage | Uc
[7 empty] | 4 | Average Line Neutral Voltage | Uavg
AO Slope and Input/Output Range | [6 empty] | 5 | Line-Line Voltage AB | Uab
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property | 6 | Line-Line Voltage BC | Ubc
AXM-IO2-1 | [6 empty] | 7 | Line-Line Voltage CA | Uca
10D0H | 4304 | AO1 Slope Selection | 1: 1 Slope 2: 2 Slope 3: 3 Slope | 1 | R/W | Word | 8 | Average Line-Line Voltage | Ulavg
10D1H | 4305 | AO1 Starting Point Value |  |  | R/W | Word | 9 | Phase A Current | Ia
10D2H | 4306 | AO1 Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Word | 10 | Phase B Current | Ib
10D3H | 4307 | AO1 Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Word | 11 | Phase C Current | Ic
10D4H | 4308 | AO1 End Point Value |  |  | R/W | Word | 12 | Average Current | Iavg
10D5H | 4309 | AO1 Output Starting Point Value | AO Type 4-20mA 0-20mA 0-5V 1-5V |  | R/W | Word | 13 | Neutral Current | In
10D6H | 4310 | AO1 Output Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Word | 14 | Phase A Power | Pa
10D7H | 4311 | AO1 Output Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Word | 15 | Phase B Power | Pb
10D8H | 4312 | AO1 Output End Point Value |  |  | R/W | Word | 16 | Phase C Power | Pc
10D9H | 4313 | AO2 Slope Selection | 1: 1 Slope 2: 2 Slope 3: 3 Slope | 1 | R/W | Word | 17 | Total System Power | Psum
10DAH | 4314 | AO2 Starting Point Value |  |  | R/W | Word | 18 | Phase A Reactive Power | Qa
10DBH | 4315 | AO2 Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Word | 19 | Phase B Reactive Power | Qb
10DCH | 4316 | AO2 Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Word | 20 | Phase C Reactive Power | Qc
10DDH | 4317 | AO2 End Point Value |  |  | R/W | Word | 21 | Total System Reactive Power | Qsum
10DEH | 4318 | AO2 Output Starting Point Value | AO Type 4-20mA 0-20mA 0-5V 1-5V |  | R/W | Word | 22 | Phase A Apparent Power | Sa
10DFH | 4319 | AO2 Output Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Word | 23 | Phase B Apparent Power | Sb
10E0H | 4320 | AO2 Output Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Word | 24 | Phase C Apparent Power | Sc
10E1H | 4321 | AO2 Output End Point Value |  |  | R/W | Word | 25 | Total System Apparent Power | Ssum
AXM-IO2-2 | [6 empty] | 26 | Phase A Power Factor | PFa
10E2H | 4322 | AO1 Slope Selection | 1: 1 Slope 2: 2 Slope 3: 3 Slope | 1 | R/W | Int | 27 | Phase B Power Factor | PFb
10E3H | 4323 | AO1 Starting Point Value |  |  | R/W | Int | 28 | Phase C Power Factor | PFc
10E4H | 4324 | AO1 Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Int | 29 | Total Power Factor | PF
10E5H | 4325 | AO1 Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Int
10E6H | 4326 | AO1 End Point Value |  |  | R/W | Int
10E7H | 4327 | AO1 Output Starting Point Value | AO Type 4-20mA 0-20mA 0-5V 1-5V |  | R/W | Int
10E8H | 4328 | AO1 Output Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Int
10E9H | 4329 | AO1 Output Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Int
10EAH | 4330 | AO1 Output End Point Value |  |  | R/W | Int
10EBH | 4331 | AO2 Slope Selection | 1: 1 Slope 2: 2 Slope 3: 3 Slope | 1 | R/W | Int
10ECH | 4332 | AO2 Starting Point Value |  |  | R/W | Int
10EDH | 4333 | AO2 Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Int
10EEH | 4334 | AO2 Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Int
10EFH | 4335 | AO2 End Point Value |  |  | R/W | Int
10F0H | 4336 | AO2 Output Starting Point Value | AO Type 4-20mA 0-20mA 0-5V 1-5V |  | R/W | Int
10F1H | 4337 | AO2 Output Slope 1 End/Slope 2 Start Point Value |  |  | R/W | Int
10F2H | 4338 | AO2 Output Slope 2 End/Slope 3 Start Point Value |  |  | R/W | Int
10F3H | 4339 | AO2 Output End Point Value |  |  | R/W | Int

## DI Counter
DI Counter: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Data Type | Access Property
AXM-IO1-1
4349H-434AH | 17225-17226 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
434BH-434CH | 17227-17228 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
434DH-434EH | 17229-17230 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
434FH-4350H | 17231-17232 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R
4351H-4352H | 17233-17234 | DI5 | DI5 Pulse Count | 0~4294967295 | Dword | R
4353H-4354H | 17235-17236 | DI6 | DI6 Pulse Count | 0~4294967295 | Dword | R
AXM-IO2-1
4355H-4356H | 17237-17238 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
4357H-4358H | 17239-17240 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
4359H-435AH | 17241-17242 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
435BH-435CH | 17243-17244 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R
AXM-IO3-1
435DH-435EH | 17245-17246 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
435FH-4360H | 17247-17248 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
4361H-4362H | 17249-17250 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
4363H-4364H | 17251-17252 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R
AXM-IO1-2
4365H-4366H | 17253-17254 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
4367H-4368H | 17255-17256 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
4369H-436AH | 17257-17258 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
436BH-436CH | 17259-17260 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R
436DH-436EH | 17261-17262 | DI5 | DI5 Pulse Count | 0~4294967295 | Dword | R
436FH-4370H | 17263-17264 | DI6 | DI6 Pulse Count | 0~4294967295 | Dword | R
AXM-IO2-2
4371H-4372H | 17265-17266 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
4373H-4374H | 17267-17268 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
4375H-4376H | 17269-17270 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
4377H-4378H | 17271-17272 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R
AXM-IO3-2
4379H-437AH | 17273-17274 | DI1 | DI1 Pulse Count | 0~4294967295 | Dword | R
437BH-437CH | 17275-17276 | DI2 | DI2 Pulse Count | 0~4294967295 | Dword | R
437DH-437EH | 17277-17278 | DI3 | DI3 Pulse Count | 0~4294967295 | Dword | R
437FH-4380H | 17279-17280 | DI4 | DI4 Pulse Count | 0~4294967295 | Dword | R

## DI Status
DI Status: 02H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Data Type | Access Property
AXM-IO1-1
0000H | 0 | DI1 | DI1 Status | 0: OFF 1: ON | Bit | R
0001H | 1 | DI2 | DI2 Status | 0: OFF 1: ON | Bit | R
0002H | 2 | DI3 | DI3 Status | 0: OFF 1: ON | Bit | R
0003H | 3 | DI4 | DI4 Status | 0: OFF 1: ON | Bit | R
0004H | 4 | DI5 | DI5 Status | 0: OFF 1: ON | Bit | R
0005H | 5 | DI6 | DI6 Status | 0: OFF 1: ON | Bit | R
AXM-IO2-1
0006H | 6 | DI1 | DI7 Status | 0: OFF 1: ON | Bit | R
0007H | 7 | DI2 | DI8 Status | 0: OFF 1: ON | Bit | R
0008H | 8 | DI3 | DI9 Status | 0: OFF 1: ON | Bit | R
0009H | 9 | DI4 | DI10 Status | 0: OFF 1: ON | Bit | R
AXM-IO3-1
000AH | 10 | DI1 | DI11 Status | 0: OFF 1: ON | Bit | R
000BH | 11 | DI2 | DI12 Status | 0: OFF 1: ON | Bit | R
000CH | 12 | DI3 | DI13 Status | 0: OFF 1: ON | Bit | R
000DH | 13 | DI4 | DI14 Status | 0: OFF 1: ON | Bit | R
AXM-IO1-2
000EH | 14 | DI1 | DI15 Status | 0: OFF 1: ON | Bit | R
000FH | 15 | DI2 | DI16 Status | 0: OFF 1: ON | Bit | R
0010H | 16 | DI3 | DI17 Status | 0: OFF 1: ON | Bit | R
0011H | 17 | DI4 | DI18 Status | 0: OFF 1: ON | Bit | R
0012H | 18 | DI5 | DI19 Status | 0: OFF 1: ON | Bit | R
0013H | 19 | DI6 | DI20 Status | 0: OFF 1: ON | Bit | R
AXM-IO2-2
0014H | 20 | DI1 | DI21 Status | 0: OFF 1: ON | Bit | R
0015H | 21 | DI2 | DI22 Status | 0: OFF 1: ON | Bit | R
0016H | 22 | DI3 | DI23 Status | 0: OFF 1: ON | Bit | R
0017H | 23 | DI4 | DI24 Status | 0: OFF 1: ON | Bit | R
AXM-IO3-2
0018H | 24 | DI1 | DI25 Status | 0: OFF 1: ON | Bit | R
0019H | 25 | DI2 | DI26 Status | 0: OFF 1: ON | Bit | R
001AH | 26 | DI3 | DI27 Status | 0: OFF 1: ON | Bit | R
001BH | 27 | DI4 | DI28 Status | 0: OFF 1: ON | Bit | R

## Analog Output
AIO Output Value: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Data Type | Access Property
4389H-438AH | 17289-17290 | AO_211 | Value of AO1 |  | Float | R
438BH-438CH | 17291-17292 | AO_212 | Value of AO2 |  | Float | R
438DH-438EH | 17293-17294 | AO_221 | Value of AO3 |  | Float | R
438FH-4390H | 17295-17296 | AO_222 | Value of AO4 |  | Float | R

## Analog Input
AI Input Value: 03H Read
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Data Type | Access Property
AXM-IO3-1
4385H | 17285 | AI1 | AI1 Sampling value | 0-4095 | Dword | R
4386H | 17286 | AI2 | AI2 Sampling vlaue | 0-4095 | Dword | R
AXM-IO3-2
4387H | 17287 | AI1 | AI3 Sampling value | 0-4095 | Dword | R
4388H | 17288 | AI2 | AI4 Sampling value | 0-4095 | Dword | R

## RO Status
RO Status: 01H Read;05H Control
Address (Hex) | Address (Dec) | Symbol | Parameter | Range | Data Type | Access Property
AXM-IO11
0000H | 0 | RO1 | Relay Output 1 | 0: OFF 1: ON | Bit | R
0001H | 1 | RO2 | Relay Output 2 | 0: OFF 1: ON | Bit | R
AXM-IO31
0002H | 2 | RO1 | Relay Output 1 | 0: OFF 1: ON | Bit | R
0003H | 3 | RO2 | Relay Output 2 | 0: OFF 1: ON | Bit | R
AXM-IO12
0004H | 4 | RO1 | Relay Output 1 | 0: OFF 1: ON | Bit | R
0005H | 5 | RO2 | Relay Output 2 | 0: OFF 1: ON | Bit | R
AXM-IO32
0006H | 6 | RO1 | Relay Output 1 | 0: OFF 1: ON | Bit | R
0007H | 7 | RO2 | Relay Output 2 | 0: OFF 1: ON | Bit | R

## Alarm Records
Alarm Records: 03H Read
Address (Hex) | Address (Dec) | Parameter | Property | Range | Data Type | Access Property
42A9H | 17065 | Alarm 1: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42AAH | 17066 | Alarm 1: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42ABH | 17067 | Alarm 1: Over/Under Limit |  | Related to Parameter chosen | Word | R
42ACH-42B2H | 17068-17074 | Alarm 1 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42B3H | 17075 | Alarm 2: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42B4H | 17076 | Alarm 2: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42B5H | 17077 | Alarm 2: Over/Under Limit |  | Related to Parameter chosen | Word | R
42B6H-42BCH | 17078-17084 | Alarm 2 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42BDH | 17085 | Alarm 3: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42BEH | 17086 | Alarm 3: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42BFH | 17087 | Alarm 3: Over/Under Limit |  | Related to Parameter chosen | Word | R
42C0H-42C6H | 17068-17094 | Alarm 3 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42C7H | 17095 | Alarm 4: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42C8H | 17096 | Alarm 4: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42C9H | 17097 | Alarm 4: Over/Under Limit |  | Related to Parameter chosen | Word | R
42CAH-42D0H | 17098-17104 | Alarm 4 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42D1H | 17105 | Alarm 5: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42D2H | 17106 | Alarm 5: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42D3H | 17107 | Alarm 5: Over/Under Limit |  | Related to Parameter chosen | Word | R
42D4H-42DAH | 17108-17114 | Alarm 5 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42DBH | 17115 | Alarm 6: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42DCH | 17116 | Alarm 6: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42DDH | 17117 | Alarm 6: Over/Under Limit |  | Related to Parameter chosen | Word | R
42DEH-42E4H | 17118-17124 | Alarm 6 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42E5H | 17125 | Alarm 7: Alarm Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42E6H | 17126 | Alarm 7: Alarm Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42E7H | 17127 | Alarm 7: Over/Under Limit |  | Related to Parameter chosen | Word | R
42E8H-42EEH | 17128-17134 | Alarm 7 Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42EFH | 17135 | Alarm 8:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42F0H | 17136 | Alarm 8: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42F1H | 17137 | Alarm 8: Over/Under Limit |  | Related to Parameter chosen | Word | R
42F2H-42F8H | 17138-17144 | Alarm 8: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
42F9H | 17145 | Alarm 9:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
42FAH | 17146 | Alarm 9: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
42FBH | 17147 | Alarm 9: Over/Under Limit |  | Related to Parameter chosen | Word | R
42FCH-4302H | 17148-17154 | Alarm 9: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
4303H | 17155 | Alarm 10:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
4304H | 17156 | Alarm 10: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
4305H | 17157 | Alarm 10: Over/Under Limit |  | Related to Parameter chosen | Word | R
4306H-430CH | 17158-17164 | Alarm 10: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
430DH | 17165 | Alarm 11:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
430EH | 17166 | Alarm 11: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
430FH | 17167 | Alarm 11: Over/Under Limit |  | Related to Parameter chosen | Word | R
4310H-4316H | 17168-17174 | Alarm 11: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
4317H | 17175 | Alarm 12:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
4318H | 17176 | Alarm 12: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
4319H | 17177 | Alarm 12: Over/Under Limit |  | Related to Parameter chosen | Word | R
431AH-4320H | 17178-17184 | Alarm 12: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
4321H | 17185 | Alarm 13:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
4322H | 17186 | Alarm 13: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
4323H | 17187 | Alarm 13: Over/Under Limit |  | Related to Parameter chosen | Word | R
4324H-432AH | 17188-17194 | Alarm 13: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
432BH | 17195 | Alarm 14:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
432CH | 17196 | Alarm 14: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
432DH | 17197 | Alarm 14: Over/Under Limit |  | Related to Parameter chosen | Word | R
432EH-4334H | 17198-17204 | Alarm 14: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
4335H | 17205 | Alarm 15:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
4336H | 17206 | Alarm 15: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
4337H | 17207 | Alarm 15: Over/Under Limit |  | Related to Parameter chosen | Word | R
4338H-433EH | 17208-17214 | Alarm 15: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R
433FH | 17215 | Alarm 16:Alarming Status | High Byte: Alarm ID Low Byte: Alarm Status 0: IN 1: OUT | 0-65535 | Word | R
4340H | 17216 | Alarm 16: Alarming Parameter Code |  | 0-79 Refer to Alarm Parameter Code Tab | Word | R
4341H | 17217 | Alarm 16: Over/Under Limit |  | Related to Parameter chosen | Word | R
4342H-4348H | 17218-17224 | Alarm 16: Time Stamp | YYY:MM:DD:hh:mm:ss:ms |  | Word | R

## Alarm Settings
Alarm Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
1046H | 4166 | Alarm Enable | 0: Disable 1: Enable | 0 | R/W | Word
1047H | 4167 | Enable Backlight flashing | 0: Disable 1: Enable | 0 | R/W | Word
1048H | 4168 | Alarm Channel Enable | 0-65535 0: Disable 1: Enable bit0: Channel 1 bit1: Channel 2 bit2: Channel 3 bit3: Channel 4 bit4: Channel 5 bit5: Channel 6 bit6: Channel 7 bit7: Channel 8 bit8: Channel 9 bit9: Channel 10 bit10: Channel 11 bit11: Channel 12 bit12: Channel 13 bit13: Channel 14 bit14: Channel 15 bit15: Channel 16 | 0 | R/W | Word
1049H | 4169 | "AND" Logic Enable | 0-255 0: Disable 1: Enable bit0: AND Alarm 1 & 2 bit1: AND Alarm 3 & 4 bit2: AND Alarm 5 & 6 bit3: AND Alarm 7 &8 bit4: AND Alarm 9 & 10 bit5: AND Alarm 11 & 12 bit6: AND Alarm 13 & 14 bit7: AND Alarm 15 & 16 | 0 | R/W | Word
104AH | 4170 | DO1 Alarm output | 0-65535 0: Disable 1: Enable bit0: Channel 1 bit1: Channel 2 bit2: Channel 3 bit3: Channel 4 bit4: Channel 5 bit5: Channel 6 bit6: Channel 7 bit7: Channel 8 bit8: Channel 9 bit9: Channel 10 bit10: Channel 11 bit11: Channel 12 bit12: Channel 13 bit13: Channel 14 bit14: Channel 15 bit15: Channel16 | 0 | R/W | Word
104BH | 4171 | DO2 Alarm output | 0-65535 0: Disable 1: Enable bit0: Channel 1 bit1: Channel 2 bit2: Channel 3 bit3: Channel 4 bit4: Channel 5 bit5: Channel 6 bit6: Channel 7 bit7: Channel 8 bit8: Channel 9 bit9: Channel 10 bit10: Channel 11 bit11: Channel 12 bit12: Channel 13 bit13: Channel 14 bit14: Channel 15 bit15: Channel16 | 0 | R/W | Word
104CH | 4172 | DO3 Alarm output | 0-65535 0: Disable 1: Enable bit0: Channel 1 bit1: Channel 2 bit2: Channel 3 bit3: Channel 4 bit4: Channel 5 bit5: Channel 6 bit6: Channel 7 bit7: Channel 8 bit8: Channel 9 bit9: Channel 10 bit10: Channel 11 bit11: Channel 12 bit12: Channel 13 bit13: Channel 14 bit14: Channel 15 bit15: Channel16 | 0
104DH | 4173 | DO4 Alarm output | 0-65535 0: Disable 1: Enable bit0: Channel 1 bit1: Channel 2 bit2: Channel 3 bit3: Channel 4 bit4: Channel 5 bit5: Channel 6 bit6: Channel 7 bit7: Channel 8 bit8: Channel 9 bit9: Channel 10 bit10: Channel 11 bit11: Channel 12 bit12: Channel 13 bit13: Channel 14 bit14: Channel 15 bit15: Channel16 | 0
Alarm Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
104EH | 4174 | Channel 1 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
104FH | 4175 | Channel 1 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1050H | 4176 | Channel 1 Setpoint Value | Related To Parameter |  | R/W | Word
1051H | 4177 | Channel 1 Delay | 0-3000 (ms) | 0 | R/W | Word
1052H | 4178 | Channel 1 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0 | R/W | Word
1053H | 4179 | Channel 2 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1054H | 4180 | Channel 2 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1055H | 4181 | Channel 2 Setpoint Value | Related To Parameter |  | R/W | Word
1056H | 4182 | Channel 2 Delay | 0-3000 (ms) | 0 | R/W | Word
1057H | 4183 | Channel 2 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1058H | 4184 | Channel 3 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1059H | 4185 | Channel 3 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
105AH | 4186 | Channel 3 Setpoint Value | Related To Parameter |  | R/W | Word
105BH | 4187 | Channel 3 Delay | 0-3000 (ms) | 0 | R/W | Word
105CH | 4188 | Channel 3 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
105DH | 4189 | Channel 4 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
105EH | 4190 | Channel 4 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
105FH | 4191 | Channel 4 Setpoint Value | Related To Parameter |  | R/W | Word
1060H | 4192 | Channel 4 Delay | 0-3000 (ms) | 0 | R/W | Word
1061H | 4193 | Channel 4 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1062H | 4194 | Channel 5 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1063H | 4195 | Channel 5 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1064H | 4196 | Channel 5 Setpoint Value | Related To Parameter |  | R/W | Word
1065H | 4197 | Channel 5 Delay | 0-3000 (ms) | 0 | R/W | Word
1066H | 4198 | Channel 5 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1067H | 4199 | Channel 6 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1068H | 4200 | Channel 6 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1069H | 4201 | Channel 6 Setpoint Value | Related To Parameter |  | R/W | Word
106AH | 4202 | Channel 6 Delay | 0-3000 (ms) | 0 | R/W | Word
106BH | 4203 | Channel 6 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
106CH | 4204 | Channel 7 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
106DH | 4205 | Channel 7 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
106EH | 4206 | Channel 7 Setpoint Value | Related To Parameter |  | R/W | Word
106FH | 4207 | Channel 7 Delay | 0-3000 (ms) | 0 | R/W | Word
1070H | 4208 | Channel 7 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1071H | 4209 | Channel 8 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1072H | 4210 | Channel 8 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1073H | 4211 | Channel 8 Setpoint Value | Related To Parameter |  | R/W | Word
1074H | 4212 | Channel 8 Delay | 0-3000 (ms) | 0 | R/W | Word
1075H | 4213 | Channel 8 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1076H | 4214 | Channel 9 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1077H | 4215 | Channel 9 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1078H | 4216 | Channel 9 Setpoint Value | Related To Parameter |  | R/W | Word
1079H | 4217 | Channel 9 Delay | 0-3000 (ms) | 0 | R/W | Word
107AH | 4218 | Channel 9 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
107BH | 4219 | Channel 10 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
107CH | 4220 | Channel 10 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
107DH | 4221 | Channel 10 Setpoint Value | Related To Parameter |  | R/W | Word
107EH | 4222 | Channel 10 Delay | 0-3000 (ms) | 0 | R/W | Word
107FH | 4223 | Channel 10 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1080H | 4224 | Channel 11 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1081H | 4225 | Channel 11 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1082H | 4226 | Channel 11 Setpoint Value | Related To Parameter |  | R/W | Word
1083H | 4227 | Channel 11 Delay | 0-3000 (ms) | 0 | R/W | Word
1084H | 4228 | Channel 11 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1085H | 4229 | Channel 12 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1086H | 4230 | Channel 12 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1087H | 4231 | Channel 12 Setpoint Value | Related To Parameter |  | R/W | Word
1088H | 4232 | Channel 12 Delay | 0-3000 (ms) | 0 | R/W | Word
1089H | 4233 | Channel 12 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
108AH | 4234 | Channel 13 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
108BH | 4235 | Channel 13 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
108CH | 4236 | Channel 13 Setpoint Value | Related To Parameter |  | R/W | Word
108DH | 4237 | Channel 13 Delay | 0-3000 (ms) | 0 | R/W | Word
108EH | 4238 | Channel 13 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
108FH | 4239 | Channel 14 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1090H | 4240 | Channel 14 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1091H | 4241 | Channel 14 Setpoint Value | Related To Parameter |  | R/W | Word
1092H | 4242 | Channel 14 Delay | 0-3000 (ms) | 0 | R/W | Word
1093H | 4243 | Channel 14 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1094H | 4244 | Channel 15 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
1095H | 4245 | Channel 15 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
1096H | 4246 | Channel 15 Setpoint Value | Related To Parameter |  | R/W | Word
1097H | 4247 | Channel 15 Delay | 0-3000 (ms) | 0 | R/W | Word
1098H | 4248 | Channel 15 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0
1099H | 4249 | Channel 16 Alarm Parameter | 0-79 Refer to Alarm Parameter Code Tab | 0 | R/W | Word
109AH | 4250 | Channel 16 Condition | 1: Greater Than 2: Equal To 3: Less Than |  | R/W | Word
109BH | 4251 | Channel 16 Setpoint Value | Related To Parameter |  | R/W | Word
109CH | 4252 | Channel 16 Delay | 0-3000 (ms) | 0 | R/W | Word
109DH | 4253 | Channel 16 Relay Output Channel | 0: None 1: RO1 (AXM-IO1-1) 2: RO2 (AXM-IO1-1) 3: RO1 (AXM-IO3-1) 4: RO2 (AXM-IO3-1) 5: RO1 (AXM-IO1-2) 6: RO2 (AXM-IO1-2 7: RO1 (AXM-IO3-2) 8: RO2 (AXM-IO3-2) | 0

## Alarm Parameter Code
Alarm Parameter Code Table
Setting Value | Alarming Object
0 | Frequency
1 | Phase A Voltage
2 | Phase B Voltage
3 | Phase C Voltage
4 | Average Phase Voltage
5 | Line Voltage AB
6 | Line Voltage BC
7 | Line Voltage CA
8 | Average Line-Line Voltage
9 | Phase A Current
10 | Phase B Current
11 | Phase C Current
12 | Average Current
13 | Neutral Current
14 | Phase A Active Power
15 | Phase B Active Power
16 | Phase C Active Power
17 | Total Active Power
18 | Phase A Reactive Power
19 | Phase B Reactive Power
20 | Phase C Reactive Power
21 | Total Reactive Power
22 | Phase A Apparent Power
23 | Phase B Apparent Power
24 | Phase C Apparent Power
25 | Total Apparent Power
26 | Phase A Power Factor
27 | Phase B Power Factor
28 | Phase C Power Factor
29 | Total Power Factor
30 | Voltage Unbalance Factor
31 | Current Unbalance Factor
32 | Load Characteristic (R/L/C)
33 | THD V1 (V12)
34 | THD V2 (V31)
35 | THD V3 (V23)
36 | Average Voltage THD
37 | THD I1
38 | THD I2
39 | THD I3
40 | Average Current THD
41 | Analog Input 1 (AXM-IO3-1)
42 | Analog Input 2 (AXM-IO3-1)
43 | Analog Input 1 (AXM-IO3-2)
44 | Analog Input 2 (AXM-IO3-2)
45 | Active Power Demand
46 | Reactive Power Demand
47 | Apparent Power Demand
48 | Phase A Current Demand
49 | Phase B Current Demand

## SOE Record
Alarm Records: 03H Read
Address (Hex) | Address (Dec) | Parameter | Property | Data Type | Access Property
4399H-439FH | 17305-17311 | 1st Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43A0H | 17312 | 1st Event DI Status | 0: OFF 1: ON | Word | R
43A1H-43A7H | 17313-17319 | 2nd Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43A8H | 17320 | 2nd Event DI Status | 0: OFF 1: ON | Word | R
43A9H-43AFH | 17321-17327 | 3rd Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43B0H | 17328 | 3rd Event DI Status | 0: OFF 1: ON | Word | R
43B1H-43B7H | 17329-17335 | 4th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43B8H | 17336 | 4th Event DI Status | 0: OFF 1: ON | Word | R
43B9H-43BFH | 17337-17343 | 5th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43C0H | 17344 | 5th Event DI Status | 0: OFF 1: ON | Word | R
43C1H-43C7H | 17345-17351 | 6th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43C8H | 17352 | 6th Event DI Status | 0: OFF 1: ON | Word | R
43C9H-43CFH | 17353-17359 | 7th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43D0H | 17360 | 7th Event DI Status | 0: OFF 1: ON | Word | R
43D1H-43D7H | 17361-17367 | 8th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43D8H | 17368 | 8th Event DI Status | 0: OFF 1: ON | Word | R
43D9H-43DFH | 17369-17375 | 9th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43E0H | 17376 | 9th Event DI Status | 0: OFF 1: ON | Word | R
43E1H-43E7H | 17377-17383 | 10th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43E8H | 17384 | 10th Event DI Status | 0: OFF 1: ON | Word | R
43E9H-43EFH | 17385-17391 | 11th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43F0H | 17392 | 11th Event DI Status | 0: OFF 1: ON | Word | R
43F1H-43F7H | 17393-17399 | 12th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
43F8H | 17400 | 12th Event DI Status | 0: OFF 1: ON | Word | R
43F9H-43FFH | 17401-17407 | 13th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4400H | 17408 | 13th Event DI Status | 0: OFF 1: ON | Word | R
4401H-4407H | 17409-17415 | 14th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4408H | 17416 | 14th Event DI Status | 0: OFF 1: ON | Word | R
4409H-440FH | 17417-17423 | 15th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4410H | 17424 | 15th Event DI Status | 0: OFF 1: ON | Word | R
4411H-4417H | 17425-17431 | 16th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4418H | 17432 | 16th Event DI Status | 0: OFF 1: ON | Word | R
4419H-441FH | 17433-17439 | 17th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4420H | 17440 | 17th Event DI Status | 0: OFF 1: ON | Word | R
4421H-4427H | 17441-17447 | 18th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4428H | 17448 | 18th Event DI Status | 0: OFF 1: ON | Word | R
4429H-442FH | 17449-17455 | 19th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4430H | 17456 | 19th Event DI Status | 0: OFF 1: ON | Word | R
4431H-4417H | 17457-17463 | 20th Event Timestamp | YYYY:MM:HH:mm:ss:ms | Word | R
4338H | 17464 | 20th Event DI Status | 0: OFF 1: ON | Word | R
4439H | 17465 | I/O Modules of SOE | 0: None 1: AXM-IO1-1 2: AXM-IO2-1 3: AXM-IO3-1 4: AXM-IO1-2 5: AXM-IO2-2 6: AXM-IO3-2 | Word | R

## Data Log 1,2,3 Settings
Data Log Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Property | Range | Data Type | Access Property
Data Log 1 Settings
1100H | 4352 | Data Log 1 Register Sector | Data Log 1 Memory Allocation | 0-100 | R/W | Word
1101H | 4353 | Data Log 1 Logging Interval | Logging interval in minutes | 0-1440 | R/W | Word
1102H-1176H | 4354-4470 | Data Log 1 Parameters Selections |  |  | R/W | Word
11B2H | 4530 | Data Log 1 Mode Selection | 0: Start Logging Immediately (No Stop, FIFO) | 0-2 | R/W | Word
1: Log only between time period
2: Start logging at a specific time (No stop, FIFO)
11B3H | 4531 | Start Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
11B4H | 4532 | Start Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
11B5H | 4533 | Start Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
11B6H | 4534 | End Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
11B7H | 4535 | End Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
11B8H | 4536 | End Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
11B9H | 4537 | Clear Data Log 1 | 0: No Clear | 0-1 | R/W | Word
1: Clear
Data Log 2 Settings
11C0H | 4544 | Data Log 2 Register Sector | Data Log 2 memory allocation | 0-100 | R/W | Word
11C1H | 4545 | Data Log 2 Logging Interval | Logging interval in minutes | 0-1440
11C2H-1236H | 4546-4662 | Data Log 2 Parameters Selection
1272H | 4722 | Data Log 2 Mode Selection | 0: Start Logging Immediately (No Stop, FIFO) | 0-2 | R/W | Word
1: Log only between time period
2: Start logging at a specific time (No stop, FIFO)
1273H | 4723 | Start Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
1274H | 4724 | Start Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
1275H | 4725 | Start Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
1276H | 4726 | End Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
1277H | 4727 | End Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
1278H | 4728 | End Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
1279H | 4729 | Clear Data Log 2 | 0: No Clear | 0-1 | R/W | Word
1: Clear
Data Log 3 Settings
11C0H | 4544 | Data Log 2 Register Sector | Data Log 2 memory allocation | 0-100 | R/W | Word
11C1H | 4545 | Data Log 2 Logging Interval | Logging interval in minutes | 0-1440
11C2H-1236H | 4546-4662 | Data Log 2 Parameters Selection
1272H | 4722 | Data Log 2 Mode Selection | 0: Start Logging Immediately (No Stop, FIFO) | 0-2 | R/W | Word
1: Log only between time period
2: Start logging at a specific time (No stop, FIFO)
1273H | 4723 | Start Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
1274H | 4724 | Start Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
1275H | 4725 | Start Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
1276H | 4726 | End Logging Time (Month, Year) |  | 1-12, 0-9999 | R/W | Word
1277H | 4727 | End Logging Time (Day, Hour) |  | 1-31, 0-23 | R/W | Word
1278H | 4728 | End Logging Time (Minute, Second) |  | 0-60, 0-60 | R/W | Word
1279H | 4729 | Clear Data Log 2 | 0: No Clear | 0-1 | R/W | Word
1: Clear

## Data Log Reading
Data Log Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Property | Range | Data Type | Access Property
6000H | 24576 | Data Log Selection | Data Log 1/2/3 |  | R/W | Word
6001H | 24577 | Data Log Record Number |  |  | R/W | Word
6002H-6003H | 24578-24579 | Recod Offset |  |  | R/W | Word
6004H-607EH | 24580-24702 | Window |  |  | R/W | Word

## Data Log Status
Data Log Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
Data Log 1 Status
6100H-6101H | 24832-24833 | Max Records |  | R | UINT32
6102H-6103H | 24834-24835 | Used Records |  | R | UINT32
6104H | 24836 | Record Size |  | R | UINT16
6105H | 24837 | Logs Available |  | R | Word
6106H-6108H | 24838-24840 | First Record Timestamp |  | R | Word
6109H-610BH | 24841-24843 | Last Record Timestamp |  | R | Word
Data Log 2 Status
6200H-6201H | 25088-25089 | Max Records |  | R | UINT32
6202H-6203H | 25090-25091 | Used Records |  | R | UINT32
6204H | 25092 | Record Size |  | R | UINT16
6205H | 25093 | Logs Available |  | R | Word
6206H-6208H | 25094-25096 | First Record Timestamp |  | R | Word
6209H-620BH | 25097-25099 | Last Record Timestamp |  | R | Word
Data Log 3 Status
6300H-6301H | 25344-25345 | Max Records |  | R | UINT32
6302H-6303H | 25346-25347 | Used Records |  | R | UINT32
6304H | 25348 | Record Size |  | R | UINT16
6305H | 25349 | Logs Available |  | R | Word
6306H-630BH | 25350-25352 | First Record Timestamp |  | R | Word
6309H-630BH | 25353-25355 | Last Record Timestamp |  | R | Word

## TOU Settings
TOU Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
TOU Basic Parameter Settings
7800H | 30720 | Season Number | 0-12 | 0 | Word | R/W
7801H | 30721 | Schedule Number | 0-14 | 0 | Word | R/W
7802H | 30722 | Segment Number | 0-14 | 0 | Word | R/W
7803H | 30723 | Tariff Number | 0-3 | 0 | Word | R/W
7804H | 30724 | Weekend setting | 0: Disable (Not Weekend) 1: Enable (Weekend) Bit0: Sunday Bit1: Monday Bit2: Tuesday Bit3: Wednesday Bit4: Thursday Bit5: Friday Bit6: Saturday | 0 | Word | R/W
7805H | 30725 | Weekend Schedule | 0-14 | 0 | Word | R/W
7806H | 30726 | Holiday Number | 0-30 | 0 | Word | R/W
7807H | 30727 | Time of Use Factory Setting | 0: Disable 1: Enable | 0 | Word | R/W
7808H | 30728 | End of Month Reset | 0: Disable 1: Enable | 0 | Word | R/W
7809H | 30729 | TOU reset date: day | 0-31 | 0 | Word | R/W
780AH | 30730 | TOU reset date :hour | 0-23 | 0 | Word | R/W
780BH | 30731 | TOU reset date: minute | 0-59 | 0 | Word | R/W
780CH | 30732 | TOU reset date: second | 0-59 | 0 | Word | R/W
780DH-780EH | 30733-30732 | Error Code | 0: Correct TOU Settings 1: Tariff Number Setting Error 2: Schedule Setting Error 4: Segment Setting Error 8: Season Setting Error 10: Segment Setting Error 12: Schedule Setting Error 16: Season Parameters Error 32: Holiday Number Setting Error 64: Holiday Parameters Error 256: Tarrif of Schedule Error 512: Time of Schedule Error 1024: Time Sequence Schdule Setting Error 2048: Weekend Schedule Number Setting Error 4096: Weekend Setting error | 0 | Word | R/W
Season Parameters
7820H-7822H | 30752-30754 | TOU Season 1 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7823H-7825H | 30755-30757 | TOU Season 2 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7826H-7828H | 30758-30760 | TOU Season 3 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7829H-782BH | 30761-30763 | TOU Season 4 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
782CH-782EH | 30764-30766 | TOU Season 5 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
782FH-7831H | 30767-30769 | TOU Season 6 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7832H-7834H | 30770-30772 | TOU Season 7 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7835H-7837H | 30773-30775 | TOU Season 8 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7838H-783AH | 30776-30778 | TOU Season 9 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
783BH-783DH | 30779-30781 | TOU Season 10 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
783EH-7840H | 30782-30784 | TOU Season 11 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7841H-7843H | 30785-30787 | TOU Season 12 | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
Schedule Parameters
Schedule 1
7844H-7846H | 30788-30790 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7847H-7849H | 30791-30793 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
784AH-784CH | 30794-30796 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
784DH-784FH | 30797-30799 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7850H-7852H | 30800-30802 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7853H-7855H | 30803-30805 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7856H-7858H | 30806-30808 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7859H-785BH | 30809-30811 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
785CH-785EH | 30812-30814 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
785FH-7861H | 30815-30817 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7862H-7864H | 30818-30820 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7865H-7867H | 30821-30823 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7868H-786AH | 30824-30826 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
786BH-786DH | 30827-30829 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 2
786EH-7870H | 30830-30832 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7871H-7873H | 30833-30835 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7874H-7876H | 30836-30838 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7877H-7879H | 30839-30841 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
787AH-787CH | 30842-30844 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
787DH-787FH | 30845-30847 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7880H-7882H | 30848-30850 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7883H-7885H | 30851-30853 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7886H-7888H | 30854-30856 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7889H-788BH | 30857-30859 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
788CH-788EH | 30860-30862 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
788FH-7891H | 30863-30865 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7892H-7894H | 30866-30868 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7895H-7897H | 30869-30871 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 3
7898H-789AH | 30872-30874 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
789BH-789DH | 30875-30877 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
789EH-78A0H | 30878-30880 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78A1H-78A3H | 30881-30883 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78A4H-78A6H | 30884-30886 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78A7H-78A9H | 30887-30889 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78AAH-78ACH | 30890-30892 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78ADH-78AFH | 30893-30895 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78B0H-78B2H | 30896-30898 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78B3H-78B5H | 30899-30901 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78B6H-78B8H | 30902-30904 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78B9H-78BBH | 30905-30907 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78BCH-78BEH | 30908-30910 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78BFH-78C1H | 30911-30913 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 4
78C2H-78C4H | 30914-30916 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78C5H-78C7H | 30917-30919 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78C8H-78CAH | 30920-30922 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78CBH-78CDH | 30923-30925 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78CEH-78D0H | 30926-30928 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78D1H-78D3H | 30929-30931 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78D4H-78D6H | 30932-30934 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78D7H-78D9H | 30935-30937 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78DAH-78DCH | 30938-30940 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78DDH-78DFH | 30941-30943 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78E0H-78E2H | 30944-30946 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78E3H-78E5H | 30947-30949 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78E6H-78E8H | 30950-30952 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78E9H-78EBH | 30953-30955 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 5
78ECH-78EEH | 30956-30958 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78EFH-78F1H | 30959-30961 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78F2H-78F4H | 30962-30964 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78F5H-78F7H | 30965-30967 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78F8H-78FAH | 30968-30970 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78FBH-78FDH | 30971-30973 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
78FEH-7900H | 30974-30976 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7901H-7903H | 30977-30979 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7904H-7906H | 30980-30982 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7907H-7909H | 30983-30985 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
790AH-790CH | 30986-30988 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
790DH-790FH | 30989-30991 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7910H-7912H | 30992-30994 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7913H-7915H | 30995-30997 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 6
7916H-7918H | 30998-31000 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7919H-791BH | 31001-31003 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
791CH-791EH | 31004-31006 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
791FH-7921H | 31007-31009 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7922H-7924H | 31010-31012 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7925H-7927H | 31013-31015 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7928H-792AH | 31016-31018 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
792BH-792DH | 31019-31021 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
792EH-7930H | 31022-31024 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7931H-7933H | 31025-31027 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7934H-7936H | 31028-31030 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7937H-7939H | 31031-31033 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
793AH-793CH | 31034-31036 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
793DH-793FH | 31037-31039 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 7
7940H-7942H | 31040-31042 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7943H-7945H | 31043-31045 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7946H-7948H | 31046-31048 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7949H-794BH | 31049-31051 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
794CH-794EH | 31052-31054 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
794FH-7951H | 31055-31057 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7952H-7954H | 31058-31060 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7955H-7957H | 31061-31063 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7958H-795AH | 31064-31066 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
795BH-795DH | 31067-31069 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
795EH-7960H | 31070-31072 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7961H-7963H | 31073-31075 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7964H-7966H | 31076-31078 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7967H-7969H | 31079-31081 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 8
796AH-796CH | 31082-31084 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
796DH-796FH | 31085-31087 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7970H-7972H | 31088-31090 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7973H-7975H | 31091-31093 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7976H-7978H | 31094-31096 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7979H-797BH | 31097-31099 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
797CH-797EH | 31100-31102 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
797FH-7981H | 31103-31105 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7982H-7984H | 31106-31108 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7985H-7987H | 31109-31111 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7988H-798AH | 31112-31114 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
798BH-798DH | 31115-31117 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
798EH-7990H | 31118-31120 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7991H-7993H | 31121-31123 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 9
7994H-7996H | 31124-31126 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7997H-7999H | 31127-31129 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
799AH-799CH | 31130-31132 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
799DH-799FH | 31133-31135 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79A0H-79A2H | 31136-31138 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79A3H-79A5H | 31139-31141 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79A6H-79A8H | 31142-31144 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79A9H-79ABH | 31145-31147 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79ACH-79AEH | 31148-31150 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79AFH-79B1H | 31151-31153 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79B2H-79B4H | 31154-31156 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79B5H-79B7H | 31157-31159 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79B8H-79BAH | 31160-31162 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79BBH-79BDH | 31163-31165 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 10
79BEH-79C0H | 31166-31168 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79C1H-79C3H | 31169-31171 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79C4H-79C6H | 31172-31174 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79C7H-79C9H | 31175-31177 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79CAH-79CCH | 31178-31180 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79CDH-79CFH | 31181-31183 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79D0H-79D2H | 31184-31186 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79D3H-79D5H | 31187-31189 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79D6H-79D8H | 31190-31192 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79D9H-79DBH | 31193-31195 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79DCH-79DEH | 31196-31198 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79DFH-79E1H | 31199-31201 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79E2H-79E4H | 31202-31204 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79E5H-79E7H | 31205-31207 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 11
79E8H-79EAH | 31208-31210 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79EBH-79EDH | 31211-31213 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79EEH-79F0H | 31214-31216 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79F1H-79F3H | 31217-31219 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79F4H-79F6H | 31220-31222 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79F7H-79F9H | 31223-31225 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79FAH-79FCH | 31226-31228 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
79FDH-79FFH | 31229-31231 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A00H-7A02H | 31232-31234 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A03H-7A05H | 31235-31237 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A06H-7A08H | 31238-31240 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A09H-7A0BH | 31241-31243 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A0CH-7A0EH | 31244-31246 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A0FH-7A11H | 31247-31249 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 12
7A12H-7A14H | 31250-31252 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A15H-7A17H | 31253-31255 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A18H-7A1AH | 31256-31258 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A1BH-7A1DH | 31259-31261 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A1EH-7A20H | 31262-31264 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A21H-7A23H | 31265-31267 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A24H-7A26H | 31268-31270 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A27H-7A29H | 31271-31273 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A2AH-7A2CH | 31274-31276 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A2DH-7A2FH | 31277-31279 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A30H-7A32H | 31280-31282 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A33H-7A35H | 31283-31285 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A36H-7A38H | 31286-31288 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A39H-7A3BH | 31289-31291 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 13
7A3CH-7A3EH | 31292-31294 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A3FH-7A41H | 31295-31297 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A42H-7A44H | 31298-31300 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A45H-7A47H | 31301-31303 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A48H-7A4AH | 31304-31306 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A4BH-7A4DH | 31307-31309 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A4EH-7A50H | 31310-31312 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A51H-7A53H | 31313-31315 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A54H-7A56H | 31316-31318 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A57H-7A59H | 31319-31321 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A5AH-7A5CH | 31322-31324 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A5DH-7A5FH | 31325-31327 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A60H-7A62H | 31328-31330 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A63H-7A65H | 31331-31333 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Schedule 14
7A66H-7A68H | 31334-31336 | Segment 1 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A69H-7A6BH | 31337-31339 | Segment 2 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A6CH-7A6EH | 31340-31342 | Segment 3 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A6FH-7A71H | 31343-31345 | Segment 4 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A72H-7A74H | 31346-31348 | Segment 5 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A75H-7A77H | 31349-31351 | Segment 6 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A78H-7A7AH | 31352-31354 | Segment 7 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A7BH-7A7DH | 31355-31357 | Segment 8 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A7EH-7A80H | 31358-31360 | Segment 9 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A81H-7A83H | 31361-31363 | Segment 10 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A84H-7A86H | 31364-31366 | Segment 11 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A87H-7A89H | 31367-31369 | Segment 12 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A8AH-7A8CH | 31370-31372 | Segment 13 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
7A8DH-7A8FH | 31373-31375 | Segment 14 (Hour, Minute, Tariff) | HH MM TT HH: 0-24 MM: 0-60 TT: 0:3 | 00 00 00 | Word | R/W
Holiday Setting
7A90H-7A92H | 31376-31378 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7A93H-7A95H | 31379-31381 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7A96H-7A98H | 31382-31384 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7A99H-7A9BH | 31385-31387 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7A9CH-7A9EH | 31388-31390 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7A9FH-7AA1H | 31391-31393 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AA2H-7AA4H | 31394-31396 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AA5H-7AA7H | 31397-31399 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AA8H-7AAAH | 31400-31402 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AABH-7AADH | 31403-31405 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AAEH-7AB0H | 31406-31408 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AB1H-7AB3H | 31409-31411 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AB4H-7AB6H | 31412-31414 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AB7H-7AB9H | 31415-31417 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ABAH-7ABCH | 31418-31420 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ABDH-7ABFH | 31421-31423 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AC0H-7AC2H | 31424-31426 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AC3H-7AC5H | 31427-31429 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AC6H-7AC8H | 31430-31432 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AC9H-7ACBH | 31433-31435 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ACCH-7ACEH | 31436-31438 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ACFH-7AD1H | 31439-31441 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AD2H-7AD4H | 31442-31444 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AD5H-7AD7H | 31445-31447 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AD8H-7ADAH | 31448-31450 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ADBH-7ADDH | 31451-31453 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7ADEH-7AE0H | 31454-31456 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AE1H-7AE3H | 31457-31459 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AE4H-7AE6H | 31460-31462 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7AE7H-7AE9H | 31463-31465 | 30th Holiday: (Month, Day, Schedule ID) | MM DD ID MM:0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W

## TOU Daylight Savings
Daylight Savings Time Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
7700H | 30464 | DST Enable | 0: Disable 1: Enable | Word | R/W
7701H | 30465 | DST format | 0: Format 1(Fixed Date) 1: Format 2 (Non Fixed Date) | Word | R/W
Format 1: Fixed Date
7702H | 30466 | DST Start Month | 1-12 | Word | R/W
7703H | 30467 | DST Start Day | 1-31 | Word | R/W
7704H | 30468 | DST Start Hour | 0-23 | Word | R/W
7705H | 30469 | DST Start Min | 0-59 | Word | R/W
7706H | 30470 | DST Start Adjust time (Unit: Min) | 1-120 | Word | R/W
7707H | 30471 | DST Ending Month | 1-12 | Word | R/W
7708H | 30472 | DST Ending Day | 1-31 | Word | R/W
7709H | 30473 | DST Ending Hour | 0-23 | Word | R/W
770AH | 30474 | DST Ending Minute | 0-59 | Word | R/W
770BH | 30475 | DST Ending Adjust time (Unit: Minute) | 1-120 | Word | R/W
Format 2: Non Fixed Date
770CH | 30476 | DST Start Month | 1-12 | Word | R/W
770DH | 30477 | DST Start Day | 0-6 0: Sunday 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday | Word | R/W
770EH | 30478 | DST Start Week | 1-5 | Word | R/W
770FH | 30479 | DST Start Hour | 0-23 | Word | R/W
7710H | 30480 | DST Start Minute | 0-59 | Word | R/W
7711H | 30481 | DST Start Adjust time (Unit: Minute) | 1-120 | Word | R/W
7712H | 30482 | DST Ending Month | 1-12 | Word | R/W
7713H | 30483 | DST Ending Day | 0-6 0: Sunday 1: Monday 2: Tuesday 3: Wednesday 4: Thursday 5: Friday 6: Saturday | Word | R/W
7714H | 30484 | DST Ending Week | 1-5 | Word | R/W
7715H | 30485 | DST Ending Hour | 0-23 | Word | R/W
7716H | 30486 | DST Ending Minute | 0-59 | Word | R/W
7717H | 30487 | DST Ending Adjust time (Unit: Minute) | 1-120 | Word | R/W

## TOU Weekends Schedule
TOU Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Data Type | Access Property
TOU Weekends Schedule Settings
7F00H | 32512 | Multiple Weekend Schedule Enable | 0: Disable 1: Enable If 0, Weekend schedule uses registers 0x7804H & 0x7805H | Word | R/W
7F01H | 32513 | 1st Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F02H | 32514 | 1st Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F03H | 32515 | 1st Season: Monday's Schedule Number | 0-14 | Word | R/W
7F04H | 32516 | 1st Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F05H | 32517 | 1st Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F06H | 32518 | 1st Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F07H | 32519 | 1st Season: Friday's Schedule Number | 0-14 | Word | R/W
7F08H | 32520 | 1st Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F09H | 32521 | 2nd Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F0AH | 32522 | 2nd Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F0BH | 32523 | 2nd Season: Monday's Schedule Number | 0-14 | Word | R/W
7F0CH | 32524 | 2nd Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F0DH | 32525 | 2nd Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F0EH | 32526 | 2nd Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F0FH | 32527 | 2nd Season: Friday's Schedule Number | 0-14 | Word | R/W
7F10H | 32528 | 2nd Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F11H | 32529 | 3rd Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F12H | 32530 | 3rd Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F13H | 32531 | 3rd Season: Monday's Schedule Number | 0-14 | Word | R/W
7F14H | 32532 | 3rd Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F15H | 32533 | 3rd Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F16H | 32534 | 3rd Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F17H | 32535 | 3rd Season: Friday's Schedule Number | 0-14 | Word | R/W
7F18H | 32536 | 3rd Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F19H | 32537 | 4th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F1AH | 32538 | 4th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F1BH | 32539 | 4th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F1CH | 32540 | 4th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F1DH | 32541 | 4th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F1EH | 32542 | 4th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F1FH | 32543 | 4th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F20H | 32544 | 4th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F21H | 32545 | 5th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F22H | 32546 | 5th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F23H | 32547 | 5th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F24H | 32548 | 5th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F25H | 32549 | 5th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F26H | 32550 | 5th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F27H | 32551 | 5th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F28H | 32552 | 5th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F29H | 32553 | 6th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F2AH | 32554 | 6th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F2BH | 32555 | 6th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F2CH | 32556 | 6th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F2DH | 32557 | 6th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F2EH | 32558 | 6th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F2FH | 32559 | 6th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F30H | 32560 | 6th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F31H | 32561 | 7th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F32H | 32562 | 7th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F33H | 32563 | 7th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F34H | 32564 | 7th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F35H | 32565 | 7th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F36H | 32566 | 7th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F37H | 32567 | 7th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F38H | 32568 | 7th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F39H | 32569 | 8th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F3AH | 32570 | 8th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F3BH | 32571 | 8th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F3CH | 32572 | 8th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F3DH | 32573 | 8th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F3EH | 32574 | 8th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F3FH | 32575 | 8th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F40H | 32576 | 8th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F41H | 32577 | 9th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F42H | 32578 | 9th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F43H | 32579 | 9th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F44H | 32580 | 9th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F45H | 32581 | 9th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F46H | 32582 | 9th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F47H | 32583 | 9th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F48H | 32584 | 9th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F49H | 32585 | 10th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F4AH | 32586 | 10th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F4BH | 32587 | 10th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F4CH | 32588 | 10th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F4DH | 32589 | 10th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F4EH | 32590 | 10th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F4FH | 32591 | 10th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F50H | 32592 | 10th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F51H | 32593 | 11th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F52H | 32594 | 11th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F53H | 32595 | 11th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F54H | 32596 | 11th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F55H | 32597 | 11th Season: Wednesday's Schedule Number | 0-14 | Word | R/W
7F56H | 32598 | 11th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F57H | 32599 | 11th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F58H | 32600 | 11th Season: Saturday's Schedule Number | 0-14 | Word | R/W
7F59H | 32601 | 12th Season: Weekend Setting | 0: Disable 1: Enable bit0: Sunday bit1: Monday bit2: Tuesday bit3: Wednesday bit4: Thursday bit5: Friday bit6: Saturday | Word | R/W
7F5AH | 32602 | 12th Season: Sunday's Schedule Number | 0-14 | Word | R/W
7F5BH | 32603 | 12th Season: Monday's Schedule Number | 0-14 | Word | R/W
7F5CH | 32604 | 12th Season: Tuesday's Schedule Number | 0-14 | Word | R/W
7F5DH | 32605 | 12th Season:Wednesday's Schedule Number | 0-14 | Word | R/W
7F5EH | 32606 | 12th Season: Thursday's Schedule Number | 0-14 | Word | R/W
7F5FH | 32607 | 12th Season: Friday's Schedule Number | 0-14 | Word | R/W
7F60H | 32608 | 12th Season: Saturday's Schedule Number | 0-14 | Word | R/W

## 10 Year Holiday
10 Year Holiday Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
7AEAH | 31466 | Holiday Setting Enable | 0: Disable 1: Enable | 0 | Word | R/W
7AEBH | 31467 | Start Year | 2000-2099 | 0 | Word | R/W
7AECH | 31468 | End Year | 2000-2099 | 0 | Word | R/W
Year 1
7B00H-7B02H | 31488-31490 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B03H-7B05H | 31491-31493 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B06H-7B08H | 31494-31496 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B09H-7B0BH | 31497-31499 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B0CH-7B0EH | 31500-31502 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B0FH-7B11H | 31503-31505 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B12H-7B14H | 31506-31508 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B15H-7B17H | 31509-31511 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B18H-7B1AH | 31512-31514 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B1BH-7B1DH | 31515-31517 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B1EH-7B20H | 31518-31520 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B21H-7B23H | 31521-31523 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B24H-7B26H | 31524-31526 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B27H-7B29H | 31527-31529 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B2AH-7B2CH | 31530-31532 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B2DH-7B2FH | 31533-31535 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B30H-7B32H | 31536-31538 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B33H-7B35H | 31539-31541 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B36H-7B38H | 31542-31544 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B39H-7B3BH | 31545-31547 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B3CH-7B3EH | 31548-31550 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B3FH-7B41H | 31551-31553 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B42H-7B44H | 31554-31556 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B45H-7B47H | 31557-31559 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B48H-7B4AH | 31560-31562 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B4BH-7B4DH | 31563-31565 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B4EH-7B50H | 31566-31568 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B51H-7B53H | 31569-31571 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B54H-7B56H | 31572-31574 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B57H-7B59H | 31575-31577 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B5AH | 31578 | Setting Year | 2000-2099 | 0 | Word | R/W
7B5BH | 31579 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 2
7B5CH-7B5EH | 31580-31582 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B5FH-7B61H | 31583-31585 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B62H-7B64H | 31586-31588 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B65H-7B67H | 31589-31591 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B68H-7B6AH | 31592-31594 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B6BH-7B6DH | 31595-31597 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B6EH-7B70H | 31598-31600 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B71H-7B73H | 31601-31603 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B74H-7B76H | 31604-31606 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B77H-7B79H | 31607-31609 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B7AH-7B7CH | 31610-31612 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B7DH-7B7FH | 31613-31615 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B80H-7B82H | 31616-31618 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B83H-7B85H | 31619-31621 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B86H-7B88H | 31622-31624 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B89H-7B8BH | 31625-31627 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B8CH-7B8EH | 31628-31630 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B8FH-7B91H | 31631-31633 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B92H-7B94H | 31634-31636 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B95H-7B97H | 31637-31639 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B98H-7B9AH | 31640-31642 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B9BH-7B9DH | 31643-31645 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7B9EH-7BA0H | 31646-31648 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BA1H-7BA3H | 31649-31651 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BA4H-7BA6H | 31652-31654 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BA7H-7BA9H | 31655-31657 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BAAH-7BACH | 31658-31660 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BADH-7BAFH | 31661-31663 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BB0H-7BB2H | 31664-31666 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BB3H-7BB5H | 31667-31669 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BB6H | 31670 | Setting Year | 2000-2099 | 0 | Word | R/W
7BB7H | 31671 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 3
7BB8H-7BBAH | 31672-31674 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BBBH-7BBDH | 31675-31677 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BBEH-7BC0H | 31678-31680 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BC1H-7BC3H | 31681-31683 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BC4H-7BC6H | 31684-31686 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BC7H-7BC9H | 31687-31689 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BCAH-7BCCH | 31690-31692 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BCDH-7BCFH | 31693-31695 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BD0H-7BD2H | 31696-31698 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BD3H-7BD5H | 31699-31701 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BD6H-7BD8H | 31702-31704 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BD9H-7BDBH | 31705-31707 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BDCH-7BDEH | 31708-31710 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BDFH-7BE1H | 31711-31713 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BE2H-7BE4H | 31714-31716 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BE5H-7BE7H | 31717-31719 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BE8H-7BEAH | 31720-31722 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BEBH-7BEDH | 31723-31725 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BEEH-7BF0H | 31726-31728 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BF1H-7BF3H | 31729-31731 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BF4H-7BF6H | 31732-31734 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BF7H-7BF9H | 31735-31737 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BFAH-7BFCH | 31738-31740 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7BFDH-7BFFH | 31741-31743 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C00H-7C02H | 31744-31746 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C03H-7C05H | 31747-31749 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C06H-7C08H | 31750-31752 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C09H-7C0BH | 31753-31755 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C0CH-7C0EH | 31756-31758 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C0FH-7C11H | 31759-31761 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C12H | 31762 | Setting Year | 2000-2099 | 0 | Word | R/W
7C13H | 31763 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 4
7C14H-7C16H | 31764-31766 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C17H-7C19H | 31767-31769 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C1AH-7C1CH | 31770-31772 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C1DH-7C1FH | 31773-31775 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C20H-7C22H | 31776-31778 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C23H-7C25H | 31779-31781 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C26H-7C28H | 31782-31784 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C29H-7C2BH | 31785-31787 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C2CH-7C2EH | 31788-31790 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C2FH-7C31H | 31791-31793 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C32H-7C34H | 31794-31796 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C35H-7C37H | 31797-31799 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C38H-7C3AH | 31800-31802 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C3BH-7C3DH | 31803-31805 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C3EH-7C40H | 31806-31808 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C41H-7C43H | 31809-31811 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C44H-7C46H | 31812-31814 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C47H-7C49H | 31815-31817 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C4AH-7C4CH | 31818-31820 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C4DH-7C4FH | 31821-31823 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C50H-7C52H | 31824-31826 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C53H-7C55H | 31827-31829 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C56H-7C58H | 31830-31832 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C59H-7C5BH | 31833-31835 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C5CH-7C5EH | 31836-31838 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C5FH-7C61H | 31839-31841 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C62H-7C64H | 31842-31844 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C65H-7C67H | 31845-31847 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C68H-7C6AH | 31848-31850 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C6BH-7C6DH | 31851-31853 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C6EH | 31854 | Setting Year | 2000-2099 | 0 | Word | R/W
7C6FH | 31855 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 5
7C70H-7C72H | 31856-31858 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C73H-7C75H | 31859-31861 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C76H-7C78H | 31862-31864 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C79H-7C7BH | 31865-31867 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C7CH-7C7EH | 31868-31870 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C7FH-7C81H | 31871-31873 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C82H-7C84H | 31874-31876 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C85H-7C87H | 31877-31879 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C88H-7C8AH | 31880-31882 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C8BH-7C8DH | 31883-31885 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C8EH-7C90H | 31886-31888 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C91H-7C93H | 31889-31891 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C94H-7C96H | 31892-31894 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C97H-7C99H | 31895-31897 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C9AH-7C9CH | 31898-31900 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7C9DH-7C9FH | 31901-31903 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CA0H-7CA2H | 31904-31906 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CA3H-7CA5H | 31907-31909 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CA6H-7CA8H | 31910-31912 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CA9H-7CABH | 31913-31915 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CACH-7CAEH | 31916-31918 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CAFH-7CB1H | 31919-31921 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CB2H-7CB4H | 31922-31924 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CB5H-7CB7H | 31925-31927 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CB8H-7CBAH | 31928-31930 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CBBH-7CBDH | 31931-31933 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CBEH-7CC0H | 31934-31936 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CC1H-7CC3H | 31937-31939 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CC4H-7CC6H | 31940-31942 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CC7H-7CC9H | 31943-31945 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CCAH | 31946 | Setting Year | 2000-2099 | 0 | Word | R/W
7CCBH | 31947 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 6
7CCCH-7CCEH | 31948-31950 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CCFH-7CD1H | 31951-31953 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CD2H-7CD4H | 31954-31956 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CD5H-7CD7H | 31957-31959 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CD8H-7CDAH | 31960-31962 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CDBH-7CDDH | 31963-31965 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CDEH-7CE0H | 31966-31968 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CE1H-7CE3H | 31969-31971 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CE4H-7CE6H | 31972-31974 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CE7H-7CE9H | 31975-31977 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CEAH-7CECH | 31978-31980 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CEDH-7CEFH | 31981-31983 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CF0H-7CF2H | 31984-31986 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CF3H-7CF5H | 31987-31989 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CF6H-7CF8H | 31990-31992 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CF9H-7CFBH | 31993-31995 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CFCH-7CFEH | 31996-31998 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7CFFH-7D01H | 31999-32001 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D02H-7D04H | 32002-32004 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D05H-7D07H | 32005-32007 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D08H-7D0AH | 32008-32010 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D0BH-7D0DH | 32011-32013 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D0EH-7D10H | 32014-32016 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D11H-7D13H | 32017-32019 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D14H-7D16H | 32020-32022 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D17H-7D19H | 32023-32025 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D1AH-7D1CH | 32026-32028 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D1DH-7D1FH | 32029-32031 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D20H-7D22H | 32032-32034 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D23H-7D25H | 32035-32037 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D26H | 32038 | Setting Year | 2000-2099 | 0 | Word | R/W
7D27H | 32039 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 7
7D28H-7D2AH | 32040-32042 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D2BH-7D2DH | 32043-32045 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D2EH-7D30H | 32046-32048 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D31H-7D33H | 32049-32051 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D34H-7D36H | 32052-32054 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D37H-7D39H | 32055-32057 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D3AH-7D3CH | 32058-32060 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D3DH-7D3FH | 32061-32063 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D40H-7D42H | 32064-32066 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D43H-7D45H | 32067-32069 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D46H-7D48H | 32070-32072 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D49H-7D4BH | 32073-32075 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D4CH-7D4EH | 32076-32078 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D4FH-7D51H | 32079-32081 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D52H-7D54H | 32082-32084 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D55H-7D57H | 32085-32087 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D58H-7D5AH | 32088-32090 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D5BH-7D5DH | 32091-32093 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D5EH-7D60H | 32094-32096 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D61H-7D63H | 32097-32099 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D64H-7D66H | 32100-32102 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D67H-7D69H | 32103-32105 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D6AH-7D6CH | 32106-32108 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D6DH-7D6FH | 32109-32111 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D70H-7D72H | 32112-32114 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D73H-7D75H | 32115-32117 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D76H-7D78H | 32118-32120 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D79H-7D7BH | 32121-32123 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D7CH-7D7EH | 32124-32126 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D7FH-7D81H | 32127-32129 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D82H | 32130 | Setting Year | 2000-2099 | 0 | Word | R/W
7D83H | 32131 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 8
7D84H-7D86H | 32132-32134 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D87H-7D89H | 32135-32137 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D8AH-7D8CH | 32138-32140 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D8DH-7D8FH | 32141-32143 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D90H-7D92H | 32144-32146 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D93H-7D95H | 32147-32149 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D96H-7D98H | 32150-32152 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D99H-7D9BH | 32153-32155 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D9CH-7D9EH | 32156-32158 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7D9FH-7DA1H | 32159-32161 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DA2H-7DA4H | 32162-32164 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DA5H-7DA7H | 32165-32167 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DA8H-7DAAH | 32168-32170 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DABH-7DADH | 32171-32173 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DAEH-7DB0H | 32174-32176 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DB1H-7DB3H | 32177-32179 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DB4H-7DB6H | 32180-32182 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DB7H-7DB9H | 32183-32185 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DBAH-7DBCH | 32186-32188 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DBDH-7DBFH | 32189-32191 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DC0H-7DC2H | 32192-32194 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DC3H-7DC5H | 32195-32197 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DC6H-7DC8H | 32198-32200 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DC9H-7DCBH | 32201-32203 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DCCH-7DCEH | 32204-32206 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DCFH-7DD1H | 32207-32209 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DD2H-7DD4H | 32210-32212 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DD5H-7DD7H | 32213-32215 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DD8H-7DDAH | 32216-32218 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DDBH-7DDDH | 32219-32221 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DDEH | 32222 | Setting Year | 2000-2099 | 0 | Word | R/W
7DDFH | 32223 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 9
7DE0H-7DE2H | 32224-32226 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DE3H-7DE5H | 32227-32229 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DE6H-7DE8H | 32230-32232 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DE9H-7DEBH | 32233-32235 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DECH-7DEEH | 32236-32238 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DEFH-7DF1H | 32239-32241 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DF2H-7DF4H | 32242-32244 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DF5H-7DF7H | 32245-32247 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DF8H-7DFAH | 32248-32250 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DFBH-7DFDH | 32251-32253 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7DFEH-7E00H | 32254-32256 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E01H-7E03H | 32257-32259 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E04H-7E06H | 32260-32262 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E07H-7E09H | 32263-32265 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E0AH-7E0CH | 32266-32268 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E0DH-7E0FH | 32269-32271 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E10H-7E12H | 32272-32274 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E13H-7E15H | 32275-32277 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E16H-7E18H | 32278-32280 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E19H-7E1BH | 32281-32283 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E1CH-7E1EH | 32284-32286 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E1FH-7E21H | 32287-32289 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E22H-7E24H | 32290-32292 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E25H-7E27H | 32293-32295 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E28H-7E2AH | 32296-32298 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E2BH-7E2DH | 32299-32301 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E2EH-7E30H | 32302-32304 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E31H-7E33H | 32305-32307 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E34H-7E36H | 32308-32310 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E37H-7E39H | 32311-32313 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E3AH | 32314 | Setting Year | 2000-2099 | 0 | Word | R/W
7E3BH | 32315 | Holiday Number setting | 0-30 | 0 | Word | R/W
Year 10
7E3CH-7E3EH | 32316-32318 | 1st Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E3FH-7E41H | 32319-32321 | 2nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E42H-7E44H | 32322-32324 | 3rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E45H-7E47H | 32325-32327 | 4th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E48H-7E4AH | 32328-32330 | 5th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E4BH-7E4DH | 32331-32333 | 6th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E4EH-7E50H | 32334-32336 | 7th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E51H-7E53H | 32337-32339 | 8th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E54H-7E56H | 32340-32342 | 9th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E57H-7E59H | 32343-32345 | 10th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E5AH-7E5CH | 32346-32348 | 11th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E5DH-7E5FH | 32349-32351 | 12th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E60H-7E62H | 32352-32354 | 13th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E63H-7E65H | 32355-32357 | 14th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E66H-7E68H | 32358-32360 | 15th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E69H-7E6BH | 32361-32363 | 16th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E6CH-7E6EH | 32364-32366 | 17th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E6FH-7E71H | 32367-32369 | 18th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E72H-7E74H | 32370-32372 | 19th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E75H-7E77H | 32373-32375 | 20th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E78H-7E7AH | 32376-32378 | 21th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E7BH-7E7DH | 32379-32381 | 22nd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E7EH-7E80H | 32382-32384 | 23rd Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E81H-7E83H | 32385-32387 | 24th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E84H-7E86H | 32388-32390 | 25th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E87H-7E89H | 32391-32393 | 26th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E8AH-7E8CH | 32394-32396 | 27th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E8DH-7E8FH | 32397-32399 | 28th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E90H-7E92H | 32400-32402 | 29th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E93H-7E95H | 32403-32405 | 30th Holiday (Month, Day, Schedule ID) | MM DD ID MM: 0-12 DD: 0-31 ID: 0-14 | 00 00 00 | Word | R/W
7E96H | 32406 | Setting Year | 2000-2099 | 0 | Word | R/W
7E97H | 32407 | Holiday Number setting | 0-30 | 0 | Word | R/W

## Waveform Capture Settings
Waveform Capture Settings: 03H Read, 10H Write
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property
8000H | 32768 | Manually Trigger Waveform | 0xAA: Trigger Manual Capture 0: No Capture | 0 | Word | R/W
8001H | 32769 | DI Trigger-AXM-IO1-1 | 00: Disable 01:From OFF to ON 10:From ON to OFF 11:Any DI change bit0, bit1: DI1 bit2, bit3: DI2 bit4,bit5: DI3 bit6, bit7: DI4 bit8, bit9: DI5 bit10, bit11: DI6 | 0 | Word | R/W
8002H | 32770 | DI Trigger-AXM-IO2-1 | 00: Disable 01:From OFF to ON 10:From ON to OFF 11:Any DI change bit0, bit1: DI1 bit2, bit3: DI2 bit4,bit5: DI3 bit6, bit7: DI4 | 0 | Word | R/W
8003H | 32771 | DI Trigger-AXM-IO3-1 | 00: Disable 01:From OFF to ON 10:From ON to OFF 11:Any DI change bit0, bit1: DI1 bit2, bit3: DI2 bit4,bit5: DI3 bit6, bit7: DI4 | 0 | Word | R/W
8004H | 32772 | Voltage Rated Value | 50V-400V 50V-690V (Delta) | 400 | Word | R/W
8005H | 32773 | Voltage Sag Trigger | 0: Disable 1: Enable | 0 | Word | R/W
8006H | 32774 | Voltage Sag Threshold | 20-100% | 50 | Word | R/W
8007H | 32775 | Voltage Sag Half Cycle | 4-200 Half Cycle | 10 | Word | R/W
8008H | 32776 | Voltage Swell Trigger | 0:Disable 1:Enable | 0 | Word | R/W
8009H | 32777 | Voltage Swell Threshold | 50-140% | 100 | Word | R/W
800AH | 32778 | Reserved
800BH | 32779 | Current Rated Value | 0.5-5A | 5 | Word | R/W
800CH | 32780 | Over-Current Trigger | 0:Disable 1:Enable | 0 | Word | R/W
800DH | 32781 | Over-Current Threshold | 50-150% | 100 | Word | R/W
800EH | 32782 | Waveform Clear | Clear: 0x55 No Clear: 0 | 0 | Word | R/W
800FH | 32783 | Power Quality Event Clear | Clear: 0x55 No Clear: 0 | 0 | Word | R/W

## SunSpec
SunSpec 03H Read
Address (Hex) | Address (Dec) | Parameter | Range | Default | Data Type | Access Property | Number of Registers
C350H-C351H | 50000-50001 | SunSpec_ID | 0x53756e53 |  | Uint16 | R | 2
C352H | 50002 | ID | 1 |  | Uint16 | R | 1
C353H | 50003 | Length | 65 |  | String | R | 1
C354H-C363H | 50004-50019 | Manufacturer |  | Accuenergy | String | R | 16
C364H-C373H | 50020-50035 | Model | Manufacturer Specific Value (32 chars) | Acuvim II | String | R | 16
C374H-C37BH | 50036-50043 | Options | Manufacturer Specific Value (16 chars) | Acuvim IIR/IIW | String | R | 8
C37CH-C383H | 50044-50051 | Version | Manufacturer Specific Value (16 chars) | H: 2.31 S: 3.60 | String | R | 8
C384H-C393H | 50052-50067 | Serial Number | Manufacturer specific value (32 chars) |  | String | R | 16
C394H | 50068 | Device Address | Modbus device address |  | Uint16 | R | 1
C395H | 50069 | ID | Meter Configuration Single Phase (AN or AB): 201 Split single phase (ABN): 202 WYE-three phase (ABCN): 203 Delta three phase (ABC): 204 |  | Uint16 | R | 1
C396H | 50070 | Length | 81 |  | Uint16 | R | 1
C397H | 50071 | Current: Amps(Average) | 0-32767 A |  | Int16 | R | 1
C398H | 50072 | Current: Phase A | 0-32767 A |  | Int16 | R | 1
C399H | 50073 | Current: Phase B | 0-32767 A |  | Int16 | R | 1
C39AH | 50074 | Current: Phase C | 0-32767 A |  | Int16 | R | 1
C39BH | 50075 | Current SunSpec Scale Factor: | -3~ 2'(used an exponent of a power of 10) |  | sunssf | R | 1
C39CH | 50076 | Voltage: Average Phase | 0-9999 V |  | Int16 | R | 1
C39DH | 50077 | Voltage:Phase A | 0-9999 V |  | Int16 | R | 1
C39EH | 50078 | Voltage: Phase B | 0-9999 V |  | Int16 | R | 1
C39FH | 50079 | Voltage: Phase C | 0-9999 V |  | Int16 | R | 1
C3A0H | 50080 | Voltage: Line-Line Average | 0-9999 V |  | Int16 | R | 1
C3A1H | 50081 | Voltage: Line AB | 0-9999 V |  | Int16 | R | 1
C3A2H | 50082 | Voltage: Line BC | 0-9999 V |  | Int16 | R | 1
C3A3H | 50083 | Voltage: Line CA | 0-9999 V |  | Int16 | R | 1
C3A4H | 50084 | Voltage Scale Factor | -2~4'(used as an exponent of a power of 10) |  | sunssf | R | 1
C3A5H | 50085 | Frequency | 45-65 Hz |  | Int16 | R | 1
C3A6H | 50086 | Frequency Scale Factor | -2'(used as an exponent of a power of 10) |  | sunssf | R | 1
C3A7H | 50087 | Total Real Power | -32768~32767' W |  | Int16 | R | 1
C3A8H | 50088 | Real Power: Phase A Watts | -32768~32767' W |  | Int16 | R | 1
C3A9H | 50089 | Real Power: Phase B Watts | -32768~32767' W |  | Int16 | R | 1
C3AAH | 50090 | Real Power: Phase C Watts | -32768~32767' W |  | Int16 | R | 1
C3ABH | 50091 | Real Power Scale Factor | -1~8'(used as an exponent of a power of 10) |  | sunssf | R | 1
C3ACH | 50092 | Total Apparent Power | 0-32367 VA |  | Int16 | R | 1
C3ADH | 50093 | Apparent Power:Phase A VA | 0-32367 VA |  | Int16 | R | 1
C3AEH | 50094 | Apparent Power: Phase B VA | 0-32367 VA |  | Int16 | R | 1
C3AFH | 50095 | Apparent Power: Phase C VA | 0-32367 VA |  | Int16 | R | 1
C3B0H | 50096 | Apparent Power Scale Factor | -1~8'(used as an exponent of a power of 10) |  | sunssf | R | 1
C3B1H | 50097 | Total Reactive Power | -32768~32767' var |  | Int16 | R | 1
C3B2H | 50098 | Reactive Power: Phase A var | -32768~32767' var |  | Int16 | R | 1
C3B3H | 50099 | Reactive Power: Phase B var | -32768~32767' var |  | Int16 | R | 1
C3B4H | 50100 | Reactive Power: Phase C var | -32768~32767' var |  | Int16 | R | 1
C3B5H | 50101 | Reactive Power Scale Factor | -1~8' (used an exponent of a power of 10) |  | sunssf | R | 1
C3B6H | 50102 | Power Factor | -1000~1000' |  | Int16 | R | 1
C3B7H | 50103 | Power Factor: Phase A PF | -1000~1000' |  | Int16 | R | 1
C3B8H | 50104 | Power Factor: Phase B PF | -1000~1000' |  | Int16 | R | 1
C3B9H | 50105 | Power Factor: Phase C PF | -1000~1000' |  | Int16 | R | 1
C3BAH | 50106 | Power Factor Scale factor | -3'(used as an exponent of a power of 10) |  | sunssf | R | 1
C3BBH-C3BCH | 50107-50108 | Total Real Energy: Export | 0-999999999 Wh |  | Int32 | R/W | 2
C3BDH-C3BEH | 50109-50110 | Export Real Energy: Phase A | 0-999999999 Wh |  | Int32 | R/W | 2
C3BFH-C3C0H | 50111-50112 | Export Real Energy:Phase B | 0-999999999 Wh |  | Int32 | R/W | 2
C3C1H-C3C2H | 50113-50114 | Export Real Energy: Phase C | 0-999999999 Wh |  | Int32 | R/W | 2
C3C3H-C3C4H | 50115-50116 | Total Real Energy:Import | 0-999999999 Wh |  | Int32 | R/W | 2
C3C5H-C3C6H | 50117-50118 | Import Real Energy: Phase A | 0-999999999 Wh |  | Int32 | R/W | 2
C3C7H-C3C8H | 50119-50120 | Import Real Energy:Phase B | 0-999999999 Wh |  | Int32 | R/W | 2
C3C9H-C3CAH | 50121-50122 | Import Real Energy: Phase C | 0-999999999 Wh |  | Int32 | R/W | 2
C3CBH | 50123 | Real Energy Scale Factor | 0,2(used as an exponent of a power of 10) |  | sunssf | R | 1
C3CCH-C3CDH | 50124-50125 | Total Apparent Energy | 0-999999999 VAh |  | Int32 | R/W | 2
C3CEH-C3CFH | 50126-50127 | Apparent Energy: Phase A | 0-999999999 VAh |  | Int32 | R/W | 2
C3D0H-C3D1H | 50128-50129 | Apparent Energy: Phase B | 0-999999999 VAh |  | Int32 | R/W | 2
C3D2H-C3D3H | 50130-50131 | Apparent Energy: Phase C | 0-999999999 VAh |  | Int32 | R/W | 2
C3D4H | 50132 | Apparent Energy Scale Factor | 0,2(used as an exponent of a power of 10) |  | sunssf |  | 1
C3D5H-C3D6H | 50133-50134 | Total Reactive Energy:Export | 0-999999999 varh |  | Int32 | R/W | 2
C3D7H-C3D8H | 50135-50136 | Export Reactive Energy: Phase A | 0-999999999 varh |  | Int32 | R/W | 2
C3D9H-C3DAH | 50137-50138 | Export Reactive Energy:Phase B | 0-999999999 varh |  | Int32 | R/W | 2
C3DBH-C3DCH | 50139-50140 | Export Reactive Energy: Phase C | 0-999999999 varh |  | Int32 | R/W | 2
C3DDH-C3DEH | 50141-50142 | Total Reactive Energy:Import | 0-999999999 varh |  | Int32 | R/W | 2
C3DFH-C3E0H | 50143-50144 | Import Reactive Energy: Phase A | 0-999999999 varh |  | Int32 | R/W | 2
C3E1H-C3E2H | 50145-50146 | Import Reactive Energy: Phase B | 0-999999999 varh |  | Int32 | R/W | 2
C3E3H-C3E4H | 50147-50148 | Import Reactive Energy: Phase C | 0-999999999 varh |  | Int32 | R/W | 2
C3E5H | 50149 | Reactive Power Scale Factor | 0,2(used as an exponent of a power of 10) |  | sunssf | R | 1
C3E6H-C3E7H | 50150-50151 | Meter Event Flags | 0 |  | Binary | R | 2
C3E8H | 50152 | SunSpec_end_ID: Sunspec | FFFF |  | Int16 |  | 1
C3E9H | 50153 | SunSpec_end_ID:Sunspec | 0 |  | Int16 |  | 1

## Class S PQ Event Settings
System Settings: 03H Read, 10H Write
Address(H) | Address(D) | Parameter | Range | Default | Data Type | Access Property
AF65H | 44901 | Class S PQ Event Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF66H | 44902 | Rated Voltage | 10-690V (3LL/2LL) 10-400V (3LN, 1LN) | 400 | Word | R/W
AF67H | 44903 | Rated Current | 0.5-5 (5A) 40.1-1 (mV/mA/RCT) | 5 (5A) 1 (mV/mA/RCT) | Word | R/W
AF68H | 44904 | Sampling Rate | 0: 16 points 1: 32 points 2: 64 points 3: 128 points 4: 256 points 5: 512 points |  | Word | R/W
AF69H | 44905 | Voltage Sag Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF6AH | 44906 | Voltage Sag Threshold | 10-90% | 90 | Word | R/W
AF6BH | 44907 | Voltage Sag Hysteresis | 1-10% |  | Word | R/W
AF6CH | 44908 | Voltage Sag Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF6DH | 44909 | Voltage Sag DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF6EH | 44910 | Voltage Sag RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W
AF6FH | 44911 | Voltage Swell Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF70H | 44912 | Voltage Swell Threshold | 110-150% | 120 | Word | R/W
AF71H | 44913 | Voltage Swell Hysteresis | 1-10% |  | Word | R/W
AF72H | 44914 | Voltage Swell Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF73H | 44915 | Voltage Swell DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF74H | 44916 | Voltage Swell RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W
AF75H | 44917 | Voltage Interrupt Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF76H | 44918 | Voltage Interrupt Threshold | 5-10% | 10 | Word | R/W
AF77H | 44919 | Voltage Interrupt Hysteresis | 1-10% |  | Word | R/W
AF78H | 44920 | Voltage Interrupt Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF79H | 44921 | Voltage Interrupt DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF7AH | 44922 | Voltage Interrupt RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W
AF7BH | 44923 | Unbalance Voltage Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF7CH | 44924 | Unbalance Voltage Threshold | 5-50% | 5 | Word | R/W
AF7DH | 44925 | Unbalance Voltage Hysteresis | 1-10% |  | Word | R/W
AF7EH | 44926 | Unbalance Voltage Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF7FH | 44927 | Unbalance Voltage DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF80H | 44928 | Unbalance Voltage RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W
AF87H | 44935 | Current Swell Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF88H | 44936 | Current Swell Threshold | 110-150% | 110 | Word | R/W
AF89H | 44937 | Current Swell Hysteresis | 1-10% |  | Word | R/W
AF8AH | 44938 | Current Swell Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF8BH | 44939 | Current Swell DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF8CH | 44940 | Current Swell RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W
AF8DH | 44941 | Unbalance Current Enable | 0: Disable 1: Enable | 0 | Word | R/W
AF8EH | 44942 | Unbalance Current Threshold | 5-50% | 5 | Word | R/W
AF8FH | 44943 | Unbalance Current Hysteresis | 1-10% |  | Word | R/W
AF90H | 44944 | Unbalance Current Waveform Trigger | 0: Disable 1: Enable | 0 | Word | R/W
AF91H | 44945 | Unbalance Current DO Enable | 0: No Output 1: DO1 2: DO2 3: DO3 4: DO4 | 0 | Word | R/W
AF92H | 44946 | Unbalance Current RO Enable | 0 No Output Bit0: RO11-1 Bit1: RO11-2 Bit2: RO31-1 Bit3: RO31-2 Bit4: RO12-1 Bit5: RO12-2 Bit6: RO32-1 Bit7: RO32-2 | 0 | Word | R/W

## Class S - 200ms Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship |  | Data Type | Access Property
|  |  | Primary | Secondary
95BBH-95BCH | 38331-38332 | Frequency | F=Rx | F=Rx | Float | R
95BDH-95BEH | 38333-38334 | Phase A Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
95BFH-95C0H | 38335-38336 | Phase B Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
95C1H-95C2H | 38337-38338 | Phase C Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
95C3H-95C4H | 38339-38340 | Line Voltage AB | U=Rx | U=PT1/PT2 | Float | R
95C5H-95C6H | 38341-38342 | Line Voltage BC | U=Rx | U=PT1/PT2 | Float | R
95C7H-95C8H | 38343-38344 | Line Voltage CA | U=Rx | U=PT1/PT2 | Float | R
95C9H-95CAH | 38345-38346 | Average Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
95CBH-95CCH | 38347-38348 | Average Line-Line Voltage | U=Rx | U=PT1/PT2 | Float | R
95CDH-95CEH | 38349-38350 | Phase A Current | I=Rx | I=CT1/CT2 | Float | R
95CFH-95D0H | 38351-38352 | Phase B Current | I=Rx | I=CT1/CT2 | Float | R
95D1H-95D2H | 38353-38354 | Phase C Current | I=Rx | I=CT1/CT2 | Float | R
95D3H-95D4H | 38355-38356 | Neutal Current | I=Rx | I=CT1/CT2 | Float | R
95D5H-95D6H | 38357-38358 | Average Current | I=Rx | I=CT1/CT2 | Float | R
95D7H-95D8H | 38359-38360 | Phase A (AB) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
95D9H-95DAH | 38361-38362 | Phase A (AB) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
95DBH-95DCH | 38363-38364 | Phase A (AB) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
95DDH-95DEH | 38365-38366 | RESERVED |  |  | Float | R
95DFH-95E0H | 38367-38368 | Phase B (BC) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
95E1H-95E2H | 38369-38370 | Phase B (BC) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
95E3H-95E4H | 38371-38372 | Phase B (BC) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
95E5H-95E6H | 38373-38374 | RESERVED |  |  | Float | R
95E7H-95E8H | 38375-38376 | Phase C (CA) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
95E9H-95EAH | 38377-38378 | Phase C (CA) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
95EBH-95ECH | 38379-38380 | Phase C (CA) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
95EDH-95EEH | 38381-38382 | RESERVED |  |  | Float | R
95EFH-95F0H | 38383-38384 | Phase A Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
95F1H-95F2H | 38385-38386 | Phase A Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
95F3H-95F4H | 38387-38388 | Phase A Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
95F5H-95F6H | 38389-38390 | RESERVED |  |  | Float | R
95F7H-95F8H | 38391-38392 | Phase B Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
95F9H-95FAH | 38393-38394 | Phase B Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
95FBH-95FCH | 38395-38396 | Phase B Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
95FDH-95FEH | 38397-38398 | RESERVED |  |  | Float | R
95FFH-9600H | 38399-38400 | Phase C Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
9601H-9602H | 38401-38402 | Phase C Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9603H-9604H | 38403-38404 | Phase C Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9605H-9606H | 38405-38406 | RESERVED |  |  | Float | R
9607H-9608H | 38407-38408 | Voltage Unbalance Factor | Uunb=Rx/100 | Uunb=Rx/100 | Float | R
9609H-960AH | 38409-38410 | Voltage Zero Unbalance Factor | Iunb=Rx/100 | Iunb=Rx/100 | Float | R
960BH-960CH | 38411-38412 | Voltage Zero Sequence (Real) | V=Rx | V=Rx | Float | R
960DH-960EH | 38413-38414 | Voltage Zero Sequence (Imaginary) | V=Rx | V=Rx | Float | R
960FH-9610H | 38415-38416 | Voltage Positive Sequence (Real) | V=Rx | V=Rx | Float | R
9611H-9612H | 38417-38418 | Voltage Positive Sequence (Imaginary) | V=Rx | V=Rx | Float | R
9613H-9614H | 38419-38420 | Voltage Negative Sequence (Real) | V=Rx | V=Rx | Float | R
9615H-9616H | 38421-38422 | Voltage Negative Sequence (Imaginary) | V=Rx | V=Rx | Float | R
9617H-9618H | 38423-38424 | Current Unbalance Factor | I=Rx | I=Rx | Float | R
9619H-961AH | 38425-38426 | Current Zero Unbalance Factor | I=Rx | I=Rx | Float | R
961BH-961CH | 38427-38428 | Current Zero Sequence (Real) | I=Rx | I=Rx | Float | R
961DH-961EH | 38429-38430 | Current Zero Sequence (Imaginary) | I=Rx | I=Rx | Float | R
961FH-9620H | 38431-38432 | Current Positive Sequence (Real) | I=Rx | I=Rx | Float | R
9621H-9622H | 38433-38434 | Current Positive Sequence (Imaginary) | I=Rx | I=Rx | Float | R
9623H-9624H | 38435-38436 | Current Negative Sequence (Real) | I=Rx | I=Rx | Float | R
9625H-9626H | 38437-38438 | Current Negative Sequence (Imaginary) | I=Rx | I=Rx | Float | R

## 200ms Harmonic Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Data Type | Access Property
V1(V12)
980CH | 38924 | V1(V12) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
980DH | 38925 | V1(V12) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
980EH | 38926 | V1(V12) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
980FH | 38927 | V1(V12) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9810H | 38928 | V1(V12) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9811H | 38929 | V1(V12) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9812H | 38930 | V1(V12) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9813H | 38931 | V1(V12) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9814H | 38932 | V1(V12) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9815H | 38933 | V1(V12) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9816H | 38934 | V1(V12) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9817H | 38935 | V1(V12) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9818H | 38936 | V1(V12) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9819H | 38937 | V1(V12) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
981AH | 38938 | V1(V12) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
981BH | 38939 | V1(V12) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
981CH | 38940 | V1(V12) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
981DH | 38941 | V1(V12) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
981EH | 38942 | V1(V12) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
981FH | 38943 | V1(V12) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9820H | 38944 | V1(V12) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9821H | 38945 | V1(V12) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9822H | 38946 | V1(V12) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9823H | 38947 | V1(V12) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9824H | 38948 | V1(V12) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9825H | 38949 | V1(V12) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9826H | 38950 | V1(V12) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9827H | 38951 | V1(V12) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9828H | 38952 | V1(V12) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9829H | 38953 | V1(V12) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
982AH | 38954 | V1(V12) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
982BH | 38955 | V1(V12) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
982CH | 38956 | V1(V12) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
982DH | 38957 | V1(V12) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
982EH | 38958 | V1(V12) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
982FH | 38959 | V1(V12) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9830H | 38960 | V1(V12) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9831H | 38961 | V1(V12) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9832H | 38962 | V1(V12) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9833H | 38963 | V1(V12) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9834H | 38964 | V1(V12) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9835H | 38965 | V1(V12) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9836H | 38966 | V1(V12) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9837H | 38967 | V1(V12) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9838H | 38968 | V1(V12) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9839H | 38969 | V1(V12) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
983AH | 38970 | V1(V12) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
983BH | 38971 | V1(V12) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
983CH | 38972 | V1(V12) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
983DH | 38973 | V1(V12) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
983EH | 38974 | V1(V12) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
983FH | 38975 | V1(V12) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9840H | 38976 | V1(V12) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9841H | 38977 | V1(V12) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9842H | 38978 | V1(V12) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9843H | 38979 | V1(V12) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9844H | 38980 | V1(V12) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9845H | 38981 | V1(V12) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9846H | 38982 | V1(V12) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9847H | 38983 | V1(V12) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9848H | 38984 | V1(V12) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9849H | 38985 | V1(V12) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
984AH | 38986 | V1(V12) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
984BH | 38987 | RESERVED |  | Word | R
984CH-984DH | 38988-38989 | V1(V12) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
984EH-984FH | 38990-38991 | V1(V12) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9850H-9851H | 38992-38993 | V1(V12) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9852H-9853H | 38994-38995 | V1(V12) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9854H-9855H | 38996-38997 | V1(V12) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9856H-9857H | 38998-38999 | V1(V12) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9858H-9859H | 39000-39001 | V1(V12) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
985AH-985BH | 39002-39003 | V1(V12) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
985CH-985DH | 39004-39005 | V1(V12) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
985EH-985FH | 39006-39007 | V1(V12) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9860H-9861H | 39008-39009 | V1(V12) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9862H-9863H | 39010-39011 | V1(V12) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9864H-9865H | 39012-39013 | V1(V12) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9866H-9867H | 39014-39015 | V1(V12) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9868H-9869H | 39016-39017 | V1(V12) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
986AH-986BH | 39018-39019 | V1(V12) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
986CH-986DH | 39020-39021 | V1(V12) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
986EH-986FH | 39022-39023 | V1(V12) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9870H-9871H | 39024-39025 | V1(V12) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9872H-9873H | 39026-39027 | V1(V12) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9874H-9875H | 39028-39029 | V1(V12) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9876H-9877H | 39030-39031 | V1(V12) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9878H-9879H | 39032-39033 | V1(V12) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
987AH-987BH | 39034-39035 | V1(V12) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
987CH-987DH | 39036-39037 | V1(V12) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
987EH-987FH | 39038-39039 | V1(V12) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9880H-9881H | 39040-39041 | V1(V12) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9882H-9883H | 39042-39043 | V1(V12) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9884H-9885H | 39044-39045 | V1(V12) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9886H-9887H | 39046-39047 | V1(V12) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9888H-9889H | 39048-39049 | V1(V12) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
988AH-988BH | 39050-39051 | V1(V12) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
988CH-988DH | 39052-39053 | V1(V12) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
988EH-988FH | 39054-39055 | V1(V12) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9890H-9891H | 39056-39057 | V1(V12) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9892H-9893H | 39058-39059 | V1(V12) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9894H-9895H | 39060-39061 | V1(V12) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9896H-9897H | 39062-39063 | V1(V12) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9898H-9899H | 39064-39065 | V1(V12) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
989AH-989BH | 39066-39067 | V1(V12) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
989CH-989DH | 39068-39069 | V1(V12) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
989EH-989FH | 39070-39071 | V1(V12) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
98A0H-98A1H | 39072-39073 | V1(V12) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
98A2H-98A3H | 39074-39075 | V1(V12) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
98A4H-98A5H | 39076-39077 | V1(V12) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
98A6H-98A7H | 39078-39079 | V1(V12) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
98A8H-98A9H | 39080-39081 | V1(V12) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
98AAH-98ABH | 39082-39083 | V1(V12) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
98ACH-98ADH | 39084-39085 | V1(V12) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
98AEH-98AFH | 39086-39087 | V1(V12) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
98B0H-98B1H | 39088-39089 | V1(V12) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
98B2H-98B3H | 39090-39091 | V1(V12) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
98B4H-98B5H | 39092-39093 | V1(V12) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
98B6H-98B7H | 39094-39095 | V1(V12) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
98B8H-98B9H | 39096-39097 | V1(V12) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
98BAH-98BBH | 39098-39099 | V1(V12) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
98BCH-98BDH | 39100-39101 | V1(V12) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
98BEH-98BFH | 39102-39103 | V1(V12) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
98C0H-98C1H | 39104-39105 | V1(V12) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
98C2H-98C3H | 39106-39107 | V1(V12) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
98C4H-98C5H | 39108-39109 | V1(V12) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
98C6H-98C7H | 39110-39111 | V1(V12) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
98C8H-98C9H | 39112-39113 | V1(V12) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V2(V23)
98CAH | 39114 | V2(V23) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
98CBH | 39115 | V2(V23) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
98CCH | 39116 | V2(V23) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
98CDH | 39117 | V2(V23) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
98CEH | 39118 | V2(V23) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
98CFH | 39119 | V2(V23) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D0H | 39120 | V2(V23) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D1H | 39121 | V2(V23) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D2H | 39122 | V2(V23) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D3H | 39123 | V2(V23) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D4H | 39124 | V2(V23) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D5H | 39125 | V2(V23) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D6H | 39126 | V2(V23) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D7H | 39127 | V2(V23) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D8H | 39128 | V2(V23) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
98D9H | 39129 | V2(V23) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
98DAH | 39130 | V2(V23) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
98DBH | 39131 | V2(V23) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
98DCH | 39132 | V2(V23) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
98DDH | 39133 | V2(V23) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
98DEH | 39134 | V2(V23) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
98DFH | 39135 | V2(V23) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
98E0H | 39136 | V2(V23) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
98E1H | 39137 | V2(V23) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E2H | 39138 | V2(V23) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E3H | 39139 | V2(V23) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E4H | 39140 | V2(V23) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E5H | 39141 | V2(V23) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E6H | 39142 | V2(V23) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E7H | 39143 | V2(V23) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
98E8H | 39144 | V2(V23) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
98E9H | 39145 | V2(V23) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
98EAH | 39146 | V2(V23) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
98EBH | 39147 | V2(V23) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
98ECH | 39148 | V2(V23) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
98EDH | 39149 | V2(V23) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
98EEH | 39150 | V2(V23) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
98EFH | 39151 | V2(V23) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F0H | 39152 | V2(V23) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F1H | 39153 | V2(V23) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F2H | 39154 | V2(V23) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
98F3H | 39155 | V2(V23) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
98F4H | 39156 | V2(V23) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
98F5H | 39157 | V2(V23) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F6H | 39158 | V2(V23) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F7H | 39159 | V2(V23) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F8H | 39160 | V2(V23) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
98F9H | 39161 | V2(V23) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
98FAH | 39162 | V2(V23) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
98FBH | 39163 | V2(V23) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
98FCH | 39164 | V2(V23) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
98FDH | 39165 | V2(V23) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
98FEH | 39166 | V2(V23) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
98FFH | 39167 | V2(V23) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9900H | 39168 | V2(V23) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9901H | 39169 | V2(V23) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9902H | 39170 | V2(V23) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9903H | 39171 | V2(V23) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9904H | 39172 | V2(V23) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9905H | 39173 | V2(V23) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9906H | 39174 | V2(V23) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9907H | 39175 | V2(V23) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9908H | 39176 | V2(V23) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9909H | 39177 | RESERVED |  | Word | R
990AH-990BH | 39178-39179 | V2(V23) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
990CH-990DH | 39180-39181 | V2(V23) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
990EH-990FH | 39182-39183 | V2(V23) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9910H-9911H | 39184-39185 | V2(V23) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9912H-9913H | 39186-39187 | V2(V23) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9914H-9915H | 39188-39189 | V2(V23) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9916H-9917H | 39190-39191 | V2(V23) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9918H-9919H | 39192-39193 | V2(V23) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
991AH-991BH | 39194-39195 | V2(V23) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
991CH-991DH | 39196-39197 | V2(V23) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
991EH-991FH | 39198-39199 | V2(V23) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9920H-9921H | 39200-39201 | V2(V23) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9922H-9923H | 39202-39203 | V2(V23) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9924H-9925H | 39204-39205 | V2(V23) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9926H-9927H | 39206-39207 | V2(V23) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9928H-9929H | 39208-39209 | V2(V23) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
992AH-992BH | 39210-39211 | V2(V23) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
992CH-992DH | 39212-39213 | V2(V23) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
992EH-992FH | 39214-39215 | V2(V23) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9930H-9931H | 39216-39217 | V2(V23) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9932H-9933H | 39218-39219 | V2(V23) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9934H-9935H | 39220-39221 | V2(V23) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9936H-9937H | 39222-39223 | V2(V23) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9938H-9939H | 39224-39225 | V2(V23) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
993AH-993BH | 39226-39227 | V2(V23) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
993CH-993DH | 39228-39229 | V2(V23) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
993EH-993FH | 39230-39231 | V2(V23) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9940H-9941H | 39232-39233 | V2(V23) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9942H-9943H | 39234-39235 | V2(V23) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9944H-9945H | 39236-39237 | V2(V23) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9946H-9947H | 39238-39239 | V2(V23) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9948H-9949H | 39240-39241 | V2(V23) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
994AH-994BH | 39242-39243 | V2(V23) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
994CH-994DH | 39244-39245 | V2(V23) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
994EH-994FH | 39246-39247 | V2(V23) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9950H-9951H | 39248-39249 | V2(V23) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9952H-9953H | 39250-39251 | V2(V23) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9954H-9955H | 39252-39253 | V2(V23) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9956H-9957H | 39254-39255 | V2(V23) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9958H-9959H | 39256-39257 | V2(V23) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
995AH-995BH | 39258-39259 | V2(V23) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
995CH-995DH | 39260-39261 | V2(V23) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
995EH-995FH | 39262-39263 | V2(V23) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9960H-9961H | 39264-39265 | V2(V23) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9962H-9963H | 39266-39267 | V2(V23) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9964H-9965H | 39268-39269 | V2(V23) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9966H-9967H | 39270-39271 | V2(V23) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9968H-9969H | 39272-39273 | V2(V23) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
996AH-996BH | 39274-39275 | V2(V23) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
996CH-996DH | 39276-39277 | V2(V23) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
996EH-996FH | 39278-39279 | V2(V23) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9970H-9971H | 39280-39281 | V2(V23) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9972H-9973H | 39282-39283 | V2(V23) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9974H-9975H | 39284-39285 | V2(V23) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9976H-9977H | 39286-39287 | V2(V23) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9978H-9979H | 39288-39289 | V2(V23) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
997AH-997BH | 39290-39291 | V2(V23) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
997CH-997DH | 39292-39293 | V2(V23) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
997EH-997FH | 39294-39295 | V2(V23) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9980H-9981H | 39296-39297 | V2(V23) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9982H-9983H | 39298-39299 | V2(V23) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9984H-9985H | 39300-39301 | V2(V23) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9986H-9987H | 39302-39303 | V2(V23) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V3(V31)
9988H | 39304 | V3(V31) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9989H | 39305 | V3(V31) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
998AH | 39306 | V3(V31) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
998BH | 39307 | V3(V31) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
998CH | 39308 | V3(V31) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
998DH | 39309 | V3(V31) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
998EH | 39310 | V3(V31) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
998FH | 39311 | V3(V31) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9990H | 39312 | V3(V31) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9991H | 39313 | V3(V31) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9992H | 39314 | V3(V31) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9993H | 39315 | V3(V31) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9994H | 39316 | V3(V31) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9995H | 39317 | V3(V31) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9996H | 39318 | V3(V31) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9997H | 39319 | V3(V31) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9998H | 39320 | V3(V31) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9999H | 39321 | V3(V31) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
999AH | 39322 | V3(V31) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
999BH | 39323 | V3(V31) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
999CH | 39324 | V3(V31) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
999DH | 39325 | V3(V31) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
999EH | 39326 | V3(V31) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
999FH | 39327 | V3(V31) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A0H | 39328 | V3(V31) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A1H | 39329 | V3(V31) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A2H | 39330 | V3(V31) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A3H | 39331 | V3(V31) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A4H | 39332 | V3(V31) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A5H | 39333 | V3(V31) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
99A6H | 39334 | V3(V31) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
99A7H | 39335 | V3(V31) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
99A8H | 39336 | V3(V31) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
99A9H | 39337 | V3(V31) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
99AAH | 39338 | V3(V31) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
99ABH | 39339 | V3(V31) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
99ACH | 39340 | V3(V31) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
99ADH | 39341 | V3(V31) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
99AEH | 39342 | V3(V31) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
99AFH | 39343 | V3(V31) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B0H | 39344 | V3(V31) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
99B1H | 39345 | V3(V31) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
99B2H | 39346 | V3(V31) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
99B3H | 39347 | V3(V31) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B4H | 39348 | V3(V31) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B5H | 39349 | V3(V31) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B6H | 39350 | V3(V31) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B7H | 39351 | V3(V31) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B8H | 39352 | V3(V31) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
99B9H | 39353 | V3(V31) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
99BAH | 39354 | V3(V31) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
99BBH | 39355 | V3(V31) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
99BCH | 39356 | V3(V31) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
99BDH | 39357 | V3(V31) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
99BEH | 39358 | V3(V31) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
99BFH | 39359 | V3(V31) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
99C0H | 39360 | V3(V31) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
99C1H | 39361 | V3(V31) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
99C2H | 39362 | V3(V31) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
99C3H | 39363 | V3(V31) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
99C4H | 39364 | V3(V31) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
99C5H | 39365 | V3(V31) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
99C6H | 39366 | V3(V31) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
99C7H | 39367 | RESERVED |  | Word | R
99C8H-99C9H | 39368-39369 | V3(V31) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
99CAH-99CBH | 39370-39371 | V3(V31) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
99CCH-99CDH | 39372-39373 | V3(V31) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
99CEH-99CFH | 39374-39375 | V3(V31) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
99D0H-99D1H | 39376-39377 | V3(V31) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
99D2H-99D3H | 39378-39379 | V3(V31) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
99D4H-99D5H | 39380-39381 | V3(V31) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
99D6H-99D7H | 39382-39383 | V3(V31) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
99D8H-99D9H | 39384-39385 | V3(V31) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
99DAH-99DBH | 39386-39387 | V3(V31) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
99DCH-99DDH | 39388-39389 | V3(V31) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
99DEH-99DFH | 39390-39391 | V3(V31) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
99E0H-99E1H | 39392-39393 | V3(V31) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
99E2H-99E3H | 39394-39395 | V3(V31) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
99E4H-99E5H | 39396-39397 | V3(V31) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
99E6H-99E7H | 39398-39399 | V3(V31) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
99E8H-99E9H | 39400-39401 | V3(V31) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
99EAH-99EBH | 39402-39403 | V3(V31) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
99ECH-99EDH | 39404-39405 | V3(V31) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
99EEH-99EFH | 39406-39407 | V3(V31) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
99F0H-99F1H | 39408-39409 | V3(V31) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
99F2H-99F3H | 39410-39411 | V3(V31) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
99F4H-99F5H | 39412-39413 | V3(V31) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
99F6H-99F7H | 39414-39415 | V3(V31) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
99F8H-99F9H | 39416-39417 | V3(V31) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
99FAH-99FBH | 39418-39419 | V3(V31) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
99FCH-99FDH | 39420-39421 | V3(V31) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
99FEH-99FFH | 39422-39423 | V3(V31) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9A00H-9A01H | 39424-39425 | V3(V31) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9A02H-9A03H | 39426-39427 | V3(V31) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9A04H-9A05H | 39428-39429 | V3(V31) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9A06H-9A07H | 39430-39431 | V3(V31) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9A08H-9A09H | 39432-39433 | V3(V31) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9A0AH-9A0BH | 39434-39435 | V3(V31) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9A0CH-9A0DH | 39436-39437 | V3(V31) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9A0EH-9A0FH | 39438-39439 | V3(V31) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9A10H-9A11H | 39440-39441 | V3(V31) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9A12H-9A13H | 39442-39443 | V3(V31) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9A14H-9A15H | 39444-39445 | V3(V31) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9A16H-9A17H | 39446-39447 | V3(V31) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9A18H-9A19H | 39448-39449 | V3(V31) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9A1AH-9A1BH | 39450-39451 | V3(V31) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9A1CH-9A1DH | 39452-39453 | V3(V31) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9A1EH-9A1FH | 39454-39455 | V3(V31) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9A20H-9A21H | 39456-39457 | V3(V31) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9A22H-9A23H | 39458-39459 | V3(V31) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9A24H-9A25H | 39460-39461 | V3(V31) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9A26H-9A27H | 39462-39463 | V3(V31) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9A28H-9A29H | 39464-39465 | V3(V31) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9A2AH-9A2BH | 39466-39467 | V3(V31) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9A2CH-9A2DH | 39468-39469 | V3(V31) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9A2EH-9A2FH | 39470-39471 | V3(V31) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9A30H-9A31H | 39472-39473 | V3(V31) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9A32H-9A33H | 39474-39475 | V3(V31) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9A34H-9A35H | 39476-39477 | V3(V31) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9A36H-9A37H | 39478-39479 | V3(V31) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9A38H-9A39H | 39480-39481 | V3(V31) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9A3AH-9A3BH | 39482-39483 | V3(V31) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9A3CH-9A3DH | 39484-39485 | V3(V31) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9A3EH-9A3FH | 39486-39487 | V3(V31) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9A40H-9A41H | 39488-39489 | V3(V31) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9A42H-9A43H | 39490-39491 | V3(V31) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9A44H-9A45H | 39492-39493 | V3(V31) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase A Current
9A46H | 39494 | I1 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A47H | 39495 | I1 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A48H | 39496 | I1 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A49H | 39497 | I1 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4AH | 39498 | I1 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4BH | 39499 | I1 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4CH | 39500 | I1 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4DH | 39501 | I1 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4EH | 39502 | I1 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A4FH | 39503 | I1 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A50H | 39504 | I1 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A51H | 39505 | I1 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A52H | 39506 | I1 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A53H | 39507 | I1 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A54H | 39508 | I1 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A55H | 39509 | I1 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A56H | 39510 | I1 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A57H | 39511 | I1 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A58H | 39512 | I1 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A59H | 39513 | I1 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5AH | 39514 | I1 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5BH | 39515 | I1 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5CH | 39516 | I1 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5DH | 39517 | I1 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5EH | 39518 | I1 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A5FH | 39519 | I1 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A60H | 39520 | I1 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A61H | 39521 | I1 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A62H | 39522 | I1 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A63H | 39523 | I1 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A64H | 39524 | I1 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A65H | 39525 | I1 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A66H | 39526 | I1 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A67H | 39527 | I1 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A68H | 39528 | I1 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A69H | 39529 | I1 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6AH | 39530 | I1 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6BH | 39531 | I1 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6CH | 39532 | I1 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6DH | 39533 | I1 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6EH | 39534 | I1 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A6FH | 39535 | I1 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A70H | 39536 | I1 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A71H | 39537 | I1 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A72H | 39538 | I1 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A73H | 39539 | I1 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A74H | 39540 | I1 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A75H | 39541 | I1 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A76H | 39542 | I1 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A77H | 39543 | I1 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A78H | 39544 | I1 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A79H | 39545 | I1 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7AH | 39546 | I1 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7BH | 39547 | I1 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7CH | 39548 | I1 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7DH | 39549 | I1 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7EH | 39550 | I1 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A7FH | 39551 | I1 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A80H | 39552 | I1 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A81H | 39553 | I1 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9A82H | 39554 | I1 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9A83H | 39555 | I1 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A84H | 39556 | I1 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9A85H | 39557 | RESERVED |  | Word | R
9A86H-9A87H | 39558-39559 | I1 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9A88H-9A89H | 39560-39561 | I1 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9A8AH-9A8BH | 39562-39563 | I1 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9A8CH-9A8DH | 39564-39565 | I1 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9A8EH-9A8FH | 39566-39567 | I1 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9A90H-9A91H | 39568-39569 | I1 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9A92H-9A93H | 39570-39571 | I1 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9A94H-9A95H | 39572-39573 | I1 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9A96H-9A97H | 39574-39575 | I1 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9A98H-9A99H | 39576-39577 | I1 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9A9AH-9A9BH | 39578-39579 | I1 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9A9CH-9A9DH | 39580-39581 | I1 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9A9EH-9A9FH | 39582-39583 | I1 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9AA0H-9AA1H | 39584-39585 | I1 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9AA2H-9AA3H | 39586-39587 | I1 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9AA4H-9AA5H | 39588-39589 | I1 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9AA6H-9AA7H | 39590-39591 | I1 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9AA8H-9AA9H | 39592-39593 | I1 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9AAAH-9AABH | 39594-39595 | I1 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9AACH-9AADH | 39596-39597 | I1 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9AAEH-9AAFH | 39598-39599 | I1 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9AB0H-9AB1H | 39600-39601 | I1 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9AB2H-9AB3H | 39602-39603 | I1 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9AB4H-9AB5H | 39604-39605 | I1 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9AB6H-9AB7H | 39606-39607 | I1 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9AB8H-9AB9H | 39608-39609 | I1 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9ABAH-9ABBH | 39610-39611 | I1 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9ABCH-9ABDH | 39612-39613 | I1 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9ABEH-9ABFH | 39614-39615 | I1 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9AC0H-9AC1H | 39616-39617 | I1 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9AC2H-9AC3H | 39618-39619 | I1 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9AC4H-9AC5H | 39620-39621 | I1 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9AC6H-9AC7H | 39622-39623 | I1 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9AC8H-9AC9H | 39624-39625 | I1 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9ACAH-9ACBH | 39626-39627 | I1 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9ACCH-9ACDH | 39628-39629 | I1 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9ACEH-9ACFH | 39630-39631 | I1 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9AD0H-9AD1H | 39632-39633 | I1 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9AD2H-9AD3H | 39634-39635 | I1 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9AD4H-9AD5H | 39636-39637 | I1 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9AD6H-9AD7H | 39638-39639 | I1 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9AD8H-9AD9H | 39640-39641 | I1 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9ADAH-9ADBH | 39642-39643 | I1 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9ADCH-9ADDH | 39644-39645 | I1 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9ADEH-9ADFH | 39646-39647 | I1 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9AE0H-9AE1H | 39648-39649 | I1 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9AE2H-9AE3H | 39650-39651 | I1 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9AE4H-9AE5H | 39652-39653 | I1 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9AE6H-9AE7H | 39654-39655 | I1 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9AE8H-9AE9H | 39656-39657 | I1 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9AEAH-9AEBH | 39658-39659 | I1 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9AECH-9AEDH | 39660-39661 | I1 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9AEEH-9AEFH | 39662-39663 | I1 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9AF0H-9AF1H | 39664-39665 | I1 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9AF2H-9AF3H | 39666-39667 | I1 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9AF4H-9AF5H | 39668-39669 | I1 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9AF6H-9AF7H | 39670-39671 | I1 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9AF8H-9AF9H | 39672-39673 | I1 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9AFAH-9AFBH | 39674-39675 | I1 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9AFCH-9AFDH | 39676-39677 | I1 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9AFEH-9AFFH | 39678-39679 | I1 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9B00H-9B01H | 39680-39681 | I1 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9B02H-9B03H | 39682-39683 | I1 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase B Current
9B04H | 39684 | I2 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B05H | 39685 | I2 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B06H | 39686 | I2 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B07H | 39687 | I2 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B08H | 39688 | I2 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B09H | 39689 | I2 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0AH | 39690 | I2 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0BH | 39691 | I2 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0CH | 39692 | I2 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0DH | 39693 | I2 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0EH | 39694 | I2 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B0FH | 39695 | I2 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B10H | 39696 | I2 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B11H | 39697 | I2 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B12H | 39698 | I2 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B13H | 39699 | I2 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B14H | 39700 | I2 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B15H | 39701 | I2 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B16H | 39702 | I2 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B17H | 39703 | I2 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B18H | 39704 | I2 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B19H | 39705 | I2 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1AH | 39706 | I2 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1BH | 39707 | I2 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1CH | 39708 | I2 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1DH | 39709 | I2 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1EH | 39710 | I2 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B1FH | 39711 | I2 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B20H | 39712 | I2 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B21H | 39713 | I2 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B22H | 39714 | I2 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B23H | 39715 | I2 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B24H | 39716 | I2 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B25H | 39717 | I2 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B26H | 39718 | I2 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B27H | 39719 | I2 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B28H | 39720 | I2 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B29H | 39721 | I2 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2AH | 39722 | I2 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2BH | 39723 | I2 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2CH | 39724 | I2 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2DH | 39725 | I2 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2EH | 39726 | I2 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B2FH | 39727 | I2 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B30H | 39728 | I2 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B31H | 39729 | I2 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B32H | 39730 | I2 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B33H | 39731 | I2 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B34H | 39732 | I2 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B35H | 39733 | I2 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B36H | 39734 | I2 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B37H | 39735 | I2 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B38H | 39736 | I2 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B39H | 39737 | I2 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3AH | 39738 | I2 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3BH | 39739 | I2 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3CH | 39740 | I2 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3DH | 39741 | I2 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3EH | 39742 | I2 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B3FH | 39743 | I2 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9B40H | 39744 | I2 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9B41H | 39745 | I2 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B42H | 39746 | I2 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9B43H | 39747 | RESERVED |  | Word | R
9B44H-9B45H | 39748-39749 | I2 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9B46H-9B47H | 39750-39751 | I2 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9B48H-9B49H | 39752-39753 | I2 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9B4AH-9B4BH | 39754-39755 | I2 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9B4CH-9B4DH | 39756-39757 | I2 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9B4EH-9B4FH | 39758-39759 | I2 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9B50H-9B51H | 39760-39761 | I2 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9B52H-9B53H | 39762-39763 | I2 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9B54H-9B55H | 39764-39765 | I2 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9B56H-9B57H | 39766-39767 | I2 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9B58H-9B59H | 39768-39769 | I2 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9B5AH-9B5BH | 39770-39771 | I2 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9B5CH-9B5DH | 39772-39773 | I2 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9B5EH-9B5FH | 39774-39775 | I2 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9B60H-9B61H | 39776-39777 | I2 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9B62H-9B63H | 39778-39779 | I2 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9B64H-9B65H | 39780-39781 | I2 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9B66H-9B67H | 39782-39783 | I2 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9B68H-9B69H | 39784-39785 | I2 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9B6AH-9B6BH | 39786-39787 | I2 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9B6CH-9B6DH | 39788-39789 | I2 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9B6EH-9B6FH | 39790-39791 | I2 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9B70H-9B71H | 39792-39793 | I2 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9B72H-9B73H | 39794-39795 | I2 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9B74H-9B75H | 39796-39797 | I2 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9B76H-9B77H | 39798-39799 | I2 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9B78H-9B79H | 39800-39801 | I2 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9B7AH-9B7BH | 39802-39803 | I2 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9B7CH-9B7DH | 39804-39805 | I2 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9B7EH-9B7FH | 39806-39807 | I2 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9B80H-9B81H | 39808-39809 | I2 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9B82H-9B83H | 39810-39811 | I2 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9B84H-9B85H | 39812-39813 | I2 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9B86H-9B87H | 39814-39815 | I2 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9B88H-9B89H | 39816-39817 | I2 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9B8AH-9B8BH | 39818-39819 | I2 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9B8CH-9B8DH | 39820-39821 | I2 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9B8EH-9B8FH | 39822-39823 | I2 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9B90H-9B91H | 39824-39825 | I2 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9B92H-9B93H | 39826-39827 | I2 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9B94H-9B95H | 39828-39829 | I2 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9B96H-9B97H | 39830-39831 | I2 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9B98H-9B99H | 39832-39833 | I2 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9B9AH-9B9BH | 39834-39835 | I2 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9B9CH-9B9DH | 39836-39837 | I2 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9B9EH-9B9FH | 39838-39839 | I2 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9BA0H-9BA1H | 39840-39841 | I2 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9BA2H-9BA3H | 39842-39843 | I2 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9BA4H-9BA5H | 39844-39845 | I2 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9BA6H-9BA7H | 39846-39847 | I2 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9BA8H-9BA9H | 39848-39849 | I2 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9BAAH-9BABH | 39850-39851 | I2 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9BACH-9BADH | 39852-39853 | I2 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9BAEH-9BAFH | 39854-39855 | I2 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9BB0H-9BB1H | 39856-39857 | I2 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9BB2H-9BB3H | 39858-39859 | I2 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9BB4H-9BB5H | 39860-39861 | I2 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9BB6H-9BB7H | 39862-39863 | I2 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9BB8H-9BB9H | 39864-39865 | I2 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9BBAH-9BBBH | 39866-39867 | I2 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9BBCH-9BBDH | 39868-39869 | I2 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9BBEH-9BBFH | 39870-39871 | I2 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9BC0H-9BC1H | 39872-39873 | I2 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase C Current
9BC2H | 39874 | I3 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC3H | 39875 | I3 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC4H | 39876 | I3 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC5H | 39877 | I3 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC6H | 39878 | I3 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC7H | 39879 | I3 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC8H | 39880 | I3 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BC9H | 39881 | I3 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCAH | 39882 | I3 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCBH | 39883 | I3 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCCH | 39884 | I3 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCDH | 39885 | I3 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCEH | 39886 | I3 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BCFH | 39887 | I3 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD0H | 39888 | I3 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD1H | 39889 | I3 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD2H | 39890 | I3 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD3H | 39891 | I3 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD4H | 39892 | I3 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD5H | 39893 | I3 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD6H | 39894 | I3 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD7H | 39895 | I3 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD8H | 39896 | I3 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BD9H | 39897 | I3 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDAH | 39898 | I3 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDBH | 39899 | I3 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDCH | 39900 | I3 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDDH | 39901 | I3 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDEH | 39902 | I3 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BDFH | 39903 | I3 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE0H | 39904 | I3 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE1H | 39905 | I3 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE2H | 39906 | I3 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE3H | 39907 | I3 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE4H | 39908 | I3 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE5H | 39909 | I3 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE6H | 39910 | I3 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE7H | 39911 | I3 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE8H | 39912 | I3 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BE9H | 39913 | I3 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BEAH | 39914 | I3 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BEBH | 39915 | I3 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BECH | 39916 | I3 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BEDH | 39917 | I3 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BEEH | 39918 | I3 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BEFH | 39919 | I3 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF0H | 39920 | I3 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF1H | 39921 | I3 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF2H | 39922 | I3 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF3H | 39923 | I3 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF4H | 39924 | I3 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF5H | 39925 | I3 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF6H | 39926 | I3 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF7H | 39927 | I3 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF8H | 39928 | I3 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BF9H | 39929 | I3 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFAH | 39930 | I3 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFBH | 39931 | I3 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFCH | 39932 | I3 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFDH | 39933 | I3 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFEH | 39934 | I3 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9BFFH | 39935 | I3 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C00H | 39936 | I3 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C01H | 39937 | RESERVED |  | Word | R
9C02H-9C03H | 39938-39939 | I3 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9C04H-9C05H | 39940-39941 | I3 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C06H-9C07H | 39942-39943 | I3 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9C08H-9C09H | 39944-39945 | I3 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9C0AH-9C0BH | 39946-39947 | I3 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9C0CH-9C0DH | 39948-39949 | I3 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9C0EH-9C0FH | 39950-39951 | I3 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9C10H-9C11H | 39952-39953 | I3 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9C12H-9C13H | 39954-39955 | I3 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9C14H-9C15H | 39956-39957 | I3 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9C16H-9C17H | 39958-39959 | I3 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9C18H-9C19H | 39960-39961 | I3 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9C1AH-9C1BH | 39962-39963 | I3 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9C1CH-9C1DH | 39964-39965 | I3 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9C1EH-9C1FH | 39966-39967 | I3 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9C20H-9C21H | 39968-39969 | I3 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9C22H-9C23H | 39970-39971 | I3 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9C24H-9C25H | 39972-39973 | I3 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9C26H-9C27H | 39974-39975 | I3 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9C28H-9C29H | 39976-39977 | I3 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9C2AH-9C2BH | 39978-39979 | I3 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9C2CH-9C2DH | 39980-39981 | I3 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C2EH-9C2FH | 39982-39983 | I3 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9C30H-9C31H | 39984-39985 | I3 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9C32H-9C33H | 39986-39987 | I3 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9C34H-9C35H | 39988-39989 | I3 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9C36H-9C37H | 39990-39991 | I3 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9C38H-9C39H | 39992-39993 | I3 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9C3AH-9C3BH | 39994-39995 | I3 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9C3CH-9C3DH | 39996-39997 | I3 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9C3EH-9C3FH | 39998-39999 | I3 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9C40H-9C41H | 40000-40001 | I3 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C42H-9C43H | 40002-40003 | I3 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9C44H-9C45H | 40004-40005 | I3 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9C46H-9C47H | 40006-40007 | I3 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9C48H-9C49H | 40008-40009 | I3 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9C4AH-9C4BH | 40010-40011 | I3 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9C4CH-9C4DH | 40012-40013 | I3 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9C4EH-9C4FH | 40014-40015 | I3 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9C50H-9C51H | 40016-40017 | I3 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9C52H-9C53H | 40018-40019 | I3 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9C54H-9C55H | 40020-40021 | I3 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C56H-9C57H | 40022-40023 | I3 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9C58H-9C59H | 40024-40025 | I3 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9C5AH-9C5BH | 40026-40027 | I3 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9C5CH-9C5DH | 40028-40029 | I3 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9C5EH-9C5FH | 40030-40031 | I3 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9C60H-9C61H | 40032-40033 | I3 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9C62H-9C63H | 40034-40035 | I3 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9C64H-9C65H | 40036-40037 | I3 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9C66H-9C67H | 40038-40039 | I3 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9C68H-9C69H | 40040-40041 | I3 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C6AH-9C6BH | 40042-40043 | I3 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9C6CH-9C6DH | 40044-40045 | I3 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9C6EH-9C6FH | 40046-40047 | I3 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9C70H-9C71H | 40048-40049 | I3 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9C72H-9C73H | 40050-40051 | I3 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9C74H-9C75H | 40052-40053 | I3 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9C76H-9C77H | 40054-40055 | I3 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9C78H-9C79H | 40056-40057 | I3 60th Harmonic Amplitude | THD= Rx/100 | Float | R
97CAH-9C7BH | 38858-40059 | I3 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9C7CH-9C7DH | 40060-40061 | I3 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9C7EH-9C7FH | 40062-40063 | I3 63rd Harmonic Amplitude | THD= Rx/100 | Float | R

## Class S - 3s Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship |  | Data Type | Access Property
|  |  | Primary | Secondary
9652H-9653H | 38482-38483 | Frequency | F=Rx | F=Rx | Float | R
9654H-9655H | 38484-38485 | Phase A Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9656H-9657H | 38486-38487 | Phase B Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9658H-9659H | 38488-38489 | Phase C Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
965AH-965BH | 38490-38491 | Line Voltage AB | U=Rx | U=PT1/PT2 | Float | R
965CH-965DH | 38492-38493 | Line Voltage BC | U=Rx | U=PT1/PT2 | Float | R
965EH-965FH | 38494-38495 | Line Voltage CA | U=Rx | U=PT1/PT2 | Float | R
9660H-9661H | 38496-38497 | Average Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9662H-9663H | 38498-38499 | Average Line-Line Voltage | U=Rx | U=PT1/PT2 | Float | R
9664H-9665H | 38500-38501 | Phase A Current | I=Rx | I=CT1/CT2 | Float | R
9666H-9667H | 38502-38503 | Phase B Current | I=Rx | I=CT1/CT2 | Float | R
9668H-9669H | 38504-38505 | Phase C Current | I=Rx | I=CT1/CT2 | Float | R
966AH-966BH | 38506-38507 | Neutal Current | I=Rx | I=CT1/CT2 | Float | R
966CH-966DH | 38508-38509 | Average Current | I=Rx | I=CT1/CT2 | Float | R
966EH-966FH | 38510-38511 | Phase A (AB) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
9670H-9671H | 38512-38513 | Phase A (AB) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9672H-9673H | 38514-38515 | Phase A (AB) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9674H-9675H | 38516-38517 | RESERVED |  |  | Float | R
9676H-9677H | 38518-38519 | Phase B (BC) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
9678H-9679H | 38520-38521 | Phase B (BC) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
967AH-967BH | 38522-38523 | Phase B (BC) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
967CH-967DH | 38524-38525 | RESERVED |  |  | Float | R
967EH-967FH | 38526-38527 | Phase C (CA) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
9680H-9681H | 38528-38529 | Phase C (CA) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9682H-9683H | 38530-38531 | Phase C (CA) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9684H-9685H | 38532-38533 | RESERVED |  |  | Float | R
9686H-9687H | 38534-38535 | Phase A Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
9688H-9689H | 38536-38537 | Phase A Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
968AH-968BH | 38538-38539 | Phase A Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
968CH-968DH | 38540-38541 | RESERVED |  |  | Float | R
968EH-968FH | 38542-38543 | Phase B Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
9690H-9691H | 38544-38545 | Phase B Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9692H-9693H | 38546-38547 | Phase B Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9694H-9695H | 38548-38549 | RESERVED |  |  | Float | R
9696H-9697H | 38550-38551 | Phase C Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
9698H-9699H | 38552-38553 | Phase C Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
969AH-969BH | 38554-38555 | Phase C Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
969CH-969DH | 38556-38557 | RESERVED |  |  | Float | R
969EH-969FH | 38558-38559 | Voltage Unbalance Factor | Uunb=Rx/100 | Uunb=Rx/100 | Float | R
96A0H-96A1H | 38560-38561 | Voltage Zero Unbalance Factor | Iunb=Rx/100 | Iunb=Rx/100 | Float | R
96A2H-96A3H | 38562-38563 | Voltage Zero Sequence (Real) | V=Rx | V=Rx | Float | R
96A4H-96A5H | 38564-38565 | Voltage Zero Sequence (Imaginary) | V=Rx | V=Rx | Float | R
96A6H-96A7H | 38566-38567 | Voltage Positive Sequence (Real) | V=Rx | V=Rx | Float | R
96A8H-96A9H | 38568-38569 | Voltage Positive Sequence (Imaginary) | V=Rx | V=Rx | Float | R
96AAH-96ABH | 38570-38571 | Voltage Negative Sequence (Real) | V=Rx | V=Rx | Float | R
96ACH-96ADH | 38572-38573 | Voltage Negative Sequence (Imaginary) | V=Rx | V=Rx | Float | R
96AEH-96AFH | 38574-38575 | Current Unbalance Factor | I=Rx | I=Rx | Float | R
96B0H-96B1H | 38576-38577 | Current Zero Unbalance Factor | I=Rx | I=Rx | Float | R
96B2H-96B3H | 38578-38579 | Current Zero Sequence (Real) | I=Rx | I=Rx | Float | R
96B4H-96B5H | 38580-38581 | Current Zero Sequence (Imaginary) | I=Rx | I=Rx | Float | R
96B6H-96B7H | 38582-38583 | Current Positive Sequence (Real) | I=Rx | I=Rx | Float | R
96B8H-96B9H | 38584-38585 | Current Positive Sequence (Imaginary) | I=Rx | I=Rx | Float | R
96BAH-96BBH | 38586-38587 | Current Negative Sequence (Real) | I=Rx | I=Rx | Float | R
96BCH-96BDH | 38588-38589 | Current Negative Sequence (Imaginary) | I=Rx | I=Rx | Float | R

## 3s Harmonic Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Data Type | Access Property
V1(V12)
9C80H | 40064 | V1(V12) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9C81H | 40065 | V1(V12) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C82H | 40066 | V1(V12) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C83H | 40067 | V1(V12) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C84H | 40068 | V1(V12) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C85H | 40069 | V1(V12) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C86H | 40070 | V1(V12) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C87H | 40071 | V1(V12) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C88H | 40072 | V1(V12) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C89H | 40073 | V1(V12) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8AH | 40074 | V1(V12) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8BH | 40075 | V1(V12) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8CH | 40076 | V1(V12) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8DH | 40077 | V1(V12) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8EH | 40078 | V1(V12) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C8FH | 40079 | V1(V12) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C90H | 40080 | V1(V12) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C91H | 40081 | V1(V12) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C92H | 40082 | V1(V12) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C93H | 40083 | V1(V12) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C94H | 40084 | V1(V12) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9C95H | 40085 | V1(V12) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C96H | 40086 | V1(V12) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9C97H | 40087 | V1(V12) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C98H | 40088 | V1(V12) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C99H | 40089 | V1(V12) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9AH | 40090 | V1(V12) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9BH | 40091 | V1(V12) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9CH | 40092 | V1(V12) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9DH | 40093 | V1(V12) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9EH | 40094 | V1(V12) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9C9FH | 40095 | V1(V12) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA0H | 40096 | V1(V12) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA1H | 40097 | V1(V12) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA2H | 40098 | V1(V12) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA3H | 40099 | V1(V12) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA4H | 40100 | V1(V12) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA5H | 40101 | V1(V12) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA6H | 40102 | V1(V12) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA7H | 40103 | V1(V12) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA8H | 40104 | V1(V12) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9CA9H | 40105 | V1(V12) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CAAH | 40106 | V1(V12) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CABH | 40107 | V1(V12) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CACH | 40108 | V1(V12) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CADH | 40109 | V1(V12) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CAEH | 40110 | V1(V12) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CAFH | 40111 | V1(V12) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB0H | 40112 | V1(V12) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB1H | 40113 | V1(V12) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB2H | 40114 | V1(V12) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB3H | 40115 | V1(V12) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB4H | 40116 | V1(V12) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB5H | 40117 | V1(V12) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB6H | 40118 | V1(V12) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB7H | 40119 | V1(V12) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB8H | 40120 | V1(V12) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CB9H | 40121 | V1(V12) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBAH | 40122 | V1(V12) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBBH | 40123 | V1(V12) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBCH | 40124 | V1(V12) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBDH | 40125 | V1(V12) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBEH | 40126 | V1(V12) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9CBFH | 40127 | RESERVED |  | Word | R
9CC0H-9CC1H | 40128-40129 | V1(V12) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9CC2H-9CC3H | 40130-40131 | V1(V12) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9CC4H-9CC5H | 40132-40133 | V1(V12) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9CC6H-9CC7H | 40134-40135 | V1(V12) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9CC8H-9CC9H | 40136-40137 | V1(V12) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9CCAH-9CCBH | 40138-40139 | V1(V12) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9CCCH-9CCDH | 40140-40141 | V1(V12) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
8CCEH-9CCFH | 36046-40143 | V1(V12) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9CD0H-9CD1H | 40144-40145 | V1(V12) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9CD2H-9CD3H | 40146-40147 | V1(V12) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9CD4H-9CD5H | 40148-40149 | V1(V12) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9CD6H-9CD7H | 40150-40151 | V1(V12) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9CD8H-9CD9H | 40152-40153 | V1(V12) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9CDAH-9CDBH | 40154-40155 | V1(V12) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9CDCH-9CDDH | 40156-40157 | V1(V12) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9CDEH-9CDFH | 40158-40159 | V1(V12) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9CE0H-9CE1H | 40160-40161 | V1(V12) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9CE2H-9CE3H | 40162-40163 | V1(V12) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9CE4H-9CE5H | 40164-40165 | V1(V12) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9CE6H-9CE7H | 40166-40167 | V1(V12) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9CE8H-9CE9H | 40168-40169 | V1(V12) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9CEAH-9CEBH | 40170-40171 | V1(V12) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9CECH-9CEDH | 40172-40173 | V1(V12) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9CEEH-9CEFH | 40174-40175 | V1(V12) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9CF0H-9CF1H | 40176-40177 | V1(V12) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9CF2H-9CF3H | 40178-40179 | V1(V12) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9CF4H-9CF5H | 40180-40181 | V1(V12) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9CF6H-9CF7H | 40182-40183 | V1(V12) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9CF8H-9CF9H | 40184-40185 | V1(V12) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9CFAH-9CFBH | 40186-40187 | V1(V12) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9CFCH-9CFDH | 40188-40189 | V1(V12) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9CFEH-9CFFH | 40190-40191 | V1(V12) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9D00H-9D01H | 40192-40193 | V1(V12) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9D02H-9D03H | 40194-40195 | V1(V12) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9D04H-9D05H | 40196-40197 | V1(V12) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9D06H-9D07H | 40198-40199 | V1(V12) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9D08H-9D09H | 40200-40201 | V1(V12) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9D0AH-9D0BH | 40202-40203 | V1(V12) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9D0CH-9D0DH | 40204-40205 | V1(V12) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9D0EH-9D0FH | 40206-40207 | V1(V12) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9D10H-9D11H | 40208-40209 | V1(V12) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9D12H-9D13H | 40210-40211 | V1(V12) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9D14H-9D15H | 40212-40213 | V1(V12) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9D16H-9D17H | 40214-40215 | V1(V12) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9D18H-9D19H | 40216-40217 | V1(V12) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9D1AH-9D1BH | 40218-40219 | V1(V12) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9D1CH-9D1DH | 40220-40221 | V1(V12) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9D1EH-9D1FH | 40222-40223 | V1(V12) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9D20H-9D21H | 40224-40225 | V1(V12) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9D22H-9D23H | 40226-40227 | V1(V12) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9D24H-9D25H | 40228-40229 | V1(V12) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9D26H-9D27H | 40230-40231 | V1(V12) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9D28H-9D29H | 40232-40233 | V1(V12) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9D2AH-9D2BH | 40234-40235 | V1(V12) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9D2CH-9D2DH | 40236-40237 | V1(V12) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9D1EH-9D2FH | 40222-40239 | V1(V12) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9D30H-9D31H | 40240-40241 | V1(V12) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9D32H-9D33H | 40242-40243 | V1(V12) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9D34H-9D35H | 40244-40245 | V1(V12) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9D36H-9D37H | 40246-40247 | V1(V12) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9D38H-9D39H | 40248-40249 | V1(V12) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9D3AH-9D3BH | 40250-40251 | V1(V12) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9D3CH-9D3DH | 40252-40253 | V1(V12) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V2(V23)
9D3EH | 40254 | V2(V23) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D3FH | 40255 | V2(V23) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D40H | 40256 | V2(V23) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D41H | 40257 | V2(V23) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D42H | 40258 | V2(V23) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D43H | 40259 | V2(V23) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D44H | 40260 | V2(V23) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D45H | 40261 | V2(V23) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D46H | 40262 | V2(V23) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D47H | 40263 | V2(V23) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D48H | 40264 | V2(V23) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D49H | 40265 | V2(V23) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4AH | 40266 | V2(V23) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4BH | 40267 | V2(V23) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4CH | 40268 | V2(V23) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4DH | 40269 | V2(V23) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4EH | 40270 | V2(V23) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D4FH | 40271 | V2(V23) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D50H | 40272 | V2(V23) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D51H | 40273 | V2(V23) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D52H | 40274 | V2(V23) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D53H | 40275 | V2(V23) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D54H | 40276 | V2(V23) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D55H | 40277 | V2(V23) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D56H | 40278 | V2(V23) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D57H | 40279 | V2(V23) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D58H | 40280 | V2(V23) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D59H | 40281 | V2(V23) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5AH | 40282 | V2(V23) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5BH | 40283 | V2(V23) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5CH | 40284 | V2(V23) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5DH | 40285 | V2(V23) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5EH | 40286 | V2(V23) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D5FH | 40287 | V2(V23) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D60H | 40288 | V2(V23) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D61H | 40289 | V2(V23) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D62H | 40290 | V2(V23) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D63H | 40291 | V2(V23) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D64H | 40292 | V2(V23) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D65H | 40293 | V2(V23) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D66H | 40294 | V2(V23) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D67H | 40295 | V2(V23) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D68H | 40296 | V2(V23) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D69H | 40297 | V2(V23) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6AH | 40298 | V2(V23) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6BH | 40299 | V2(V23) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6CH | 40300 | V2(V23) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6DH | 40301 | V2(V23) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6EH | 40302 | V2(V23) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D6FH | 40303 | V2(V23) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D70H | 40304 | V2(V23) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D71H | 40305 | V2(V23) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D72H | 40306 | V2(V23) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D73H | 40307 | V2(V23) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D74H | 40308 | V2(V23) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D75H | 40309 | V2(V23) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D76H | 40310 | V2(V23) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D77H | 40311 | V2(V23) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D78H | 40312 | V2(V23) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D79H | 40313 | V2(V23) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9D7AH | 40314 | V2(V23) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9D7BH | 40315 | V2(V23) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D7CH | 40316 | V2(V23) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9D7DH | 40317 | RESERVED |  | Word | R
9D7EH-9D7FH | 40318-40319 | V2(V23) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9D80H-9D81H | 40320-40321 | V2(V23) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9D82H-9D83H | 40322-40323 | V2(V23) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9D84H-9D85H | 40324-40325 | V2(V23) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9D86H-9D87H | 40326-40327 | V2(V23) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9D88H-9D89H | 40328-40329 | V2(V23) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9D8AH-9D8BH | 40330-40331 | V2(V23) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9D8CH-9D8DH | 40332-40333 | V2(V23) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9D8EH-9D8FH | 40334-40335 | V2(V23) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9D90H-9D91H | 40336-40337 | V2(V23) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9D92H-9D93H | 40338-40339 | V2(V23) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9D94H-9D95H | 40340-40341 | V2(V23) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9D96H-9D97H | 40342-40343 | V2(V23) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9D98H-9D99H | 40344-40345 | V2(V23) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9D9AH-9D9BH | 40346-40347 | V2(V23) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9D9CH-9D9DH | 40348-40349 | V2(V23) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9D9EH-9D9FH | 40350-40351 | V2(V23) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9DA0H-9DA1H | 40352-40353 | V2(V23) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9DA2H-9DA3H | 40354-40355 | V2(V23) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9DA4H-9DA5H | 40356-40357 | V2(V23) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9DA6H-9DA7H | 40358-40359 | V2(V23) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9DA8H-9DA9H | 40360-40361 | V2(V23) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9DAAH-9DABH | 40362-40363 | V2(V23) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9DACH-9DADH | 40364-40365 | V2(V23) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9DAEH-9DAFH | 40366-40367 | V2(V23) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9DB0H-9DB1H | 40368-40369 | V2(V23) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9DB2H-9DB3H | 40370-40371 | V2(V23) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9DB4H-9DB5H | 40372-40373 | V2(V23) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9DB6H-9DB7H | 40374-40375 | V2(V23) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9DB8H-9DB9H | 40376-40377 | V2(V23) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9DBAH-9DBBH | 40378-40379 | V2(V23) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9DBCH-9DBDH | 40380-40381 | V2(V23) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9DBEH-9DBFH | 40382-40383 | V2(V23) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9DC0H-9DC1H | 40384-40385 | V2(V23) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9DC2H-9DC3H | 40386-40387 | V2(V23) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9DC4H-9DC5H | 40388-40389 | V2(V23) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9DC6H-9DC7H | 40390-40391 | V2(V23) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9DC8H-9DC9H | 40392-40393 | V2(V23) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9DCAH-9DCBH | 40394-40395 | V2(V23) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9DCCH-9DCDH | 40396-40397 | V2(V23) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9DCEH-9DCFH | 40398-40399 | V2(V23) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9DD0H-9DD1H | 40400-40401 | V2(V23) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9DD2H-9DD3H | 40402-40403 | V2(V23) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9DD4H-9DD5H | 40404-40405 | V2(V23) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9DD6H-9DD7H | 40406-40407 | V2(V23) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9DD8H-9DD9H | 40408-40409 | V2(V23) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9DDAH-9DDBH | 40410-40411 | V2(V23) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9DDCH-9DDDH | 40412-40413 | V2(V23) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9DDEH-9DDFH | 40414-40415 | V2(V23) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9DE0H-9DE1H | 40416-40417 | V2(V23) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9DE2H-9DE3H | 40418-40419 | V2(V23) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9DE4H-9DE5H | 40420-40421 | V2(V23) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9DE6H-9DE7H | 40422-40423 | V2(V23) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9DE8H-9DE9H | 40424-40425 | V2(V23) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9DEAH-9DEBH | 40426-40427 | V2(V23) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9DECH-9DEDH | 40428-40429 | V2(V23) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9DEEH-9DEFH | 40430-40431 | V2(V23) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9DF0H-9DF1H | 40432-40433 | V2(V23) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9DF2H-9DF3H | 40434-40435 | V2(V23) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9DF4H-9DF5H | 40436-40437 | V2(V23) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9DF6H-9DF7H | 40438-40439 | V2(V23) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9DF8H-9DF9H | 40440-40441 | V2(V23) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9DFAH-9DFBH | 40442-40443 | V2(V23) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V3(V31)
9DFCH | 40444 | V3(V31) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9DFDH | 40445 | V3(V31) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9DFEH | 40446 | V3(V31) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9DFFH | 40447 | V3(V31) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E00H | 40448 | V3(V31) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E01H | 40449 | V3(V31) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E02H | 40450 | V3(V31) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E03H | 40451 | V3(V31) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E04H | 40452 | V3(V31) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E05H | 40453 | V3(V31) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E06H | 40454 | V3(V31) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E07H | 40455 | V3(V31) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E08H | 40456 | V3(V31) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E09H | 40457 | V3(V31) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0AH | 40458 | V3(V31) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0BH | 40459 | V3(V31) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0CH | 40460 | V3(V31) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0DH | 40461 | V3(V31) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0EH | 40462 | V3(V31) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E0FH | 40463 | V3(V31) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E10H | 40464 | V3(V31) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9E11H | 40465 | V3(V31) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E12H | 40466 | V3(V31) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E13H | 40467 | V3(V31) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E14H | 40468 | V3(V31) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E15H | 40469 | V3(V31) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E16H | 40470 | V3(V31) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E17H | 40471 | V3(V31) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E18H | 40472 | V3(V31) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E19H | 40473 | V3(V31) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1AH | 40474 | V3(V31) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1BH | 40475 | V3(V31) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1CH | 40476 | V3(V31) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1DH | 40477 | V3(V31) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1EH | 40478 | V3(V31) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E1FH | 40479 | V3(V31) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E20H | 40480 | V3(V31) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E21H | 40481 | V3(V31) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E22H | 40482 | V3(V31) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E23H | 40483 | V3(V31) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E24H | 40484 | V3(V31) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9E25H | 40485 | V3(V31) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E26H | 40486 | V3(V31) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E27H | 40487 | V3(V31) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E28H | 40488 | V3(V31) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E29H | 40489 | V3(V31) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2AH | 40490 | V3(V31) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2BH | 40491 | V3(V31) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2CH | 40492 | V3(V31) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2DH | 40493 | V3(V31) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2EH | 40494 | V3(V31) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9E2FH | 40495 | V3(V31) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E30H | 40496 | V3(V31) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E31H | 40497 | V3(V31) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E32H | 40498 | V3(V31) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E33H | 40499 | V3(V31) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E34H | 40500 | V3(V31) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E35H | 40501 | V3(V31) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E36H | 40502 | V3(V31) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E37H | 40503 | V3(V31) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9E38H | 40504 | V3(V31) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9E39H | 40505 | V3(V31) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E3AH | 40506 | V3(V31) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9E3BH | 40507 | RESERVED |  | Word | R
9E3CH-9E3DH | 40508-40509 | V3(V31) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9E3EH-9E3FH | 40510-40511 | V3(V31) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9E40H-9E41H | 40512-40513 | V3(V31) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9E42H-9E43H | 40514-40515 | V3(V31) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9E44H-9E45H | 40516-40517 | V3(V31) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9E46H-9E47H | 40518-40519 | V3(V31) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9E48H-9E49H | 40520-40521 | V3(V31) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9E4AH-9E4BH | 40522-40523 | V3(V31) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9E4CH-9E4DH | 40524-40525 | V3(V31) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9E4EH-9E4FH | 40526-40527 | V3(V31) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9E50H-9E51H | 40528-40529 | V3(V31) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9E52H-9E53H | 40530-40531 | V3(V31) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9E54H-9E55H | 40532-40533 | V3(V31) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9E56H-9E57H | 40534-40535 | V3(V31) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9E58H-9E59H | 40536-40537 | V3(V31) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9E5AH-9E5BH | 40538-40539 | V3(V31) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9E5CH-9E5DH | 40540-40541 | V3(V31) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9E5EH-9E5FH | 40542-40543 | V3(V31) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9E60H-9E61H | 40544-40545 | V3(V31) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9E62H-9E63H | 40546-40547 | V3(V31) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9E64H-9E65H | 40548-40549 | V3(V31) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9E66H-9E67H | 40550-40551 | V3(V31) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9E68H-9E69H | 40552-40553 | V3(V31) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9E6AH-9E6BH | 40554-40555 | V3(V31) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9E6CH-9E6DH | 40556-40557 | V3(V31) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9E6EH-9E6FH | 40558-40559 | V3(V31) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9E70H-9E71H | 40560-40561 | V3(V31) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9E72H-9E73H | 40562-40563 | V3(V31) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9E74H-9E75H | 40564-40565 | V3(V31) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9E76H-9E77H | 40566-40567 | V3(V31) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9E78H-9E79H | 40568-40569 | V3(V31) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9E7AH-9E7BH | 40570-40571 | V3(V31) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9E7CH-9E7DH | 40572-40573 | V3(V31) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9E7EH-9E7FH | 40574-40575 | V3(V31) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9E80H-9E81H | 40576-40577 | V3(V31) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9E82H-9E83H | 40578-40579 | V3(V31) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9E84H-9E85H | 40580-40581 | V3(V31) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9E86H-9E87H | 40582-40583 | V3(V31) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9E88H-9E89H | 40584-40585 | V3(V31) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9E8AH-9E8BH | 40586-40587 | V3(V31) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9E8CH-9E8DH | 40588-40589 | V3(V31) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9E8EH-9E8FH | 40590-40591 | V3(V31) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9E90H-9E91H | 40592-40593 | V3(V31) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9E92H-9E93H | 40594-40595 | V3(V31) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9E94H-9E95H | 40596-40597 | V3(V31) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9E96H-9E97H | 40598-40599 | V3(V31) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9E98H-9E99H | 40600-40601 | V3(V31) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9E9AH-9E9BH | 40602-40603 | V3(V31) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9E9CH-9E9DH | 40604-40605 | V3(V31) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9E9EH-9E9FH | 40606-40607 | V3(V31) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9EA0H-9EA1H | 40608-40609 | V3(V31) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9EA2H-9EA3H | 40610-40611 | V3(V31) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9EA4H-9EA5H | 40612-40613 | V3(V31) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9EA6H-9EA7H | 40614-40615 | V3(V31) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9EA8H-9EA9H | 40616-40617 | V3(V31) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9EAAH-9EABH | 40618-40619 | V3(V31) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9EACH-9EADH | 40620-40621 | V3(V31) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9EAEH-9EAFH | 40622-40623 | V3(V31) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9EB0H-9EB1H | 40624-40625 | V3(V31) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9EB2H-9EB3H | 40626-40627 | V3(V31) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9EB4H-9EB5H | 40628-40629 | V3(V31) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9EB6H-9EB7H | 40630-40631 | V3(V31) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9EB8H-9EB9H | 40632-40633 | V3(V31) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase A Current
9EBAH | 40634 | I1 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9EBBH | 40635 | I1 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EBCH | 40636 | I1 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EBDH | 40637 | I1 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EBEH | 40638 | I1 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EBFH | 40639 | I1 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC0H | 40640 | I1 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC1H | 40641 | I1 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC2H | 40642 | I1 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC3H | 40643 | I1 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC4H | 40644 | I1 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC5H | 40645 | I1 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC6H | 40646 | I1 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC7H | 40647 | I1 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC8H | 40648 | I1 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EC9H | 40649 | I1 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECAH | 40650 | I1 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECBH | 40651 | I1 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECCH | 40652 | I1 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECDH | 40653 | I1 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECEH | 40654 | I1 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9ECFH | 40655 | I1 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED0H | 40656 | I1 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED1H | 40657 | I1 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED2H | 40658 | I1 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED3H | 40659 | I1 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED4H | 40660 | I1 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED5H | 40661 | I1 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED6H | 40662 | I1 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED7H | 40663 | I1 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED8H | 40664 | I1 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9ED9H | 40665 | I1 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDAH | 40666 | I1 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDBH | 40667 | I1 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDCH | 40668 | I1 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDDH | 40669 | I1 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDEH | 40670 | I1 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EDFH | 40671 | I1 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE0H | 40672 | I1 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE1H | 40673 | I1 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE2H | 40674 | I1 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE3H | 40675 | I1 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE4H | 40676 | I1 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE5H | 40677 | I1 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE6H | 40678 | I1 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE7H | 40679 | I1 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE8H | 40680 | I1 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EE9H | 40681 | I1 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EEAH | 40682 | I1 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EEBH | 40683 | I1 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EECH | 40684 | I1 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9EEDH | 40685 | I1 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EEEH | 40686 | I1 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EEFH | 40687 | I1 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF0H | 40688 | I1 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF1H | 40689 | I1 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF2H | 40690 | I1 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF3H | 40691 | I1 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF4H | 40692 | I1 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF5H | 40693 | I1 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF6H | 40694 | I1 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF7H | 40695 | I1 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF8H | 40696 | I1 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9EF9H | 40697 | RESERVED |  | Word | R
9EFAB-9EFBH | 40698-40699 | I1 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9EFCH-9EFDH | 40700-40701 | I1 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9EFEH-9EFFH | 40702-40703 | I1 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9F00H-9F01H | 40704-40705 | I1 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9F02H-9F03H | 40706-40707 | I1 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9F04H-9F05H | 40708-40709 | I1 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9F06H-9F07H | 40710-40711 | I1 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9F08H-9F09H | 40712-40713 | I1 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9F0AH-9F0BH | 40714-40715 | I1 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9F0CH-9F0DH | 40716-40717 | I1 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9F0EH-9F0FH | 40718-40719 | I1 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9F10H-9F11H | 40720-40721 | I1 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9F12H-9F13H | 40722-40723 | I1 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9F14H-9F15H | 40724-40725 | I1 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9F16H-9F17H | 40726-40727 | I1 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9F18H-9F19H | 40728-40729 | I1 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9F1AH-9F1BH | 40730-40731 | I1 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9F1CH-9F1DH | 40732-40733 | I1 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9F1EH-9F1FH | 40734-40735 | I1 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9F20H-9F21H | 40736-40737 | I1 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9F22H-9F23H | 40738-40739 | I1 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9F24H-9F25H | 40740-40741 | I1 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9F26H-9F27H | 40742-40743 | I1 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9F28H-9F29H | 40744-40745 | I1 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9F2AH-9F2BH | 40746-40747 | I1 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9F2CH-9F2DH | 40748-40749 | I1 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9F2EH-9F2FH | 40750-40751 | I1 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9F30H-9F31H | 40752-40753 | I1 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9F32H-9F33H | 40754-40755 | I1 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9F34H-9F35H | 40756-40757 | I1 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9F36H-9F37H | 40758-40759 | I1 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9F38H-9F39H | 40760-40761 | I1 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9F3AH-9F3BH | 40762-40763 | I1 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9F3CH-9F3DH | 40764-40765 | I1 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9F3EH-9F3FH | 40766-40767 | I1 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9F40H-9F41H | 40768-40769 | I1 36th Harmonic Amplitude | THD= Rx/100 | Float | R
9F42H-9F43H | 40770-40771 | I1 37th Harmonic Amplitude | THD= Rx/100 | Float | R
9F44H-9F45H | 40772-40773 | I1 38th Harmonic Amplitude | THD= Rx/100 | Float | R
9F46H-9F47H | 40774-40775 | I1 39th Harmonic Amplitude | THD= Rx/100 | Float | R
9F48H-9F49H | 40776-40777 | I1 40th Harmonic Amplitude | THD= Rx/100 | Float | R
9F4AH-9F4BH | 40778-40779 | I1 41st Harmonic Amplitude | THD= Rx/100 | Float | R
9F4CH-9F4DH | 40780-40781 | I1 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
9F4EH-9F4FH | 40782-40783 | I1 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
9F50H-9F51H | 40784-40785 | I1 44th Harmonic Amplitude | THD= Rx/100 | Float | R
9F52H-9F53H | 40786-40787 | I1 45th Harmonic Amplitude | THD= Rx/100 | Float | R
9F54H-9F55H | 40788-40789 | I1 46th Harmonic Amplitude | THD= Rx/100 | Float | R
9F56H-9F57H | 40790-40791 | I1 47th Harmonic Amplitude | THD= Rx/100 | Float | R
9F58H-9F59H | 40792-40793 | I1 48th Harmonic Amplitude | THD= Rx/100 | Float | R
9F5AH-9F5BH | 40794-40795 | I1 49th Harmonic Amplitude | THD= Rx/100 | Float | R
9F5CH-9F5DH | 40796-40797 | I1 50th Harmonic Amplitude | THD= Rx/100 | Float | R
9F5EH-9F5FH | 40798-40799 | I1 51st Harmonic Amplitude | THD= Rx/100 | Float | R
9F60H-9F61H | 40800-40801 | I1 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
9F62H-9F63H | 40802-40803 | I1 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
9F64H-9F65H | 40804-40805 | I1 54th Harmonic Amplitude | THD= Rx/100 | Float | R
9F66H-9F67H | 40806-40807 | I1 55th Harmonic Amplitude | THD= Rx/100 | Float | R
9F68H-9F69H | 40808-40809 | I1 56th Harmonic Amplitude | THD= Rx/100 | Float | R
9F6AH-9F6BH | 40810-40811 | I1 57th Harmonic Amplitude | THD= Rx/100 | Float | R
9F6CH-9F6DH | 40812-40813 | I1 58th Harmonic Amplitude | THD= Rx/100 | Float | R
9F6EH-9F6FH | 40814-40815 | I1 59th Harmonic Amplitude | THD= Rx/100 | Float | R
9F70H-9F71H | 40816-40817 | I1 60th Harmonic Amplitude | THD= Rx/100 | Float | R
9F72H-9F73H | 40818-40819 | I1 61st Harmonic Amplitude | THD= Rx/100 | Float | R
9F74H-9F75H | 40820-40821 | I1 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
9F76H-9F77H | 40822-40823 | I1 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase B Current
9F78H | 40824 | I2 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
9F79H | 40825 | I2 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7AH | 40826 | I2 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7BH | 40827 | I2 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7CH | 40828 | I2 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7DH | 40829 | I2 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7EH | 40830 | I2 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F7FH | 40831 | I2 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F80H | 40832 | I2 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F81H | 40833 | I2 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F82H | 40834 | I2 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F83H | 40835 | I2 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F84H | 40836 | I2 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F85H | 40837 | I2 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F86H | 40838 | I2 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F87H | 40839 | I2 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F88H | 40840 | I2 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F89H | 40841 | I2 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8AH | 40842 | I2 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8BH | 40843 | I2 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8CH | 40844 | I2 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8DH | 40845 | I2 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8EH | 40846 | I2 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F8FH | 40847 | I2 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F90H | 40848 | I2 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F91H | 40849 | I2 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F92H | 40850 | I2 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F93H | 40851 | I2 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F94H | 40852 | I2 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F95H | 40853 | I2 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F96H | 40854 | I2 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
9F97H | 40855 | I2 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F98H | 40856 | I2 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9F99H | 40857 | I2 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9AH | 40858 | I2 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9BH | 40859 | I2 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9CH | 40860 | I2 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9DH | 40861 | I2 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9EH | 40862 | I2 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
9F9FH | 40863 | I2 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA0H | 40864 | I2 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA1H | 40865 | I2 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA2H | 40866 | I2 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA3H | 40867 | I2 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA4H | 40868 | I2 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA5H | 40869 | I2 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA6H | 40870 | I2 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA7H | 40871 | I2 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA8H | 40872 | I2 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FA9H | 40873 | I2 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FAAH | 40874 | I2 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
9FABH | 40875 | I2 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FACH | 40876 | I2 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FADH | 40877 | I2 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FAEH | 40878 | I2 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FAFH | 40879 | I2 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB0H | 40880 | I2 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB1H | 40881 | I2 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB2H | 40882 | I2 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB3H | 40883 | I2 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB4H | 40884 | I2 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB5H | 40885 | I2 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB6H | 40886 | I2 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
9FB7H | 40887 | RESERVED |  | Word | R
9FB8H-9FB9H | 40888-40889 | I2 1st Harmonic Amplitude | THD= Rx/100 | Float | R
9FBAH-9FBBH | 40890-40891 | I2 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
9FBCH-9FBDH | 40892-40893 | I2 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
9FBEH-9FBFH | 40894-40895 | I2 4th Harmonic Amplitude | THD= Rx/100 | Float | R
9FC0H-9FC1H | 40896-40897 | I2 5th Harmonic Amplitude | THD= Rx/100 | Float | R
9FC2H-9FC3H | 40898-40899 | I2 6th Harmonic Amplitude | THD= Rx/100 | Float | R
9FC4H-9FC5H | 40900-40901 | I2 7th Harmonic Amplitude | THD= Rx/100 | Float | R
9FC6H-9FC7H | 40902-40903 | I2 8th Harmonic Amplitude | THD= Rx/100 | Float | R
9FC8H-9FC9H | 40904-40905 | I2 9th Harmonic Amplitude | THD= Rx/100 | Float | R
9FCAH-9FCBH | 40906-40907 | I2 10th Harmonic Amplitude | THD= Rx/100 | Float | R
9FCCH-9FCDH | 40908-40909 | I2 11th Harmonic Amplitude | THD= Rx/100 | Float | R
9FCEH-9FCFH | 40910-40911 | I2 12th Harmonic Amplitude | THD= Rx/100 | Float | R
9FD0H-9FD1H | 40912-40913 | I2 13th Harmonic Amplitude | THD= Rx/100 | Float | R
9FD2H-9FD3H | 40914-40915 | I2 14th Harmonic Amplitude | THD= Rx/100 | Float | R
9FD4H-9FD5H | 40916-40917 | I2 15th Harmonic Amplitude | THD= Rx/100 | Float | R
9FD6H-9FD7H | 40918-40919 | I2 16th Harmonic Amplitude | THD= Rx/100 | Float | R
9FD8H-9FD9H | 40920-40921 | I2 17th Harmonic Amplitude | THD= Rx/100 | Float | R
9FDAH-9FDBH | 40922-40923 | I2 18th Harmonic Amplitude | THD= Rx/100 | Float | R
9FDCH-9FDDH | 40924-40925 | I2 19th Harmonic Amplitude | THD= Rx/100 | Float | R
9FDEH-9FDFH | 40926-40927 | I2 20th Harmonic Amplitude | THD= Rx/100 | Float | R
9FE0H-9FE1H | 40928-40929 | I2 21st Harmonic Amplitude | THD= Rx/100 | Float | R
9FE2H-9FE3H | 40930-40931 | I2 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
9FE4H-9FE5H | 40932-40933 | I2 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
9FE6H-9FE7H | 40934-40935 | I2 24th Harmonic Amplitude | THD= Rx/100 | Float | R
9FE8H-9FE9H | 40936-40937 | I2 25th Harmonic Amplitude | THD= Rx/100 | Float | R
9FEAH-9FEBH | 40938-40939 | I2 26th Harmonic Amplitude | THD= Rx/100 | Float | R
9FECH-9FEDH | 40940-40941 | I2 27th Harmonic Amplitude | THD= Rx/100 | Float | R
9FEEH-9FEFH | 40942-40943 | I2 28th Harmonic Amplitude | THD= Rx/100 | Float | R
9FF0H-9FF1H | 40944-40945 | I2 29th Harmonic Amplitude | THD= Rx/100 | Float | R
9FF2H-9FF3H | 40946-40947 | I2 30th Harmonic Amplitude | THD= Rx/100 | Float | R
9FF4H-9FF5H | 40948-40949 | I2 31st Harmonic Amplitude | THD= Rx/100 | Float | R
9FF6H-9FF7H | 40950-40951 | I2 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
9FF8H-9FF9H | 40952-40953 | I2 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
9FFAH-9FFBH | 40954-40955 | I2 34th Harmonic Amplitude | THD= Rx/100 | Float | R
9FFCH-9FFDH | 40956-40957 | I2 35th Harmonic Amplitude | THD= Rx/100 | Float | R
9FFEH-9FFFH | 40958-40959 | I2 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A000H-A001H | 40960-40961 | I2 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A002H-A003H | 40962-40963 | I2 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A004H-A005H | 40964-40965 | I2 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A006H-A007H | 40966-40967 | I2 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A008H-A009H | 40968-40969 | I2 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A00AH-A00BH | 40970-40971 | I2 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A00CH-A00DH | 40972-40973 | I2 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A00EH-A00FH | 40974-40975 | I2 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A010H-A011H | 40976-40977 | I2 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A012H-A013H | 40978-40979 | I2 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A014H-A015H | 40980-40981 | I2 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A016H-A017H | 40982-40983 | I2 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A018H-A019H | 40984-40985 | I2 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A01AH-A01BH | 40986-40987 | I2 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A01CH-A01DH | 40988-40989 | I2 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A01EH-A01FH | 40990-40991 | I2 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A020H-A021H | 40992-40993 | I2 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A022H-A023H | 40994-40995 | I2 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A024H-A025H | 40996-40997 | I2 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A026H-A027H | 40998-40999 | I2 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A028H-A029H | 41000-41001 | I2 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A02AH-A02BH | 41002-41003 | I2 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A02CH-A02DH | 41004-41005 | I2 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A02EH-A02FH | 41006-41007 | I2 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A030H-A031H | 41008-41009 | I2 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A032H-A033H | 41010-41011 | I2 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A034H-A035H | 41012-41013 | I2 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase C Current
A036H | 41014 | I3 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A037H | 41015 | I3 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A038H | 41016 | I3 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A039H | 41017 | I3 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03AH | 41018 | I3 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03BH | 41019 | I3 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03CH | 41020 | I3 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03DH | 41021 | I3 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03EH | 41022 | I3 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A03FH | 41023 | I3 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A040H | 41024 | I3 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A041H | 41025 | I3 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A042H | 41026 | I3 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A043H | 41027 | I3 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A044H | 41028 | I3 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A045H | 41029 | I3 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A046H | 41030 | I3 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A047H | 41031 | I3 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A048H | 41032 | I3 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A049H | 41033 | I3 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A04AH | 41034 | I3 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A04BH | 41035 | I3 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A04CH | 41036 | I3 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A04DH | 41037 | I3 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A04EH | 41038 | I3 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A04FH | 41039 | I3 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A050H | 41040 | I3 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A051H | 41041 | I3 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A052H | 41042 | I3 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A053H | 41043 | I3 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A054H | 41044 | I3 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A055H | 41045 | I3 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A056H | 41046 | I3 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A057H | 41047 | I3 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A058H | 41048 | I3 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A059A | 41049 | I3 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A05AH | 41050 | I3 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A05BH | 41051 | I3 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A05CH | 41052 | I3 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A05DH | 41053 | I3 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A05EH | 41054 | I3 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A05FH | 41055 | I3 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A060H | 41056 | I3 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A061H | 41057 | I3 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A062H | 41058 | I3 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A063H | 41059 | I3 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A064H | 41060 | I3 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A065H | 41061 | I3 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A066H | 41062 | I3 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A067H | 41063 | I3 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A068H | 41064 | I3 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A069H | 41065 | I3 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A06AH | 41066 | I3 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A06BH | 41067 | I3 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A06CH | 41068 | I3 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A06DH | 41069 | I3 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A06EH | 41070 | I3 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A06FH | 41071 | I3 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A070H | 41072 | I3 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A071H | 41073 | I3 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A072H | 41074 | I3 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A073H | 41075 | I3 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A074H | 41076 | I3 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A075H | 41077 | RESERVED |  | Word | R
A076H-A077H | 41078-41079 | I3 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A078H-A079H | 41080-41081 | I3 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A07AH-A07BH | 41082-41083 | I3 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A07CH-A07DH | 41084-41085 | I3 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A07EH-A07FH | 41086-41087 | I3 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A080H-A081H | 41088-41089 | I3 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A082H-A083H | 41090-41091 | I3 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A084H-A085H | 41092-41093 | I3 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A086H-A087H | 41094-41095 | I3 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A088H-A089H | 41096-41097 | I3 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A08AH-A08BH | 41098-41099 | I3 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A08CH-A08DH | 41100-41101 | I3 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A08EH-A08FH | 41102-41103 | I3 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A090H-A091H | 41104-41105 | I3 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A092H-A093H | 41106-41107 | I3 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A094H-A095H | 41108-41109 | I3 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A096H-A097H | 41110-41111 | I3 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A098H-A099H | 41112-41113 | I3 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A09AH-A09BH | 41114-41115 | I3 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A09CH-A09DH | 41116-41117 | I3 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A09EH-A09FH | 41118-41119 | I3 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A0A0H-A0A1H | 41120-41121 | I3 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A0A2H-A0A3H | 41122-41123 | I3 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A0A4H-A0A5H | 41124-41125 | I3 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A0A6H-A0A7H | 41126-41127 | I3 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A0A8H-A0A9H | 41128-41129 | I3 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A0AAH-A0ABH | 41130-41131 | I3 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A0ACH-A0ADH | 41132-41133 | I3 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A0AEH-A0AFH | 41134-41135 | I3 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A0B0H-A0B1H | 41136-41137 | I3 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A0B2H-A0B3H | 41138-41139 | I3 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A0B4H-A0B5H | 41140-41141 | I3 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A0B6H-A0B7H | 41142-41143 | I3 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A0B8H-A0B9H | 41144-41145 | I3 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A0BAH-A0BBH | 41146-41147 | I3 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A0BCH-A0BDH | 41148-41149 | I3 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A0BEH-A0BFH | 41150-41151 | I3 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A0C0H-A0C1H | 41152-41153 | I3 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A0C2H-A0C3H | 41154-41155 | I3 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A0C4H-A0C5H | 41156-41157 | I3 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A0C6H-A0C7H | 41158-41159 | I3 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A0C8H-A0C9H | 41160-41161 | I3 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A0CAH-A0CBH | 41162-41163 | I3 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A0CCH-A0CDH | 41164-41165 | I3 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A0CEH-A0CFH | 41166-41167 | I3 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A0D0H-A0D1H | 41168-41169 | I3 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A0D2H-A0D3H | 41170-41171 | I3 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A0D4H-A0D5H | 41172-41173 | I3 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A0D6H-A0D7H | 41174-41175 | I3 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A0D8H-A0D9H | 41176-41177 | I3 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A0DAH-A0DBH | 41178-41179 | I3 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A0DCH-A0DDH | 41180-41181 | I3 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A0DEH-A0DFH | 41182-41183 | I3 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A0E0H-A0E1H | 41184-41185 | I3 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A0E2H-A0E3H | 41186-41187 | I3 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A0E4H-A0E5H | 41188-41189 | I3 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A0E6H-A0E7H | 41190-41191 | I3 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A0E8H-A0E9H | 41192-41193 | I3 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A0EAH-A0EBH | 41194-41195 | I3 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A0ECH-A0EDH | 41196-41197 | I3 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A0EEH-A0EFH | 41198-41199 | I3 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A0F0H-A0F1H | 41200-41201 | I3 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A0F2H-A0F3H | 41202-41203 | I3 63rd Harmonic Amplitude | THD= Rx/100 | Float | R

## Class S - 10min Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship |  | Data Type | Access Property
|  |  | Primary | Secondary
96E9H-96EAH | 38633-38634 | Frequency | F=Rx | F=Rx | Float | R
96EBH-96ECH | 38635-38636 | Phase A Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
96EDH-96EEH | 38637-38638 | Phase B Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
96EFH-96F0H | 38639-38640 | Phase C Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
96F1H-96F2H | 38641-38642 | Line Voltage AB | U=Rx | U=PT1/PT2 | Float | R
96F3H-96F4H | 38643-38644 | Line Voltage BC | U=Rx | U=PT1/PT2 | Float | R
96F5H-96F6H | 38645-38646 | Line Voltage CA | U=Rx | U=PT1/PT2 | Float | R
96F7H-96F8H | 38647-38648 | Average Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
96F9H-96FAH | 38649-38650 | Average Line-Line Voltage | U=Rx | U=PT1/PT2 | Float | R
96FBH-96FCH | 38651-38652 | Phase A Current | I=Rx | I=CT1/CT2 | Float | R
96FDH-96FEH | 38653-38654 | Phase B Current | I=Rx | I=CT1/CT2 | Float | R
96FFH-9700H | 38655-38656 | Phase C Current | I=Rx | I=CT1/CT2 | Float | R
9701H-9702H | 38657-38658 | Neutal Current | I=Rx | I=CT1/CT2 | Float | R
9703H-9704H | 38659-38660 | Average Current | I=Rx | I=CT1/CT2 | Float | R
9705H-9706H | 38661-38662 | Phase A (AB) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
9707H-9708H | 38663-38664 | Phase A (AB) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9709H-970AH | 38665-38666 | Phase A (AB) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
970BH-970CH | 38667-38668 | RESERVED |  |  | Float | R
970DH-970EH | 38669-38670 | Phase B (BC) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
970FH-9710H | 38671-38672 | Phase B (BC) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9711H-9712H | 38673-38674 | Phase B (BC) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9713H-9714H | 38675-38676 | RESERVED |  |  | Float | R
9715H-9716H | 38677-38678 | Phase C (CA) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
9717H-9718H | 38679-38680 | Phase C (CA) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9719H-971AH | 38681-38682 | Phase C (CA) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
971BH-971CH | 38683-38684 | RESERVED |  |  | Float | R
971DH-971EH | 38685-38686 | Phase A Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
971FH-9720H | 38687-38688 | Phase A Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9721H-9722H | 38689-38690 | Phase A Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9723H-9724H | 38691-38692 | RESERVED |  |  | Float | R
9725H-9726H | 38693-38694 | Phase B Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
9727H-9728H | 38695-38696 | Phase B Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9729H-972AH | 38697-38698 | Phase B Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
972BH-972CH | 38699-38700 | RESERVED |  |  | Float | R
972DH-972EH | 38701-38702 | Phase C Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
972FH-9730H | 38703-38704 | Phase C Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
9731H-9732H | 38705-38706 | Phase C Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
9733H-9734H | 38707-38708 | RESERVED |  |  | Float | R
9735H-9736H | 38709-38710 | Voltage Unbalance Factor | Uunb=Rx/100 | Uunb=Rx/100 | Float | R
9737H-9738H | 38711-38712 | Voltage Zero Unbalance Factor | Iunb=Rx/100 | Iunb=Rx/100 | Float | R
9739H-973AH | 38713-38714 | Voltage Zero Sequence (Real) | V=Rx | V=Rx | Float | R
973BH-973CH | 38715-38716 | Voltage Zero Sequence (Imaginary) | V=Rx | V=Rx | Float | R
973DH-973EH | 38717-38718 | Voltage Positive Sequence (Real) | V=Rx | V=Rx | Float | R
973FH-9740H | 38719-38720 | Voltage Positive Sequence (Imaginary) | V=Rx | V=Rx | Float | R
9741H-9742H | 38721-38722 | Voltage Negative Sequence (Real) | V=Rx | V=Rx | Float | R
9743H-9744H | 38723-38724 | Voltage Negative Sequence (Imaginary) | V=Rx | V=Rx | Float | R
9745H-9746H | 38725-38726 | Current Unbalance Factor | I=Rx | I=Rx | Float | R
9747H-9748H | 38727-38728 | Current Zero Unbalance Factor | I=Rx | I=Rx | Float | R
9749H-974AH | 38729-38730 | Current Zero Sequence (Real) | I=Rx | I=Rx | Float | R
974BH-974CH | 38731-38732 | Current Zero Sequence (Imaginary) | I=Rx | I=Rx | Float | R
974DH-974EH | 38733-38734 | Current Positive Sequence (Real) | I=Rx | I=Rx | Float | R
974FH-9750H | 38735-38736 | Current Positive Sequence (Imaginary) | I=Rx | I=Rx | Float | R
9751H-9752H | 38737-38738 | Current Negative Sequence (Real) | I=Rx | I=Rx | Float | R
9753H-9754H | 38739-38740 | Current Negative Sequence (Imaginary) | I=Rx | I=Rx | Float | R

## 10min Harmonic Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Data Type | Access Property
V1(V12)
A0F4H | 41204 | V1(V12) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A0F5H | 41205 | V1(V12) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A0F6H | 41206 | V1(V12) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A0F7H | 41207 | V1(V12) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0F8H | 41208 | V1(V12) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0F9H | 41209 | V1(V12) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FAH | 41210 | V1(V12) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FBH | 41211 | V1(V12) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FCH | 41212 | V1(V12) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FDH | 41213 | V1(V12) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FEH | 41214 | V1(V12) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A0FFH | 41215 | V1(V12) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A100H | 41216 | V1(V12) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A101H | 41217 | V1(V12) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A102H | 41218 | V1(V12) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A103H | 41219 | V1(V12) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A104H | 41220 | V1(V12) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A105H | 41221 | V1(V12) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A106H | 41222 | V1(V12) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A107H | 41223 | V1(V12) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A108H | 41224 | V1(V12) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A109H | 41225 | V1(V12) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A10AH | 41226 | V1(V12) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A10BH | 41227 | V1(V12) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A10CH | 41228 | V1(V12) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A10DH | 41229 | V1(V12) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A10EH | 41230 | V1(V12) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A10FH | 41231 | V1(V12) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A110H | 41232 | V1(V12) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A111H | 41233 | V1(V12) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A112H | 41234 | V1(V12) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A113H | 41235 | V1(V12) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A114H | 41236 | V1(V12) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A115H | 41237 | V1(V12) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A116H | 41238 | V1(V12) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A117H | 41239 | V1(V12) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A118H | 41240 | V1(V12) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A119H | 41241 | V1(V12) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A11AH | 41242 | V1(V12) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A11BH | 41243 | V1(V12) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A11CH | 41244 | V1(V12) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A11DH | 41245 | V1(V12) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A11EH | 41246 | V1(V12) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A11FH | 41247 | V1(V12) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A120H | 41248 | V1(V12) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A121H | 41249 | V1(V12) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A122H | 41250 | V1(V12) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A123H | 41251 | V1(V12) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A124H | 41252 | V1(V12) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A125H | 41253 | V1(V12) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A126H | 41254 | V1(V12) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A127H | 41255 | V1(V12) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A128H | 41256 | V1(V12) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A129H | 41257 | V1(V12) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12AH | 41258 | V1(V12) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12BH | 41259 | V1(V12) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12CH | 41260 | V1(V12) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12DH | 41261 | V1(V12) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12EH | 41262 | V1(V12) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A12FH | 41263 | V1(V12) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A130H | 41264 | V1(V12) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A131H | 41265 | V1(V12) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A132H | 41266 | V1(V12) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A133H | 41267 | RESERVED |  | Word | R
A134H-A135H | 41268-41269 | V1(V12) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A136H-A137H | 41270-41271 | V1(V12) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A138H-A139H | 41272-41273 | V1(V12) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A13AH-A13BH | 41274-41275 | V1(V12) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A13CH-A13DH | 41276-41277 | V1(V12) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A13EH-A13FH | 41278-41279 | V1(V12) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A140H-A141H | 41280-41281 | V1(V12) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A142H-A143H | 41282-41283 | V1(V12) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A144H-A145H | 41284-41285 | V1(V12) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A146H-A147H | 41286-41287 | V1(V12) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A148H-A149H | 41288-41289 | V1(V12) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A14AH-A14BH | 41290-41291 | V1(V12) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A14CH-A14DH | 41292-41293 | V1(V12) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A14EH-A14FH | 41294-41295 | V1(V12) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A150H-A151H | 41296-41297 | V1(V12) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A152H-A153H | 41298-41299 | V1(V12) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A154H-A155H | 41300-41301 | V1(V12) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A156H-A157H | 41302-41303 | V1(V12) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A158H-A159H | 41304-41305 | V1(V12) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A15AH-A15BH | 41306-41307 | V1(V12) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A15CH-A15DH | 41308-41309 | V1(V12) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A15EH-A15FH | 41310-41311 | V1(V12) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A160H-A161H | 41312-41313 | V1(V12) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A162H-A163H | 41314-41315 | V1(V12) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A164H-A165H | 41316-41317 | V1(V12) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A166H-A167H | 41318-41319 | V1(V12) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A168H-A169H | 41320-41321 | V1(V12) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A16AH-A16BH | 41322-41323 | V1(V12) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A16CH-A16DH | 41324-41325 | V1(V12) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A16EH-A16FH | 41326-41327 | V1(V12) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A170H-A171H | 41328-41329 | V1(V12) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A172H-A173H | 41330-41331 | V1(V12) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A174H-A175H | 41332-41333 | V1(V12) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A176H-A177H | 41334-41335 | V1(V12) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A178H-A179H | 41336-41337 | V1(V12) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A17AH-A17BH | 41338-41339 | V1(V12) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A17CH-A17DH | 41340-41341 | V1(V12) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A17EH-A17FH | 41342-41343 | V1(V12) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A180H-A181H | 41344-41345 | V1(V12) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A182H-A183H | 41346-41347 | V1(V12) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A184H-A185H | 41348-41349 | V1(V12) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A186H-A187H | 41350-41351 | V1(V12) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A188H-A189H | 41352-41353 | V1(V12) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A18AH-A18BH | 41354-41355 | V1(V12) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A18CH-A18DH | 41356-41357 | V1(V12) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A18EH-A18FH | 41358-41359 | V1(V12) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A190H-A191H | 41360-41361 | V1(V12) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A192H-A193H | 41362-41363 | V1(V12) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A194H-A195H | 41364-41365 | V1(V12) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A196H-A197H | 41366-41367 | V1(V12) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A198H-A199H | 41368-41369 | V1(V12) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A19AH-A19BH | 41370-41371 | V1(V12) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A19CH-A19DH | 41372-41373 | V1(V12) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A19EH-A19FH | 41374-41375 | V1(V12) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A1A0H-A1A1H | 41376-41377 | V1(V12) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A1A2H-A1A3H | 41378-41379 | V1(V12) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A1A4H-A1A5H | 41380-41381 | V1(V12) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A1A6H-A1A7H | 41382-41383 | V1(V12) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A1A8H-A1A9H | 41384-41385 | V1(V12) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A1AAH-A1ABH | 41386-41387 | V1(V12) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A1ACH-A1ADH | 41388-41389 | V1(V12) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A1AEH-A1AFH | 41390-41391 | V1(V12) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A1B0H-A1B1H | 41392-41393 | V1(V12) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V2(V23)
A1B2H | 41394 | V2(V23) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B3H | 41395 | V2(V23) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B4H | 41396 | V2(V23) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B5H | 41397 | V2(V23) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B6H | 41398 | V2(V23) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B7H | 41399 | V2(V23) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B8H | 41400 | V2(V23) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1B9H | 41401 | V2(V23) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BAH | 41402 | V2(V23) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BBH | 41403 | V2(V23) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BCH | 41404 | V2(V23) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BDH | 41405 | V2(V23) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BEH | 41406 | V2(V23) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1BFH | 41407 | V2(V23) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C0H | 41408 | V2(V23) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C1H | 41409 | V2(V23) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C2H | 41410 | V2(V23) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C3H | 41411 | V2(V23) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C4H | 41412 | V2(V23) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C5H | 41413 | V2(V23) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C6H | 41414 | V2(V23) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C7H | 41415 | V2(V23) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C8H | 41416 | V2(V23) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1C9H | 41417 | V2(V23) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CAH | 41418 | V2(V23) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CBH | 41419 | V2(V23) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CCH | 41420 | V2(V23) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CDH | 41421 | V2(V23) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CEH | 41422 | V2(V23) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1CFH | 41423 | V2(V23) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D0H | 41424 | V2(V23) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D1H | 41425 | V2(V23) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D2H | 41426 | V2(V23) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D3H | 41427 | V2(V23) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D4H | 41428 | V2(V23) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D5H | 41429 | V2(V23) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D6H | 41430 | V2(V23) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D7H | 41431 | V2(V23) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D8H | 41432 | V2(V23) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1D9H | 41433 | V2(V23) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DAH | 41434 | V2(V23) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DBH | 41435 | V2(V23) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DCH | 41436 | V2(V23) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DDH | 41437 | V2(V23) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DEH | 41438 | V2(V23) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1DFH | 41439 | V2(V23) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E0H | 41440 | V2(V23) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E1H | 41441 | V2(V23) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E2H | 41442 | V2(V23) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E3H | 41443 | V2(V23) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E4H | 41444 | V2(V23) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E5H | 41445 | V2(V23) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E6H | 41446 | V2(V23) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E7H | 41447 | V2(V23) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E8H | 41448 | V2(V23) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1E9H | 41449 | V2(V23) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1EAH | 41450 | V2(V23) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1EBH | 41451 | V2(V23) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1ECH | 41452 | V2(V23) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1EDH | 41453 | V2(V23) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A1EEH | 41454 | V2(V23) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A1EFH | 41455 | V2(V23) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1F0H | 41456 | V2(V23) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A1F1H | 41457 | RESERVED |  | Word | R
A1F2H-A1F3H | 41458-41459 | V2(V23) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A1F4H-A1F5H | 41460-41461 | V2(V23) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A1F6H-A1F7H | 41462-41463 | V2(V23) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A1F8H-A1F9H | 41464-41465 | V2(V23) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A1FAH-A1FBH | 41466-41467 | V2(V23) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A1FCH-A1FDH | 41468-41469 | V2(V23) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A1FEH-A1FFH | 41470-41471 | V2(V23) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A200H-A201H | 41472-41473 | V2(V23) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A202H-A203H | 41474-41475 | V2(V23) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A204H-A205H | 41476-41477 | V2(V23) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A206H-A207H | 41478-41479 | V2(V23) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A208H-A209H | 41480-41481 | V2(V23) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A20AH-A20BH | 41482-41483 | V2(V23) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A20CH-A20DH | 41484-41485 | V2(V23) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A20EH-A20FH | 41486-41487 | V2(V23) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A210H-A211H | 41488-41489 | V2(V23) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A212H-A213H | 41490-41491 | V2(V23) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A214H-A215H | 41492-41493 | V2(V23) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A216H-A217H | 41494-41495 | V2(V23) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A218H-A219H | 41496-41497 | V2(V23) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A21AH-A21BH | 41498-41499 | V2(V23) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A21CH-A21DH | 41500-41501 | V2(V23) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A21EH-A21FH | 41502-41503 | V2(V23) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A220H-A221H | 41504-41505 | V2(V23) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A222H-A223H | 41506-41507 | V2(V23) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A224H-A225H | 41508-41509 | V2(V23) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A226H-A227H | 41510-41511 | V2(V23) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A228H-A229H | 41512-41513 | V2(V23) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A22AH-A22BH | 41514-41515 | V2(V23) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A22CH-A22DH | 41516-41517 | V2(V23) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A22EH-A22FH | 41518-41519 | V2(V23) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A230H-A231H | 41520-41521 | V2(V23) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A232H-A233H | 41522-41523 | V2(V23) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A234H-A235H | 41524-41525 | V2(V23) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A236H-A237H | 41526-41527 | V2(V23) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A238H-A239H | 41528-41529 | V2(V23) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A23AH-A23BH | 41530-41531 | V2(V23) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A23CH-A23DH | 41532-41533 | V2(V23) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A23EH-A23FH | 41534-41535 | V2(V23) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A240H-A241H | 41536-41537 | V2(V23) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A242H-A243H | 41538-41539 | V2(V23) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A244H-A245H | 41540-41541 | V2(V23) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A246H-A247H | 41542-41543 | V2(V23) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A248H-A249H | 41544-41545 | V2(V23) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A24AH-A24BH | 41546-41547 | V2(V23) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A24CH-A24DH | 41548-41549 | V2(V23) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A24EH-A24FH | 41550-41551 | V2(V23) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A250H-A251H | 41552-41553 | V2(V23) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A252H-A253H | 41554-41555 | V2(V23) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A254H-A255H | 41556-41557 | V2(V23) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A256H-A257H | 41558-41559 | V2(V23) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A258H-A259H | 41560-41561 | V2(V23) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A25AH-A25BH | 41562-41563 | V2(V23) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A25CH-A25DH | 41564-41565 | V2(V23) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A25EH-A25FH | 41566-41567 | V2(V23) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A260H-A261H | 41568-41569 | V2(V23) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A262H-A263H | 41570-41571 | V2(V23) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A264H-A265H | 41572-41573 | V2(V23) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A266H-A267H | 41574-41575 | V2(V23) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A268H-A269H | 41576-41577 | V2(V23) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A26AH-A26BH | 41578-41579 | V2(V23) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A26CH-A26DH | 41580-41581 | V2(V23) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A26EH-A26FH | 41582-41583 | V2(V23) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V3(V31)
A270H | 41584 | V3(V31) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A271H | 41585 | V3(V31) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A272H | 41586 | V3(V31) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A273H | 41587 | V3(V31) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A274H | 41588 | V3(V31) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A275H | 41589 | V3(V31) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A276H | 41590 | V3(V31) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A277H | 41591 | V3(V31) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A278H | 41592 | V3(V31) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A279H | 41593 | V3(V31) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27AH | 41594 | V3(V31) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27BH | 41595 | V3(V31) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27CH | 41596 | V3(V31) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27DH | 41597 | V3(V31) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27EH | 41598 | V3(V31) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A27FH | 41599 | V3(V31) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A280H | 41600 | V3(V31) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A281H | 41601 | V3(V31) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A282H | 41602 | V3(V31) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A283H | 41603 | V3(V31) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A284H | 41604 | V3(V31) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A285H | 41605 | V3(V31) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A286H | 41606 | V3(V31) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A287H | 41607 | V3(V31) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A288H | 41608 | V3(V31) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A289H | 41609 | V3(V31) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A28AH | 41610 | V3(V31) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A28BH | 41611 | V3(V31) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A28CH | 41612 | V3(V31) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A28DH | 41613 | V3(V31) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A28EH | 41614 | V3(V31) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A28FH | 41615 | V3(V31) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A290H | 41616 | V3(V31) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A291H | 41617 | V3(V31) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A292H | 41618 | V3(V31) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A293H | 41619 | V3(V31) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A294H | 41620 | V3(V31) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A295H | 41621 | V3(V31) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A296H | 41622 | V3(V31) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A297H | 41623 | V3(V31) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A298H | 41624 | V3(V31) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A299H | 41625 | V3(V31) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A29AH | 41626 | V3(V31) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A29BH | 41627 | V3(V31) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A29CH | 41628 | V3(V31) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A29DH | 41629 | V3(V31) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A29EH | 41630 | V3(V31) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A29FH | 41631 | V3(V31) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A0H | 41632 | V3(V31) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A1H | 41633 | V3(V31) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A2H | 41634 | V3(V31) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A3H | 41635 | V3(V31) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A4H | 41636 | V3(V31) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A5H | 41637 | V3(V31) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A6H | 41638 | V3(V31) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A7H | 41639 | V3(V31) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A8H | 41640 | V3(V31) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2A9H | 41641 | V3(V31) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2AAH | 41642 | V3(V31) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2ABH | 41643 | V3(V31) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A2ACH | 41644 | V3(V31) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A2ADH | 41645 | V3(V31) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A2AEH | 41646 | V3(V31) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A2AFH | 41647 | RESERVED |  | Word | R
A2B0H-A2B1H | 41648-41649 | V3(V31) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A2B2H-A2B3H | 41650-41651 | V3(V31) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A2B4H-A2B5H | 41652-41653 | V3(V31) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A2B6H-A2B7H | 41654-41655 | V3(V31) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A2B8H-A2B9H | 41656-41657 | V3(V31) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A2BAH-A2BBH | 41658-41659 | V3(V31) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A2BCH-A2BDH | 41660-41661 | V3(V31) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A2BEH-A2BFH | 41662-41663 | V3(V31) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A2C0H-A2C1H | 41664-41665 | V3(V31) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A2C2H-A2C3H | 41666-41667 | V3(V31) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A2C4H-A2C5H | 41668-41669 | V3(V31) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A2C6H-A2C7H | 41670-41671 | V3(V31) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A2C8H-A2C9H | 41672-41673 | V3(V31) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A2CAH-A2CBH | 41674-41675 | V3(V31) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A2CCH-A2CDH | 41676-41677 | V3(V31) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A2CEH-A2CFH | 41678-41679 | V3(V31) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A2D0H-A2D1H | 41680-41681 | V3(V31) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A2D2H-A2D3H | 41682-41683 | V3(V31) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A2D4H-A2D5H | 41684-41685 | V3(V31) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A2D6H-A2D7H | 41686-41687 | V3(V31) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A2D8H-A2D9H | 41688-41689 | V3(V31) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A2DAH-A2DBH | 41690-41691 | V3(V31) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A2DCH-A2DDH | 41692-41693 | V3(V31) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A2DEH-A2DFH | 41694-41695 | V3(V31) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A2E0H-A2E1H | 41696-41697 | V3(V31) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A2E2H-A2E3H | 41698-41699 | V3(V31) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A2E4H-A2E5H | 41700-41701 | V3(V31) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A2E6H-A2E7H | 41702-41703 | V3(V31) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A2E8H-A2E9H | 41704-41705 | V3(V31) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A2EAH-A2EBH | 41706-41707 | V3(V31) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A2ECH-A2EDH | 41708-41709 | V3(V31) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A2EEH-A2EFH | 41710-41711 | V3(V31) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A2F0H-A2F1H | 41712-41713 | V3(V31) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A2F2H-A2F3H | 41714-41715 | V3(V31) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A2F4H-A2F5H | 41716-41717 | V3(V31) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A2F6H-A2F7H | 41718-41719 | V3(V31) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A2F8H-A2F9H | 41720-41721 | V3(V31) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A2FAH-A2FBH | 41722-41723 | V3(V31) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A2FCH-A2FDH | 41724-41725 | V3(V31) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A2FEH-A2FFH | 41726-41727 | V3(V31) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A300H-A301H | 41728-41729 | V3(V31) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A302H-A303H | 41730-41731 | V3(V31) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A304H-A305H | 41732-41733 | V3(V31) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A306H-A307H | 41734-41735 | V3(V31) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A308H-A309H | 41736-41737 | V3(V31) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A30AH-A30BH | 41738-41739 | V3(V31) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A30CH-A30DH | 41740-41741 | V3(V31) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A30EH-A30FH | 41742-41743 | V3(V31) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A310H-A311H | 41744-41745 | V3(V31) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A312H-A313H | 41746-41747 | V3(V31) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A314H-A315H | 41748-41749 | V3(V31) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A316H-A317H | 41750-41751 | V3(V31) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A318H-A319H | 41752-41753 | V3(V31) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A31AH-A31BH | 41754-41755 | V3(V31) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A31CH-A31DH | 41756-41757 | V3(V31) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A31EH-A31FH | 41758-41759 | V3(V31) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A320H-A321H | 41760-41761 | V3(V31) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A322H-A323H | 41762-41763 | V3(V31) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A324H-A325H | 41764-41765 | V3(V31) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A326H-A327H | 41766-41767 | V3(V31) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A328H-A329H | 41768-41769 | V3(V31) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A32AH-A32BH | 41770-41771 | V3(V31) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A32CH-A32DH | 41772-41773 | V3(V31) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase A Current
A32EH | 41774 | I1 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A32FH | 41775 | I1 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A330H | 41776 | I1 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A331H | 41777 | I1 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A332H | 41778 | I1 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A333H | 41779 | I1 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A334H | 41780 | I1 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A335H | 41781 | I1 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A336H | 41782 | I1 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A337H | 41783 | I1 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A338H | 41784 | I1 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A339H | 41785 | I1 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33AH | 41786 | I1 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33BH | 41787 | I1 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33CH | 41788 | I1 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33DH | 41789 | I1 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33EH | 41790 | I1 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A33FH | 41791 | I1 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A340H | 41792 | I1 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A341H | 41793 | I1 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A342H | 41794 | I1 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A343H | 41795 | I1 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A344H | 41796 | I1 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A345H | 41797 | I1 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A346H | 41798 | I1 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A347H | 41799 | I1 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A348H | 41800 | I1 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A349H | 41801 | I1 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A34AH | 41802 | I1 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A34BH | 41803 | I1 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A34CH | 41804 | I1 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A34DH | 41805 | I1 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A34EH | 41806 | I1 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A34FH | 41807 | I1 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A350H | 41808 | I1 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A351H | 41809 | I1 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A352H | 41810 | I1 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A353H | 41811 | I1 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A354H | 41812 | I1 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A355H | 41813 | I1 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A356H | 41814 | I1 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A357H | 41815 | I1 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A358H | 41816 | I1 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A359H | 41817 | I1 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35AH | 41818 | I1 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35BH | 41819 | I1 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35CH | 41820 | I1 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35DH | 41821 | I1 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35EH | 41822 | I1 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A35FH | 41823 | I1 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A360H | 41824 | I1 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A361H | 41825 | I1 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A362H | 41826 | I1 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A363H | 41827 | I1 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A364H | 41828 | I1 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A365H | 41829 | I1 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A366H | 41830 | I1 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A367H | 41831 | I1 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A368H | 41832 | I1 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A369H | 41833 | I1 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A36AH | 41834 | I1 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A36BH | 41835 | I1 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A36CH | 41836 | I1 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A36DH | 41837 | RESERVED |  | Word | R
A36EH-A36FH | 41838-41839 | I1 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A370H-A371H | 41840-41841 | I1 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A372H-A373H | 41842-41843 | I1 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A374H-A375H | 41844-41845 | I1 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A376H-A377H | 41846-41847 | I1 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A378H-A379H | 41848-41849 | I1 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A37AH-A37BH | 41850-41851 | I1 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A37CH-A37DH | 41852-41853 | I1 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A37EH-A37FH | 41854-41855 | I1 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A380H-A381H | 41856-41857 | I1 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A382H-A383H | 41858-41859 | I1 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A384H-A385H | 41860-41861 | I1 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A386H-A387H | 41862-41863 | I1 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A388H-A389H | 41864-41865 | I1 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A38AH-A38BH | 41866-41867 | I1 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A38CH-A38DH | 41868-41869 | I1 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A38EH-A38FH | 41870-41871 | I1 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A390H-A391H | 41872-41873 | I1 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A392H-A393H | 41874-41875 | I1 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A394H-A395H | 41876-41877 | I1 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A396H-A397H | 41878-41879 | I1 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A398H-A399H | 41880-41881 | I1 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A39AH-A39BH | 41882-41883 | I1 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A39CH-A39DH | 41884-41885 | I1 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A39EH-A39FH | 41886-41887 | I1 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A3A0H-A3A1H | 41888-41889 | I1 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A3A2H-A3A3H | 41890-41891 | I1 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A3A4H-A3A5H | 41892-41893 | I1 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A3A6H-A3A7H | 41894-41895 | I1 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A3A8H-A3A9H | 41896-41897 | I1 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A3AAH-A3ABH | 41898-41899 | I1 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A3ACH-A3ADH | 41900-41901 | I1 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A3AEH-A3AFH | 41902-41903 | I1 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A3B0H-A3B1H | 41904-41905 | I1 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A3B2H-A3B3H | 41906-41907 | I1 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A3B4H-A3B5H | 41908-41909 | I1 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A3B6H-A3B7H | 41910-41911 | I1 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A3B8H-A3B9H | 41912-41913 | I1 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A3BAH-A3BBH | 41914-41915 | I1 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A3BCH-A3BDH | 41916-41917 | I1 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A3BEH-A3BFH | 41918-41919 | I1 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A3C0H-A3C1H | 41920-41921 | I1 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A3C2H-A3C3H | 41922-41923 | I1 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A3C4H-A3C5H | 41924-41925 | I1 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A3C6H-A3C7H | 41926-41927 | I1 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A3C8H-A3C9H | 41928-41929 | I1 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A3CAH-A3CBH | 41930-41931 | I1 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A3CCH-A3CDH | 41932-41933 | I1 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A3CEH-A3CFH | 41934-41935 | I1 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A3D0H-A3D1H | 41936-41937 | I1 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A3D2H-A3D3H | 41938-41939 | I1 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A3D4H-A3D5H | 41940-41941 | I1 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A3D6H-A3D7H | 41942-41943 | I1 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A3D8H-A3D9H | 41944-41945 | I1 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A3DAH-A3DBH | 41946-41947 | I1 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A3DCH-A3DDH | 41948-41949 | I1 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A3DEH-A3DFH | 41950-41951 | I1 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A3E0H-A3E1H | 41952-41953 | I1 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A3E2H-A3E3H | 41954-41955 | I1 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A3E4H-A3E5H | 41956-41957 | I1 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A3E6H-A3E7H | 41958-41959 | I1 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A3E8H-A3E9H | 41960-41961 | I1 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A3EAH-A3EBH | 41962-41963 | I1 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase B Current
A3ECH | 41964 | I2 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A3EDH | 41965 | I2 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A3EEH | 41966 | I2 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A3EFH | 41967 | I2 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F0H | 41968 | I2 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F1H | 41969 | I2 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F2H | 41970 | I2 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F3H | 41971 | I2 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F4H | 41972 | I2 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F5H | 41973 | I2 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F6H | 41974 | I2 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F7H | 41975 | I2 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F8H | 41976 | I2 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3F9H | 41977 | I2 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FAH | 41978 | I2 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FBH | 41979 | I2 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FCH | 41980 | I2 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FDH | 41981 | I2 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FEH | 41982 | I2 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A3FFH | 41983 | I2 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A400H | 41984 | I2 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A401H | 41985 | I2 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A402H | 41986 | I2 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A403H | 41987 | I2 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A404H | 41988 | I2 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A405H | 41989 | I2 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A406H | 41990 | I2 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A407H | 41991 | I2 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A408H | 41992 | I2 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A409H | 41993 | I2 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A40AH | 41994 | I2 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A40BH | 41995 | I2 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A40CH | 41996 | I2 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A40DH | 41997 | I2 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A40EH | 41998 | I2 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A40FH | 41999 | I2 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A410H | 42000 | I2 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A411H | 42001 | I2 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A412H | 42002 | I2 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A413H | 42003 | I2 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A414H | 42004 | I2 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A415H | 42005 | I2 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A416H | 42006 | I2 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A417H | 42007 | I2 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A418H | 42008 | I2 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A419H | 42009 | I2 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A41AH | 42010 | I2 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A41BH | 42011 | I2 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A41CH | 42012 | I2 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A41DH | 42013 | I2 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A41EH | 42014 | I2 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A41FH | 42015 | I2 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A420H | 42016 | I2 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A421H | 42017 | I2 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A422H | 42018 | I2 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A423H | 42019 | I2 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A424H | 42020 | I2 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A425H | 42021 | I2 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A426H | 42022 | I2 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A427H | 42023 | I2 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A428H | 42024 | I2 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A429H | 42025 | I2 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A42AH | 42026 | I2 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A42BH | 42027 | RESERVED |  | Word | R
A42CH-A42DH | 42028-42029 | I2 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A42EH-A42FH | 42030-42031 | I2 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A430H-A431H | 42032-42033 | I2 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A432H-A433H | 42034-42035 | I2 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A434H-A435H | 42036-42037 | I2 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A436H-A437H | 42038-42039 | I2 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A438H-A439H | 42040-42041 | I2 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A43AH-A43BH | 42042-42043 | I2 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A43CH-A43DH | 42044-42045 | I2 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A43EH-A43FH | 42046-42047 | I2 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A440H-A441H | 42048-42049 | I2 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A442H-A443H | 42050-42051 | I2 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A444H-A445H | 42052-42053 | I2 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A446H-A447H | 42054-42055 | I2 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A448H-A449H | 42056-42057 | I2 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A44AH-A44BH | 42058-42059 | I2 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A44CH-A44DH | 42060-42061 | I2 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A44EH-A44FH | 42062-42063 | I2 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A450H-A451H | 42064-42065 | I2 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A452H-A453H | 42066-42067 | I2 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A454H-A455H | 42068-42069 | I2 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A456H-A457H | 42070-42071 | I2 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A458H-A459H | 42072-42073 | I2 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A45AH-A45BH | 42074-42075 | I2 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A45CH-A45DH | 42076-42077 | I2 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A45EH-A45FH | 42078-42079 | I2 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A460H-A461H | 42080-42081 | I2 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A462H-A463H | 42082-42083 | I2 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A464H-A465H | 42084-42085 | I2 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A466H-A467H | 42086-42087 | I2 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A468H-A469H | 42088-42089 | I2 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A46AH-A46BH | 42090-42091 | I2 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A46CH-A46DH | 42092-42093 | I2 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A46EH-A46FH | 42094-42095 | I2 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A470H-A471H | 42096-42097 | I2 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A472H-A473H | 42098-42099 | I2 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A474H-A475H | 42100-42101 | I2 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A476H-A477H | 42102-42103 | I2 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A478H-A479H | 42104-42105 | I2 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A47AH-A47BH | 42106-42107 | I2 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A47CH-A47DH | 42108-42109 | I2 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A47EH-A47FH | 42110-42111 | I2 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A480H-A481H | 42112-42113 | I2 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A482H-A483H | 42114-42115 | I2 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A484H-A485H | 42116-42117 | I2 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A486H-A487H | 42118-42119 | I2 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A488H-A489H | 42120-42121 | I2 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A48AH-A48BH | 42122-42123 | I2 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A48CH-A48DH | 42124-42125 | I2 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A48EH-A48FH | 42126-42127 | I2 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A490H-A491H | 42128-42129 | I2 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A492H-A493H | 42130-42131 | I2 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A494H-A495H | 42132-42133 | I2 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A496H-A497H | 42134-42135 | I2 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A498H-A499H | 42136-42137 | I2 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A49AH-A49BH | 42138-42139 | I2 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A49CH-A49DH | 42140-42141 | I2 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A49EH-A49FH | 42142-42143 | I2 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A4A0H-A4A1H | 42144-42145 | I2 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A4A2H-A4A3H | 42146-42147 | I2 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A4A4H-A4A5H | 42148-42149 | I2 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A4A6H-A4A7H | 42150-42151 | I2 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A4A8H-A4A9H | 42152-42153 | I2 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase C Current
A4AAH | 42154 | I3 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4ABH | 42155 | I3 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4ACH | 42156 | I3 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4ADH | 42157 | I3 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4AEH | 42158 | I3 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4AFH | 42159 | I3 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B0H | 42160 | I3 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B1H | 42161 | I3 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B2H | 42162 | I3 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B3H | 42163 | I3 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B4H | 42164 | I3 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B5H | 42165 | I3 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B6H | 42166 | I3 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B7H | 42167 | I3 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B8H | 42168 | I3 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4B9H | 42169 | I3 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BAH | 42170 | I3 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BBH | 42171 | I3 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BCH | 42172 | I3 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BDH | 42173 | I3 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BEH | 42174 | I3 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4BFH | 42175 | I3 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C0H | 42176 | I3 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C1H | 42177 | I3 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C2H | 42178 | I3 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C3H | 42179 | I3 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C4H | 42180 | I3 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C5H | 42181 | I3 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C6H | 42182 | I3 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C7H | 42183 | I3 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C8H | 42184 | I3 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4C9H | 42185 | I3 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CAH | 42186 | I3 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CBH | 42187 | I3 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CCH | 42188 | I3 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CDH | 42189 | I3 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CEH | 42190 | I3 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4CFH | 42191 | I3 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D0H | 42192 | I3 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D1H | 42193 | I3 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D2H | 42194 | I3 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D3H | 42195 | I3 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D4H | 42196 | I3 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D5H | 42197 | I3 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D6H | 42198 | I3 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D7H | 42199 | I3 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D8H | 42200 | I3 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4D9H | 42201 | I3 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DAH | 42202 | I3 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DBH | 42203 | I3 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DCH | 42204 | I3 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DDH | 42205 | I3 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DEH | 42206 | I3 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4DFH | 42207 | I3 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E0H | 42208 | I3 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E1H | 42209 | I3 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E2H | 42210 | I3 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E3H | 42211 | I3 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E4H | 42212 | I3 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E5H | 42213 | I3 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E6H | 42214 | I3 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E7H | 42215 | I3 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E8H | 42216 | I3 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A4E9H | 42217 | RESERVED |  | Word | R
A4EAH-A4EBH | 42218-42219 | I3 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A4ECH-A4EDH | 42220-42221 | I3 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A4EEH-A4EFH | 42222-42223 | I3 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A4F0H-A4F1H | 42224-42225 | I3 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A4F2H-A4F3H | 42226-42227 | I3 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A4F4H-A4F5H | 42228-42229 | I3 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A4F6H-A4F7H | 42230-42231 | I3 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A4F8H-A4F9H | 42232-42233 | I3 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A4FAH-A4FBH | 42234-42235 | I3 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A4FCH-A4FDH | 42236-42237 | I3 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A4FEH-A4FFH | 42238-42239 | I3 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A500H-A501H | 42240-42241 | I3 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A502H-A503H | 42242-42243 | I3 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A504H-A505H | 42244-42245 | I3 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A506H-A507H | 42246-42247 | I3 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A508H-A509H | 42248-42249 | I3 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A50AH-A50BH | 42250-42251 | I3 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A50CH-A50DH | 42252-42253 | I3 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A50EH-A50FH | 42254-42255 | I3 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A510H-A511H | 42256-42257 | I3 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A512H-A513H | 42258-42259 | I3 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A514H-A515H | 42260-42261 | I3 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A516H-A517H | 42262-42263 | I3 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A518H-A519H | 42264-42265 | I3 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A51AH-A51BH | 42266-42267 | I3 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A51CH-A51DH | 42268-42269 | I3 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A51EH-A51FH | 42270-42271 | I3 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A520H-A521H | 42272-42273 | I3 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A522H-A523H | 42274-42275 | I3 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A524H-A525H | 42276-42277 | I3 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A526H-A527H | 42278-42279 | I3 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A528H-A529H | 42280-42281 | I3 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A52AH-A52BH | 42282-42283 | I3 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A52CH-A52DH | 42284-42285 | I3 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A52EH-A52FH | 42286-42287 | I3 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A530H-A531H | 42288-42289 | I3 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A532H-A533H | 42290-42291 | I3 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A534H-A535H | 42292-42293 | I3 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A536H-A537H | 42294-42295 | I3 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A538H-A539H | 42296-42297 | I3 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A53AH-A53BH | 42298-42299 | I3 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A53CH-A53DH | 42300-42301 | I3 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A53EH-A53FH | 42302-42303 | I3 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A540H-A541H | 42304-42305 | I3 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A542H-A543H | 42306-42307 | I3 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A544H-A545H | 42308-42309 | I3 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A546H-A547H | 42310-42311 | I3 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A548H-A549H | 42312-42313 | I3 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A54AH-A54BH | 42314-42315 | I3 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A54CH-A54DH | 42316-42317 | I3 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A54EH-A54FH | 42318-42319 | I3 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A550H-A551H | 42320-42321 | I3 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A552H-A553H | 42322-42323 | I3 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A554H-A555H | 42324-42325 | I3 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A556H-A557H | 42326-42327 | I3 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A558H-A559H | 42328-42329 | I3 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A55AH-A55BH | 42330-42331 | I3 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A55CH-A55DH | 42332-42333 | I3 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A55EH-A55FH | 42334-42335 | I3 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A560H-A561H | 42336-42337 | I3 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A562H-A563H | 42338-42339 | I3 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A564H-A565H | 42340-42341 | I3 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A566H-A567H | 42342-42343 | I3 63rd Harmonic Amplitude | THD= Rx/100 | Float | R

## Class S - 2h Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship |  | Data Type | Access Property
|  |  | Primary | Secondary
9780H-9781H | 38784-38785 | Frequency | F=Rx | F=Rx | Float | R
9782H-9783H | 38786-38787 | Phase A Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9784H-9785H | 38788-38789 | Phase B Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9786H-9787H | 38790-38791 | Phase C Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9788H-9789H | 38792-38793 | Line Voltage AB | U=Rx | U=PT1/PT2 | Float | R
978AH-978BH | 38794-38795 | Line Voltage BC | U=Rx | U=PT1/PT2 | Float | R
978CH-978DH | 38796-38797 | Line Voltage CA | U=Rx | U=PT1/PT2 | Float | R
978EH-978FH | 38798-38799 | Average Line-Neutral Voltage | U=Rx | U=PT1/PT2 | Float | R
9790H-9791H | 38800-38801 | Average Line-Line Voltage | U=Rx | U=PT1/PT2 | Float | R
9792H-9793H | 38802-38803 | Phase A Current | I=Rx | I=CT1/CT2 | Float | R
9794H-9795H | 38804-38805 | Phase B Current | I=Rx | I=CT1/CT2 | Float | R
9796H-9797H | 38806-38807 | Phase C Current | I=Rx | I=CT1/CT2 | Float | R
9798H-9799H | 38808-38809 | Neutal Current | I=Rx | I=CT1/CT2 | Float | R
979AH-979BH | 38810-38811 | Average Current | I=Rx | I=CT1/CT2 | Float | R
979CH-979DH | 38812-38813 | Phase A (AB) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
979EH-979FH | 38814-38815 | Phase A (AB) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97A0H-97A1H | 38816-38817 | Phase A (AB) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97A2H-97A3H | 38818-38819 | RESERVED |  |  | Float | R
97A4H-97A5H | 38820-38821 | Phase B (BC) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
97A6H-97A7H | 38822-38823 | Phase B (BC) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97A8H-97A9H | 38824-38825 | Phase B (BC) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97AAH-97ABH | 38826-38827 | RESERVED |  |  | Float | R
97ACH-97ADH | 38828-38829 | Phase C (CA) Voltage THD | THD=Rx/100 | THD=Rx/100 | Float | R
97AEH-97AFH | 38830-38831 | Phase C (CA) Voltage ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97B0H-97B1H | 38832-38833 | Phase C (CA) Voltage EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97B2H-97B3H | 38834-38835 | RESERVED |  |  | Float | R
97B4H-97B5H | 38836-38837 | Phase A Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
97B6H-97B7H | 38838-38839 | Phase A Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97B8H-97B9H | 38840-38841 | Phase A Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97BAH-97BBH | 38842-38843 | RESERVED |  |  | Float | R
97BCH-97BDH | 38844-38845 | Phase B Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
97BEH-97BFH | 38846-38847 | Phase B Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97C0H-97C1H | 38848-38849 | Phase B Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97C2H-97C3H | 38850-38851 | RESERVED |  |  | Float | R
97C4H-97C5H | 38852-38853 | Phase C Current THD | THD=Rx/100 | THD=Rx/100 | Float | R
97C6H-97C7H | 38854-38855 | Phase C Current ODD THD | THD=Rx/100 | THD=Rx/100 | Float | R
97C8H-97C9H | 38856-38857 | Phase C Current EVEN THD | THD=Rx/100 | THD=Rx/100 | Float | R
97CAH-97CBH | 38858-38859 | RESERVED |  |  | Float | R
97CCH-97CDH | 38860-38861 | Voltage Unbalance Factor | Uunb=Rx/100 | Uunb=Rx/100 | Float | R
97CEH-97CFH | 38862-38863 | Voltage Zero Unbalance Factor | Iunb=Rx/100 | Iunb=Rx/100 | Float | R
97D0H-97D1H | 38864-38865 | Voltage Zero Sequence (Real) | V=Rx | V=Rx | Float | R
97D2H-97D3H | 38866-38867 | Voltage Zero Sequence (Imaginary) | V=Rx | V=Rx | Float | R
97D4H-97D5H | 38868-38869 | Voltage Positive Sequence (Real) | V=Rx | V=Rx | Float | R
97D6H-97D7H | 38870-38871 | Voltage Positive Sequence (Imaginary) | V=Rx | V=Rx | Float | R
97D8H-97D9H | 38872-38873 | Voltage Negative Sequence (Real) | V=Rx | V=Rx | Float | R
97DAH-97DBH | 38874-38875 | Voltage Negative Sequence (Imaginary) | V=Rx | V=Rx | Float | R
97DCH-97DDH | 38876-38877 | Current Unbalance Factor | I=Rx | I=Rx | Float | R
97DEH-97DFH | 38878-38879 | Current Zero Unbalance Factor | I=Rx | I=Rx | Float | R
97E0H-97E1H | 38880-38881 | Current Zero Sequence (Real) | I=Rx | I=Rx | Float | R
97E2H-97E3H | 38882-38883 | Current Zero Sequence (Imaginary) | I=Rx | I=Rx | Float | R
97E4H-97E5H | 38884-38885 | Current Positive Sequence (Real) | I=Rx | I=Rx | Float | R
97E6H-97E7H | 38886-38887 | Current Positive Sequence (Imaginary) | I=Rx | I=Rx | Float | R
97E8H-97E9H | 38888-38889 | Current Negative Sequence (Real) | I=Rx | I=Rx | Float | R
97EAH-97EBH | 38890-38891 | Current Negative Sequence (Imaginary) | I=Rx | I=Rx | Float | R

## 2h Harmonic Aggreation
Basic Measurements: 03H Read
Address (Hex) | Address (Dec) | Parameter | Relationship | Data Type | Access Property
V1(V12)
A568H | 42344 | V1(V12) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A569H | 42345 | V1(V12) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A56AH | 42346 | V1(V12) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A56BH | 42347 | V1(V12) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A56CH | 42348 | V1(V12) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A56DH | 42349 | V1(V12) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A56EH | 42350 | V1(V12) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A56FH | 42351 | V1(V12) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A570H | 42352 | V1(V12) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A571H | 42353 | V1(V12) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A572H | 42354 | V1(V12) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A573H | 42355 | V1(V12) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A574H | 42356 | V1(V12) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A575H | 42357 | V1(V12) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A576H | 42358 | V1(V12) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A577H | 42359 | V1(V12) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A578H | 42360 | V1(V12) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A579H | 42361 | V1(V12) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A57AH | 42362 | V1(V12) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A57BH | 42363 | V1(V12) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A57CH | 42364 | V1(V12) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A57DH | 42365 | V1(V12) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A57EH | 42366 | V1(V12) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A57FH | 42367 | V1(V12) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A580H | 42368 | V1(V12) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A581H | 42369 | V1(V12) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A582H | 42370 | V1(V12) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A583H | 42371 | V1(V12) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A584H | 42372 | V1(V12) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A585H | 42373 | V1(V12) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A586H | 42374 | V1(V12) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A587H | 42375 | V1(V12) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A588H | 42376 | V1(V12) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A589H | 42377 | V1(V12) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58AH | 42378 | V1(V12) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58BH | 42379 | V1(V12) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58CH | 42380 | V1(V12) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58DH | 42381 | V1(V12) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58EH | 42382 | V1(V12) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A58FH | 42383 | V1(V12) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A590H | 42384 | V1(V12) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A591H | 42385 | V1(V12) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A592H | 42386 | V1(V12) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A593H | 42387 | V1(V12) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A594H | 42388 | V1(V12) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A595H | 42389 | V1(V12) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A596H | 42390 | V1(V12) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A597H | 42391 | V1(V12) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A598H | 42392 | V1(V12) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A599H | 42393 | V1(V12) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A59AH | 42394 | V1(V12) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A59BH | 42395 | V1(V12) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A59CH | 42396 | V1(V12) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A59DH | 42397 | V1(V12) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A59EH | 42398 | V1(V12) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A59FH | 42399 | V1(V12) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A0H | 42400 | V1(V12) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A1H | 42401 | V1(V12) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A2H | 42402 | V1(V12) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A3H | 42403 | V1(V12) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A4H | 42404 | V1(V12) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A5H | 42405 | V1(V12) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A6H | 42406 | V1(V12) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A5A7H | 42407 | RESERVED |  | Word | R
A5A8H-A5A9H | 42408-42409 | V1(V12) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A5AAH-A5ABH | 42410-42411 | V1(V12) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A5ACH-A5ADH | 42412-42413 | V1(V12) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A5AEH-A5AFH | 42414-42415 | V1(V12) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A5B0H-A5B1H | 42416-42417 | V1(V12) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A5B2H-A5B3H | 42418-42419 | V1(V12) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A5B4H-A5B5H | 42420-42421 | V1(V12) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A5B6H-A5B7H | 42422-42423 | V1(V12) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A5B8H-A5B9H | 42424-42425 | V1(V12) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A5BAH-A5BBH | 42426-42427 | V1(V12) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A5BCH-A5BDH | 42428-42429 | V1(V12) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A5BEH-A5BFH | 42430-42431 | V1(V12) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A5C0H-A5C1H | 42432-42433 | V1(V12) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A5C2H-A5C3H | 42434-42435 | V1(V12) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A5C4H-A5C5H | 42436-42437 | V1(V12) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A5C6H-A5C7H | 42438-42439 | V1(V12) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A5C8H-A5C9H | 42440-42441 | V1(V12) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A5CAH-A5CBH | 42442-42443 | V1(V12) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A5CCH-A5CDH | 42444-42445 | V1(V12) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A5CEH-A5CFH | 42446-42447 | V1(V12) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A5D0H-A5D1H | 42448-42449 | V1(V12) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A5D2H-A5D3H | 42450-42451 | V1(V12) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A5D4H-A5D5H | 42452-42453 | V1(V12) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A5D6H-A5D7H | 42454-42455 | V1(V12) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A5D8H-A5D9H | 42456-42457 | V1(V12) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A5DAH-A5DBH | 42458-42459 | V1(V12) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A5DCH-A5DDH | 42460-42461 | V1(V12) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A5DEH-A5DFH | 42462-42463 | V1(V12) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A5E0H-A5E1H | 42464-42465 | V1(V12) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A5E2H-A5E3H | 42466-42467 | V1(V12) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A5E4H-A5E5H | 42468-42469 | V1(V12) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A5E6H-A5E7H | 42470-42471 | V1(V12) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A5E8H-A5E9H | 42472-42473 | V1(V12) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A5EAH-A5EBH | 42474-42475 | V1(V12) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A5ECH-A5EDH | 42476-42477 | V1(V12) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A5EEH-A5EFH | 42478-42479 | V1(V12) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A5F0H-A5F1H | 42480-42481 | V1(V12) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A5F2H-A5F3H | 42482-42483 | V1(V12) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A5F4H-A5F5H | 42484-42485 | V1(V12) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A5F6H-A5F7H | 42486-42487 | V1(V12) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A5F8H-A5F9H | 42488-42489 | V1(V12) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A5FAH-A5FBH | 42490-42491 | V1(V12) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A5FCH-A5FDH | 42492-42493 | V1(V12) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A5FEH-A5FFH | 42494-42495 | V1(V12) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A600H-A601H | 42496-42497 | V1(V12) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A602H-A603H | 42498-42499 | V1(V12) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A604H-A605H | 42500-42501 | V1(V12) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A606H-A607H | 42502-42503 | V1(V12) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A608H-A609H | 42504-42505 | V1(V12) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A60AH-A60BH | 42506-42507 | V1(V12) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A60CH-A60DH | 42508-42509 | V1(V12) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A60EH-A60FH | 42510-42511 | V1(V12) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A610H-A611H | 42512-42513 | V1(V12) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A612H-A613H | 42514-42515 | V1(V12) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A614H-A615H | 42516-42517 | V1(V12) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A616H-A617H | 42518-42519 | V1(V12) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A618H-A619H | 42520-42521 | V1(V12) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A61AH-A61BH | 42522-42523 | V1(V12) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A61CH-A61DH | 42524-42525 | V1(V12) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A61EH-A61FH | 42526-42527 | V1(V12) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A620H-A621H | 42528-42529 | V1(V12) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A622H-A623H | 42530-42531 | V1(V12) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A624H-A625H | 42532-42533 | V1(V12) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V2(V23)
A626H | 42534 | V2(V23) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A627H | 42535 | V2(V23) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A628H | 42536 | V2(V23) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A629H | 42537 | V2(V23) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62AH | 42538 | V2(V23) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62BH | 42539 | V2(V23) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62CH | 42540 | V2(V23) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62DH | 42541 | V2(V23) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62EH | 42542 | V2(V23) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A62FH | 42543 | V2(V23) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A630H | 42544 | V2(V23) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A631H | 42545 | V2(V23) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A632H | 42546 | V2(V23) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A633H | 42547 | V2(V23) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A634H | 42548 | V2(V23) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A635H | 42549 | V2(V23) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A636H | 42550 | V2(V23) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A637H | 42551 | V2(V23) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A638H | 42552 | V2(V23) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A639H | 42553 | V2(V23) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A63AH | 42554 | V2(V23) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A63BH | 42555 | V2(V23) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A63CH | 42556 | V2(V23) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A63DH | 42557 | V2(V23) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A63EH | 42558 | V2(V23) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A63FH | 42559 | V2(V23) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A640H | 42560 | V2(V23) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A641H | 42561 | V2(V23) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A642H | 42562 | V2(V23) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A643H | 42563 | V2(V23) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A644H | 42564 | V2(V23) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A645H | 42565 | V2(V23) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A646H | 42566 | V2(V23) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A647H | 42567 | V2(V23) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A648H | 42568 | V2(V23) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A649H | 42569 | V2(V23) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A64AH | 42570 | V2(V23) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A64BH | 42571 | V2(V23) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A64CH | 42572 | V2(V23) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A64DH | 42573 | V2(V23) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A64EH | 42574 | V2(V23) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A64FH | 42575 | V2(V23) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A650H | 42576 | V2(V23) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A651H | 42577 | V2(V23) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A652H | 42578 | V2(V23) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A653H | 42579 | V2(V23) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A654H | 42580 | V2(V23) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A655H | 42581 | V2(V23) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A656H | 42582 | V2(V23) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A657H | 42583 | V2(V23) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A658H | 42584 | V2(V23) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A659H | 42585 | V2(V23) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A65AH | 42586 | V2(V23) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A65BH | 42587 | V2(V23) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A65CH | 42588 | V2(V23) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A65DH | 42589 | V2(V23) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A65EH | 42590 | V2(V23) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A65FH | 42591 | V2(V23) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A660H | 42592 | V2(V23) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A661H | 42593 | V2(V23) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A662H | 42594 | V2(V23) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A663H | 42595 | V2(V23) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A664H | 42596 | V2(V23) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A665H | 42597 | RESERVED |  | Word | R
A666H-A667H | 42598-42599 | V2(V23) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A668H-A669H | 42600-42601 | V2(V23) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A66AH-A66BH | 42602-42603 | V2(V23) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A66CH-A66DH | 42604-42605 | V2(V23) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A66EH-A66FH | 42606-42607 | V2(V23) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A670H-A671H | 42608-42609 | V2(V23) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A672H-A673H | 42610-42611 | V2(V23) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A674H-A675H | 42612-42613 | V2(V23) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A676H-A677H | 42614-42615 | V2(V23) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A678H-A679H | 42616-42617 | V2(V23) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A67AH-A67BH | 42618-42619 | V2(V23) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A67CH-A67DH | 42620-42621 | V2(V23) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A67EH-A67FH | 42622-42623 | V2(V23) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A680H-A681H | 42624-42625 | V2(V23) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A682H-A683H | 42626-42627 | V2(V23) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A684H-A685H | 42628-42629 | V2(V23) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A686H-A687H | 42630-42631 | V2(V23) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A688H-A689H | 42632-42633 | V2(V23) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A68AH-A68BH | 42634-42635 | V2(V23) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A68CH-A68DH | 42636-42637 | V2(V23) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A68EH-A68FH | 42638-42639 | V2(V23) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A690H-A691H | 42640-42641 | V2(V23) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A692H-A693H | 42642-42643 | V2(V23) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A694H-A695H | 42644-42645 | V2(V23) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A696H-A697H | 42646-42647 | V2(V23) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A698H-A699H | 42648-42649 | V2(V23) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A69AH-A69BH | 42650-42651 | V2(V23) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A69CH-A69DH | 42652-42653 | V2(V23) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A69EH-A69FH | 42654-42655 | V2(V23) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A6A0H-A6A1H | 42656-42657 | V2(V23) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A6A2H-A6A3H | 42658-42659 | V2(V23) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A6A4H-A6A5H | 42660-42661 | V2(V23) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A6A6H-A6A7H | 42662-42663 | V2(V23) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A6A8H-A6A9H | 42664-42665 | V2(V23) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A6AAH-A6ABH | 42666-42667 | V2(V23) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A6ACH-A6ADH | 42668-42669 | V2(V23) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A6AEH-A6AFH | 42670-42671 | V2(V23) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A6B0H-A6B1H | 42672-42673 | V2(V23) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A6B2H-A6B3H | 42674-42675 | V2(V23) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A6B4H-A6B5H | 42676-42677 | V2(V23) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A6B6H-A6B7H | 42678-42679 | V2(V23) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A6B8H-A6B9H | 42680-42681 | V2(V23) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A6BAH-A6BBH | 42682-42683 | V2(V23) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A6BCH-A6BDH | 42684-42685 | V2(V23) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A6BEH-A6BFH | 42686-42687 | V2(V23) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A6C0H-A6C1H | 42688-42689 | V2(V23) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A6C2H-A6C3H | 42690-42691 | V2(V23) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A6C4H-A6C5H | 42692-42693 | V2(V23) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A6C6H-A6C7H | 42694-42695 | V2(V23) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A6C8H-A6C9H | 42696-42697 | V2(V23) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A6CAH-A6CBH | 42698-42699 | V2(V23) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A6CCH-A6CDH | 42700-42701 | V2(V23) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A6CEH-A6CFH | 42702-42703 | V2(V23) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A6D0H-A6D1H | 42704-42705 | V2(V23) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A6D2H-A6D3H | 42706-42707 | V2(V23) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A6D4H-A6D5H | 42708-42709 | V2(V23) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A6D6H-A6D7H | 42710-42711 | V2(V23) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A6D8H-A6D9H | 42712-42713 | V2(V23) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A6DAH-A6DBH | 42714-42715 | V2(V23) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A6DCH-A6DDH | 42716-42717 | V2(V23) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A6DEH-A6DFH | 42718-42719 | V2(V23) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A6E0H-A6E1H | 42720-42721 | V2(V23) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A6E2H-A6E3H | 42722-42723 | V2(V23) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
V3(V31)
A6E4H | 42724 | V3(V31) 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A6E5H | 42725 | V3(V31) 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A6E6H | 42726 | V3(V31) 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A6E7H | 42727 | V3(V31) 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6E8H | 42728 | V3(V31) 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6E9H | 42729 | V3(V31) 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6EAH | 42730 | V3(V31) 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6EBH | 42731 | V3(V31) 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6ECH | 42732 | V3(V31) 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6EDH | 42733 | V3(V31) 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6EEH | 42734 | V3(V31) 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6EFH | 42735 | V3(V31) 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F0H | 42736 | V3(V31) 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F1H | 42737 | V3(V31) 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F2H | 42738 | V3(V31) 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F3H | 42739 | V3(V31) 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F4H | 42740 | V3(V31) 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F5H | 42741 | V3(V31) 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F6H | 42742 | V3(V31) 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F7H | 42743 | V3(V31) 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F8H | 42744 | V3(V31) 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A6F9H | 42745 | V3(V31) 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FAH | 42746 | V3(V31) 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FBH | 42747 | V3(V31) 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FCH | 42748 | V3(V31) 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FDH | 42749 | V3(V31) 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FEH | 42750 | V3(V31) 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A6FFH | 42751 | V3(V31) 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A700H | 42752 | V3(V31) 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A701H | 42753 | V3(V31) 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A702H | 42754 | V3(V31) 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A703H | 42755 | V3(V31) 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A704H | 42756 | V3(V31) 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A705H | 42757 | V3(V31) 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A706H | 42758 | V3(V31) 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A707H | 42759 | V3(V31) 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A708H | 42760 | V3(V31) 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A709H | 42761 | V3(V31) 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A70AH | 42762 | V3(V31) 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A70BH | 42763 | V3(V31) 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A70CH | 42764 | V3(V31) 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A70DH | 42765 | V3(V31) 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A70EH | 42766 | V3(V31) 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A70FH | 42767 | V3(V31) 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A710H | 42768 | V3(V31) 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A711H | 42769 | V3(V31) 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A712H | 42770 | V3(V31) 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A713H | 42771 | V3(V31) 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A714H | 42772 | V3(V31) 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A715H | 42773 | V3(V31) 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A716H | 42774 | V3(V31) 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A717H | 42775 | V3(V31) 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A718H | 42776 | V3(V31) 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A719H | 42777 | V3(V31) 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71AH | 42778 | V3(V31) 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71BH | 42779 | V3(V31) 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71CH | 42780 | V3(V31) 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71DH | 42781 | V3(V31) 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71EH | 42782 | V3(V31) 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A71FH | 42783 | V3(V31) 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A720H | 42784 | V3(V31) 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A721H | 42785 | V3(V31) 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A722H | 42786 | V3(V31) 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A723H | 42787 | RESERVED |  | Word | R
A724H-A725H | 42788-42789 | V3(V31) 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A726H-A727H | 42790-42791 | V3(V31) 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A728H-A729H | 42792-42793 | V3(V31) 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A72AH-A72BH | 42794-42795 | V3(V31) 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A72CH-A72DH | 42796-42797 | V3(V31) 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A72EH-A72FH | 42798-42799 | V3(V31) 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A730H-A731H | 42800-42801 | V3(V31) 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A732H-A733H | 42802-42803 | V3(V31) 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A734H-A735H | 42804-42805 | V3(V31) 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A736H-A737H | 42806-42807 | V3(V31) 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A738H-A739H | 42808-42809 | V3(V31) 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A73AH-A73BH | 42810-42811 | V3(V31) 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A73CH-A73DH | 42812-42813 | V3(V31) 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A73EH-A73FH | 42814-42815 | V3(V31) 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A740H-A741H | 42816-42817 | V3(V31) 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A742H-A743H | 42818-42819 | V3(V31) 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A744H-A745H | 42820-42821 | V3(V31) 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A746H-A747H | 42822-42823 | V3(V31) 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A748H-A749H | 42824-42825 | V3(V31) 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A74AH-A74BH | 42826-42827 | V3(V31) 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A74CH-A74DH | 42828-42829 | V3(V31) 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A74EH-A74FH | 42830-42831 | V3(V31) 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A750H-A751H | 42832-42833 | V3(V31) 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A752H-A753H | 42834-42835 | V3(V31) 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A754H-A755H | 42836-42837 | V3(V31) 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A756H-A757H | 42838-42839 | V3(V31) 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A758H-A759H | 42840-42841 | V3(V31) 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A75AH-A75BH | 42842-42843 | V3(V31) 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A75CH-A75DH | 42844-42845 | V3(V31) 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A75EH-A75FH | 42846-42847 | V3(V31) 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A760H-A761H | 42848-42849 | V3(V31) 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A762H-A763H | 42850-42851 | V3(V31) 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A764H-A765H | 42852-42853 | V3(V31) 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A766H-A767H | 42854-42855 | V3(V31) 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A768H-A769H | 42856-42857 | V3(V31) 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A76AH-A76BH | 42858-42859 | V3(V31) 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A76CH-A76DH | 42860-42861 | V3(V31) 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A76EH-A76FH | 42862-42863 | V3(V31) 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A770H-A771H | 42864-42865 | V3(V31) 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A772H-A773H | 42866-42867 | V3(V31) 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A774H-A775H | 42868-42869 | V3(V31) 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A776H-A777H | 42870-42871 | V3(V31) 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A778H-A779H | 42872-42873 | V3(V31) 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A77AH-A77BH | 42874-42875 | V3(V31) 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A77CH-A77DH | 42876-42877 | V3(V31) 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A77EH-A77FH | 42878-42879 | V3(V31) 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A780H-A781H | 42880-42881 | V3(V31) 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A782H-A783H | 42882-42883 | V3(V31) 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A784H-A785H | 42884-42885 | V3(V31) 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A786H-A787H | 42886-42887 | V3(V31) 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A788H-A789H | 42888-42889 | V3(V31) 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A78AH-A78BH | 42890-42891 | V3(V31) 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A78CH-A78DH | 42892-42893 | V3(V31) 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A78EH-A78FH | 42894-42895 | V3(V31) 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A790H-A791H | 42896-42897 | V3(V31) 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A792H-A793H | 42898-42899 | V3(V31) 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A794H-A795H | 42900-42901 | V3(V31) 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A796H-A797H | 42902-42903 | V3(V31) 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A798H-A799H | 42904-42905 | V3(V31) 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A79AH-A79BH | 42906-42907 | V3(V31) 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A79CH-A79DH | 42908-42909 | V3(V31) 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A79EH-A79FH | 42910-42911 | V3(V31) 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A7A0H-A7A1H | 42912-42913 | V3(V31) 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase A Current
A7A2H | 42914 | I1 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A3H | 42915 | I1 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A4H | 42916 | I1 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A5H | 42917 | I1 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A6H | 42918 | I1 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A7H | 42919 | I1 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A8H | 42920 | I1 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7A9H | 42921 | I1 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7AAH | 42922 | I1 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7ABH | 42923 | I1 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7ACH | 42924 | I1 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7ADH | 42925 | I1 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7AEH | 42926 | I1 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7AFH | 42927 | I1 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B0H | 42928 | I1 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B1H | 42929 | I1 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B2H | 42930 | I1 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B3H | 42931 | I1 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B4H | 42932 | I1 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B5H | 42933 | I1 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B6H | 42934 | I1 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B7H | 42935 | I1 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B8H | 42936 | I1 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7B9H | 42937 | I1 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BAH | 42938 | I1 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BBH | 42939 | I1 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BCH | 42940 | I1 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BDH | 42941 | I1 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BEH | 42942 | I1 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7BFH | 42943 | I1 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C0H | 42944 | I1 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C1H | 42945 | I1 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C2H | 42946 | I1 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C3H | 42947 | I1 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C4H | 42948 | I1 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C5H | 42949 | I1 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C6H | 42950 | I1 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C7H | 42951 | I1 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C8H | 42952 | I1 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7C9H | 42953 | I1 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CAH | 42954 | I1 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CBH | 42955 | I1 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CCH | 42956 | I1 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CDH | 42957 | I1 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CEH | 42958 | I1 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7CFH | 42959 | I1 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D0H | 42960 | I1 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D1H | 42961 | I1 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D2H | 42962 | I1 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D3H | 42963 | I1 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D4H | 42964 | I1 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D5H | 42965 | I1 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D6H | 42966 | I1 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D7H | 42967 | I1 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D8H | 42968 | I1 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7D9H | 42969 | I1 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DAH | 42970 | I1 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DBH | 42971 | I1 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DCH | 42972 | I1 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DDH | 42973 | I1 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DEH | 42974 | I1 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A7DFH | 42975 | I1 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7E0H | 42976 | I1 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A7E1H | 42977 | RESERVED |  | Word | R
A7E2H-A7E3H | 42978-42979 | I1 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A7E4H-A7E5H | 42980-42981 | I1 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A7E6H-A7E7H | 42982-42983 | I1 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A7E8H-A7E9H | 42984-42985 | I1 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A7EAH-A7EBH | 42986-42987 | I1 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A7ECH-A7EDH | 42988-42989 | I1 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A7EEH-A7EFH | 42990-42991 | I1 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A7F0H-A7F1H | 42992-42993 | I1 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A7F2H-A7F3H | 42994-42995 | I1 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A7F4H-A7F5H | 42996-42997 | I1 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A7F6H-A7F7H | 42998-42999 | I1 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A7F8H-A7F9H | 43000-43001 | I1 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A7FAH-A7FBH | 43002-43003 | I1 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A7FCH-A7FDH | 43004-43005 | I1 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A7FEH-A7FFH | 43006-43007 | I1 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A800H-A801H | 43008-43009 | I1 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A802H-A803H | 43010-43011 | I1 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A804H-A805H | 43012-43013 | I1 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A806H-A807H | 43014-43015 | I1 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A808H-A809H | 43016-43017 | I1 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A80AH-A80BH | 43018-43019 | I1 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A80CH-A80DH | 43020-43021 | I1 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A80EH-A80FH | 43022-43023 | I1 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A810H-A811H | 43024-43025 | I1 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A812H-A813H | 43026-43027 | I1 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A814H-A815H | 43028-43029 | I1 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A816H-A817H | 43030-43031 | I1 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A818H-A819H | 43032-43033 | I1 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A81AH-A81BH | 43034-43035 | I1 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A81CH-A81DH | 43036-43037 | I1 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A81EH-A81FH | 43038-43039 | I1 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A820H-A821H | 43040-43041 | I1 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A822H-A823H | 43042-43043 | I1 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A824H-A825H | 43044-43045 | I1 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A826H-A827H | 43046-43047 | I1 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A828H-A829H | 43048-43049 | I1 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A82AH-A82BH | 43050-43051 | I1 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A82CH-A82DH | 43052-43053 | I1 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A82EH-A82FH | 43054-43055 | I1 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A830H-A831H | 43056-43057 | I1 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A832H-A833H | 43058-43059 | I1 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A834H-A835H | 43060-43061 | I1 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A836H-A837H | 43062-43063 | I1 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A838H-A839H | 43064-43065 | I1 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A83AH-A83BH | 43066-43067 | I1 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A83CH-A83DH | 43068-43069 | I1 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A83EH-A83FH | 43070-43071 | I1 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A840H-A841H | 43072-43073 | I1 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A842H-A843H | 43074-43075 | I1 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A844H-A845H | 43076-43077 | I1 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A846H-A847H | 43078-43079 | I1 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A848H-A849H | 43080-43081 | I1 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A84AH-A84BH | 43082-43083 | I1 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A84CH-A84DH | 43084-43085 | I1 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A84EH-A84FH | 43086-43087 | I1 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A850H-A851H | 43088-43089 | I1 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A852H-A853H | 43090-43091 | I1 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A854H-A855H | 43092-43093 | I1 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A856H-A857H | 43094-43095 | I1 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A858H-A859H | 43096-43097 | I1 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A85AH-A85BH | 43098-43099 | I1 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A85CH-A85DH | 43100-43101 | I1 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A85EH-A85FH | 43102-43103 | I1 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase B Current
A860H | 43104 | I2 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A861H | 43105 | I2 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A862H | 43106 | I2 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A863H | 43107 | I2 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A864H | 43108 | I2 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A865H | 43109 | I2 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A866H | 43110 | I2 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A867H | 43111 | I2 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A868H | 43112 | I2 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A869H | 43113 | I2 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86AH | 43114 | I2 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86BH | 43115 | I2 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86CH | 43116 | I2 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86DH | 43117 | I2 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86EH | 43118 | I2 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A86FH | 43119 | I2 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A870H | 43120 | I2 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A871H | 43121 | I2 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A872H | 43122 | I2 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A873H | 43123 | I2 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A874H | 43124 | I2 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A875H | 43125 | I2 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A876H | 43126 | I2 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A877H | 43127 | I2 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A878H | 43128 | I2 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A879H | 43129 | I2 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A87AH | 43130 | I2 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A87BH | 43131 | I2 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A87CH | 43132 | I2 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A87DH | 43133 | I2 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A87EH | 43134 | I2 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A87FH | 43135 | I2 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A880H | 43136 | I2 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A881H | 43137 | I2 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A882H | 43138 | I2 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A883H | 43139 | I2 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A884H | 43140 | I2 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A885H | 43141 | I2 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A886H | 43142 | I2 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A887H | 43143 | I2 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A888H | 43144 | I2 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A889H | 43145 | I2 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A88AH | 43146 | I2 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A88BH | 43147 | I2 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A88CH | 43148 | I2 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A88DH | 43149 | I2 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A88EH | 43150 | I2 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A88FH | 43151 | I2 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A890H | 43152 | I2 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A891H | 43153 | I2 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A892H | 43154 | I2 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A893H | 43155 | I2 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A894H | 43156 | I2 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A895H | 43157 | I2 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A896H | 43158 | I2 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A897H | 43159 | I2 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A898H | 43160 | I2 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A899H | 43161 | I2 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A89AH | 43162 | I2 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A89BH | 43163 | I2 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A89CH | 43164 | I2 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A89DH | 43165 | I2 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A89EH | 43166 | I2 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A89FH | 43167 | RESERVED |  | Word | R
A8A0H-A8A1H | 43168-43169 | I2 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A8A2H-A8A3H | 43170-43171 | I2 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A8A4H-A8A5H | 43172-43173 | I2 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A8A6H-A8A7H | 43174-43175 | I2 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A8A8H-A8A9H | 43176-43177 | I2 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A8AAH-A8ABH | 43178-43179 | I2 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A8ACH-A8ADH | 43180-43181 | I2 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A8AEH-A8AFH | 43182-43183 | I2 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A8B0H-A8B1H | 43184-43185 | I2 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A8B2H-A8B3H | 43186-43187 | I2 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A8B4H-A8B5H | 43188-43189 | I2 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A8B6H-A8B7H | 43190-43191 | I2 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A8B8H-A8B9H | 43192-43193 | I2 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A8BAH-A8BBH | 43194-43195 | I2 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A8BCH-A8BDH | 43196-43197 | I2 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A8BEH-A8BFH | 43198-43199 | I2 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A8C0H-A8C1H | 43200-43201 | I2 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A8C2H-A8C3H | 43202-43203 | I2 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A8C4H-A8C5H | 43204-43205 | I2 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A8C6H-A8C7H | 43206-43207 | I2 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A8C8H-A8C9H | 43208-43209 | I2 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A8CAH-A8CBH | 43210-43211 | I2 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A8CCH-A8CDH | 43212-43213 | I2 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A8CEH-A8CFH | 43214-43215 | I2 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A8D0H-A8D1H | 43216-43217 | I2 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A8D2H-A8D3H | 43218-43219 | I2 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A8D4H-A8D5H | 43220-43221 | I2 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A8D6H-A8D7H | 43222-43223 | I2 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A8D8H-A8D9H | 43224-43225 | I2 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A8DAH-A8DBH | 43226-43227 | I2 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A8DCH-A8DDH | 43228-43229 | I2 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A8DEH-A8DFH | 43230-43231 | I2 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A8E0H-A8E1H | 43232-43233 | I2 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A8E2H-A8E3H | 43234-43235 | I2 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A8E4H-A8E5H | 43236-43237 | I2 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A8E6H-A8E7H | 43238-43239 | I2 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A8E8H-A8E9H | 43240-43241 | I2 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A8EAH-A8EBH | 43242-43243 | I2 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A8ECH-A8EDH | 43244-43245 | I2 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A8EEH-A8EFH | 43246-43247 | I2 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A8F0H-A8F1H | 43248-43249 | I2 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A8F2H-A8F3H | 43250-43251 | I2 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A8F4H-A8F5H | 43252-43253 | I2 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A8F6H-A8F7H | 43254-43255 | I2 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A8F8H-A8F9H | 43256-43257 | I2 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A8FAH-A8FBH | 43258-43259 | I2 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A8FCH-A8FDH | 43260-43261 | I2 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A8FEH-A8FFH | 43262-43263 | I2 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A900H-A901H | 43264-43265 | I2 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A902H-A903H | 43266-43267 | I2 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A904H-A905H | 43268-43269 | I2 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A906H-A907H | 43270-43271 | I2 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A908H-A909H | 43272-43273 | I2 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A90AH-A90BH | 43274-43275 | I2 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A90CH-A90DH | 43276-43277 | I2 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A90EH-A90FH | 43278-43279 | I2 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A910H-A911H | 43280-43281 | I2 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A912H-A913H | 43282-43283 | I2 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A914H-A915H | 43284-43285 | I2 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A916H-A917H | 43286-43287 | I2 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A918H-A919H | 43288-43289 | I2 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A91AH-A91BH | 43290-43291 | I2 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A91CH-A91DH | 43292-43293 | I2 63rd Harmonic Amplitude | THD= Rx/100 | Float | R
Phase C Current
A91EH | 43294 | I3 1st Harmonic Amplitude % | THD= Rx/100 | Word | R
A91FH | 43295 | I3 2nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A920H | 43296 | I3 3rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A921H | 43297 | I3 4th Harmonic Amplitude % | THD= Rx/100 | Word | R
A922H | 43298 | I3 5th Harmonic Amplitude % | THD= Rx/100 | Word | R
A923H | 43299 | I3 6th Harmonic Amplitude % | THD= Rx/100 | Word | R
A924H | 43300 | I3 7th Harmonic Amplitude % | THD= Rx/100 | Word | R
A925H | 43301 | I3 8th Harmonic Amplitude % | THD= Rx/100 | Word | R
A926H | 43302 | I3 9th Harmonic Amplitude % | THD= Rx/100 | Word | R
A927H | 43303 | I3 10th Harmonic Amplitude % | THD= Rx/100 | Word | R
A928H | 43304 | I3 11th Harmonic Amplitude % | THD= Rx/100 | Word | R
A929H | 43305 | I3 12th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92AH | 43306 | I3 13th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92BH | 43307 | I3 14th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92CH | 43308 | I3 15th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92DH | 43309 | I3 16th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92EH | 43310 | I3 17th Harmonic Amplitude % | THD= Rx/100 | Word | R
A92FH | 43311 | I3 18th Harmonic Amplitude % | THD= Rx/100 | Word | R
A930H | 43312 | I3 19th Harmonic Amplitude % | THD= Rx/100 | Word | R
A931H | 43313 | I3 20th Harmonic Amplitude % | THD= Rx/100 | Word | R
A932H | 43314 | I3 21st Harmonic Amplitude % | THD= Rx/100 | Word | R
A933H | 43315 | I3 22nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A934H | 43316 | I3 23rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A935H | 43317 | I3 24th Harmonic Amplitude % | THD= Rx/100 | Word | R
A936H | 43318 | I3 25th Harmonic Amplitude % | THD= Rx/100 | Word | R
A937H | 43319 | I3 26th Harmonic Amplitude % | THD= Rx/100 | Word | R
A938H | 43320 | I3 27th Harmonic Amplitude % | THD= Rx/100 | Word | R
A939H | 43321 | I3 28th Harmonic Amplitude % | THD= Rx/100 | Word | R
A93AH | 43322 | I3 29th Harmonic Amplitude % | THD= Rx/100 | Word | R
A93BH | 43323 | I3 30th Harmonic Amplitude % | THD= Rx/100 | Word | R
A93CH | 43324 | I3 31st Harmonic Amplitude % | THD= Rx/100 | Word | R
A93DH | 43325 | I3 32nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A93EH | 43326 | I3 33rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A93FH | 43327 | I3 34th Harmonic Amplitude % | THD= Rx/100 | Word | R
A940H | 43328 | I3 35th Harmonic Amplitude % | THD= Rx/100 | Word | R
A941H | 43329 | I3 36th Harmonic Amplitude % | THD= Rx/100 | Word | R
A942H | 43330 | I3 37th Harmonic Amplitude % | THD= Rx/100 | Word | R
A943H | 43331 | I3 38th Harmonic Amplitude % | THD= Rx/100 | Word | R
A944H | 43332 | I3 39th Harmonic Amplitude % | THD= Rx/100 | Word | R
A945H | 43333 | I3 40th Harmonic Amplitude % | THD= Rx/100 | Word | R
A946H | 43334 | I3 41st Harmonic Amplitude % | THD= Rx/100 | Word | R
A947H | 43335 | I3 42nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A948H | 43336 | I3 43rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A949H | 43337 | I3 44th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94AH | 43338 | I3 45th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94BH | 43339 | I3 46th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94CH | 43340 | I3 47th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94DH | 43341 | I3 48th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94EH | 43342 | I3 49th Harmonic Amplitude % | THD= Rx/100 | Word | R
A94FH | 43343 | I3 50th Harmonic Amplitude % | THD= Rx/100 | Word | R
A950H | 43344 | I3 51st Harmonic Amplitude % | THD= Rx/100 | Word | R
A951H | 43345 | I3 52nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A952H | 43346 | I3 53rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A953H | 43347 | I3 54th Harmonic Amplitude % | THD= Rx/100 | Word | R
A954H | 43348 | I3 55th Harmonic Amplitude % | THD= Rx/100 | Word | R
A955H | 43349 | I3 56th Harmonic Amplitude % | THD= Rx/100 | Word | R
A956H | 43350 | I3 57th Harmonic Amplitude % | THD= Rx/100 | Word | R
A957H | 43351 | I3 58th Harmonic Amplitude % | THD= Rx/100 | Word | R
A958H | 43352 | I3 59th Harmonic Amplitude % | THD= Rx/100 | Word | R
A959H | 43353 | I3 60th Harmonic Amplitude % | THD= Rx/100 | Word | R
A95AH | 43354 | I3 61st Harmonic Amplitude % | THD= Rx/100 | Word | R
A95BH | 43355 | I3 62nd Harmonic Amplitude % | THD= Rx/100 | Word | R
A95CH | 43356 | I3 63rd Harmonic Amplitude % | THD= Rx/100 | Word | R
A95DH | 43357 | RESERVED |  | Word | R
A95EH-A95FH | 43358-43359 | I3 1st Harmonic Amplitude | THD= Rx/100 | Float | R
A960H-A961H | 43360-43361 | I3 2nd Harmonic Amplitude | THD= Rx/100 | Float | R
A962H-A963H | 43362-43363 | I3 3rd Harmonic Amplitude | THD= Rx/100 | Float | R
A964H-A965H | 43364-43365 | I3 4th Harmonic Amplitude | THD= Rx/100 | Float | R
A966H-A967H | 43366-43367 | I3 5th Harmonic Amplitude | THD= Rx/100 | Float | R
A968H-A969H | 43368-43369 | I3 6th Harmonic Amplitude | THD= Rx/100 | Float | R
A96AH-A96BH | 43370-43371 | I3 7th Harmonic Amplitude | THD= Rx/100 | Float | R
A96CH-A96DH | 43372-43373 | I3 8th Harmonic Amplitude | THD= Rx/100 | Float | R
A96EH-A96FH | 43374-43375 | I3 9th Harmonic Amplitude | THD= Rx/100 | Float | R
A970H-A971H | 43376-43377 | I3 10th Harmonic Amplitude | THD= Rx/100 | Float | R
A972H-A973H | 43378-43379 | I3 11th Harmonic Amplitude | THD= Rx/100 | Float | R
A974H-A975H | 43380-43381 | I3 12th Harmonic Amplitude | THD= Rx/100 | Float | R
A976H-A977H | 43382-43383 | I3 13th Harmonic Amplitude | THD= Rx/100 | Float | R
A978H-A979H | 43384-43385 | I3 14th Harmonic Amplitude | THD= Rx/100 | Float | R
A97AH-A97BH | 43386-43387 | I3 15th Harmonic Amplitude | THD= Rx/100 | Float | R
A97CH-A97DH | 43388-43389 | I3 16th Harmonic Amplitude | THD= Rx/100 | Float | R
A97EH-A97FH | 43390-43391 | I3 17th Harmonic Amplitude | THD= Rx/100 | Float | R
A980H-A981H | 43392-43393 | I3 18th Harmonic Amplitude | THD= Rx/100 | Float | R
A982H-A983H | 43394-43395 | I3 19th Harmonic Amplitude | THD= Rx/100 | Float | R
A984H-A985H | 43396-43397 | I3 20th Harmonic Amplitude | THD= Rx/100 | Float | R
A986H-A987H | 43398-43399 | I3 21st Harmonic Amplitude | THD= Rx/100 | Float | R
A988H-A989H | 43400-43401 | I3 22nd Harmonic Amplitude | THD= Rx/100 | Float | R
A98AH-A98BH | 43402-43403 | I3 23rd Harmonic Amplitude | THD= Rx/100 | Float | R
A98CH-A98DH | 43404-43405 | I3 24th Harmonic Amplitude | THD= Rx/100 | Float | R
A98EH-A98FH | 43406-43407 | I3 25th Harmonic Amplitude | THD= Rx/100 | Float | R
A990H-A991H | 43408-43409 | I3 26th Harmonic Amplitude | THD= Rx/100 | Float | R
A992H-A993H | 43410-43411 | I3 27th Harmonic Amplitude | THD= Rx/100 | Float | R
A994H-A995H | 43412-43413 | I3 28th Harmonic Amplitude | THD= Rx/100 | Float | R
A996H-A997H | 43414-43415 | I3 29th Harmonic Amplitude | THD= Rx/100 | Float | R
A998H-A999H | 43416-43417 | I3 30th Harmonic Amplitude | THD= Rx/100 | Float | R
A99AH-A99BH | 43418-43419 | I3 31st Harmonic Amplitude | THD= Rx/100 | Float | R
A99CH-A99DH | 43420-43421 | I3 32nd Harmonic Amplitude | THD= Rx/100 | Float | R
A99EH-A99FH | 43422-43423 | I3 33rd Harmonic Amplitude | THD= Rx/100 | Float | R
A9A0H-A9A1H | 43424-43425 | I3 34th Harmonic Amplitude | THD= Rx/100 | Float | R
A9A2H-A9A3H | 43426-43427 | I3 35th Harmonic Amplitude | THD= Rx/100 | Float | R
A9A4H-A9A5H | 43428-43429 | I3 36th Harmonic Amplitude | THD= Rx/100 | Float | R
A9A6H-A9A7H | 43430-43431 | I3 37th Harmonic Amplitude | THD= Rx/100 | Float | R
A9A8H-A9A9H | 43432-43433 | I3 38th Harmonic Amplitude | THD= Rx/100 | Float | R
A9AAH-A9ABH | 43434-43435 | I3 39th Harmonic Amplitude | THD= Rx/100 | Float | R
A9ACH-A9ADH | 43436-43437 | I3 40th Harmonic Amplitude | THD= Rx/100 | Float | R
A9AEH-A9AFH | 43438-43439 | I3 41st Harmonic Amplitude | THD= Rx/100 | Float | R
A9B0H-A9B1H | 43440-43441 | I3 42nd Harmonic Amplitude | THD= Rx/100 | Float | R
A9B2H-A9B3H | 43442-43443 | I3 43rd Harmonic Amplitude | THD= Rx/100 | Float | R
A9B4H-A9B5H | 43444-43445 | I3 44th Harmonic Amplitude | THD= Rx/100 | Float | R
A9B6H-A9B7H | 43446-43447 | I3 45th Harmonic Amplitude | THD= Rx/100 | Float | R
A9B8H-A9B9H | 43448-43449 | I3 46th Harmonic Amplitude | THD= Rx/100 | Float | R
A9BAH-A9BBH | 43450-43451 | I3 47th Harmonic Amplitude | THD= Rx/100 | Float | R
A9BCH-A9BDH | 43452-43453 | I3 48th Harmonic Amplitude | THD= Rx/100 | Float | R
A9BEH-A9BFH | 43454-43455 | I3 49th Harmonic Amplitude | THD= Rx/100 | Float | R
A9C0H-A9C1H | 43456-43457 | I3 50th Harmonic Amplitude | THD= Rx/100 | Float | R
A9C2H-A9C3H | 43458-43459 | I3 51st Harmonic Amplitude | THD= Rx/100 | Float | R
A9C4H-A9C5H | 43460-43461 | I3 52nd Harmonic Amplitude | THD= Rx/100 | Float | R
A9C6H-A9C7H | 43462-43463 | I3 53rd Harmonic Amplitude | THD= Rx/100 | Float | R
A9C8H-A9C9H | 43464-43465 | I3 54th Harmonic Amplitude | THD= Rx/100 | Float | R
A9CAH-A9CBH | 43466-43467 | I3 55th Harmonic Amplitude | THD= Rx/100 | Float | R
A9CCH-A9CDH | 43468-43469 | I3 56th Harmonic Amplitude | THD= Rx/100 | Float | R
A9CEH-A9CFH | 43470-43471 | I3 57th Harmonic Amplitude | THD= Rx/100 | Float | R
A9D0H-A9D1H | 43472-43473 | I3 58th Harmonic Amplitude | THD= Rx/100 | Float | R
A9D2H-A9D3H | 43474-43475 | I3 59th Harmonic Amplitude | THD= Rx/100 | Float | R
A9D4H-A9D5H | 43476-43477 | I3 60th Harmonic Amplitude | THD= Rx/100 | Float | R
A9D6H-A9D7H | 43478-43479 | I3 61st Harmonic Amplitude | THD= Rx/100 | Float | R
A9D8H-A9D9H | 43480-43481 | I3 62nd Harmonic Amplitude | THD= Rx/100 | Float | R
A9DAH-A9DBH | 43482-43483 | I3 63rd Harmonic Amplitude | THD= Rx/100 | Float | R