## Acuvim II V3
BACnet Points List Acuvim II V3
Firmware v6.39. List generated 2026-10-05 from firmware source.
ID | Name | Object Description | Object Type | Units
Real-time metering (AI 1-39)
AI 1 | Freq_rms | Frequency | analog-input | hertz (27)
AI 2 | Ua_rms | Phase A Voltage | analog-input | volts (5)
AI 3 | Ub_rms | Phase B Voltage | analog-input | volts (5)
AI 4 | Uc_rms | Phase C Voltage | analog-input | volts (5)
AI 5 | Uavg_rms | Average Phase Voltage | analog-input | volts (5)
AI 6 | Uab_rms | Line Voltage AB | analog-input | volts (5)
AI 7 | Ubc_rms | Line Voltage BC | analog-input | volts (5)
AI 8 | Uca_rms | Line Voltage CA | analog-input | volts (5)
AI 9 | Ulavg_rms | Average Line Voltage | analog-input | volts (5)
AI 10 | Ia_rms | Phase A Current | analog-input | amperes (3)
AI 11 | Ib_rms | Phase B Current | analog-input | amperes (3)
AI 12 | Ic_rms | Phase C Current | analog-input | amperes (3)
AI 13 | Iavg_rms | Average Current | analog-input | amperes (3)
AI 14 | In_rms | Neutral Current | analog-input | amperes (3)
AI 15 | Pa_rms | Phase A Active Power | analog-input | kilowatts (48)
AI 16 | Pb_rms | Phase B Active Power | analog-input | kilowatts (48)
AI 17 | Pc_rms | Phase C Active Power | analog-input | kilowatts (48)
AI 18 | P_rms | Total Active Power | analog-input | kilowatts (48)
AI 19 | Qa_rms | Phase A Reactive Power | analog-input | kilovolt-amperes-reactive (51)
AI 20 | Qb_rms | Phase B Reactive Power | analog-input | kilovolt-amperes-reactive (51)
AI 21 | Qc_rms | Phase C Reactive Power | analog-input | kilovolt-amperes-reactive (51)
AI 22 | Q_rms | Total Reactive Power | analog-input | kilovolt-amperes-reactive (51)
AI 23 | Sa_rms | Phase A Apparent Power | analog-input | kilovolt-amperes (9)
AI 24 | Sb_rms | Phase B Apparent Power | analog-input | kilovolt-amperes (9)
AI 25 | Sc_rms | Phase C Apparent Power | analog-input | kilovolt-amperes (9)
AI 26 | S_rms | Total Apparent Power | analog-input | kilovolt-amperes (9)
AI 27 | PFa_rms | Phase A Power Factor | analog-input | power-factor (15)
AI 28 | PFb_rms | Phase B Power Factor | analog-input | power-factor (15)
AI 29 | PFc_rms | Phase C Power Factor | analog-input | power-factor (15)
AI 30 | PF_rms | Total Power Factor | analog-input | power-factor (15)
AI 31 | U_unbl | Voltage Unbalance Factor | analog-input | no-units (95)
AI 32 | I_unbl | Current Unbalance Factor | analog-input | no-units (95)
AI 33 | Rlc_val | Load Type (82:Resistive load 76:Inductive load 67:Capacitive load) | analog-input | no-units (95)
AI 34 | P_dema | Active Power Demand | analog-input | kilowatts (48)
AI 35 | Q_dema | Reactive Power Demand | analog-input | kilovolt-amperes-reactive (51)
AI 36 | S_dema | Apparent Power Demand | analog-input | kilovolt-amperes (9)
AI 37 | Ia_dema | Phase A Current Demand | analog-input | amperes (3)
AI 38 | Ib_dema | Phase B Current Demand | analog-input | amperes (3)
AI 39 | Ic_dema | Phase C Current Demand | analog-input | amperes (3)
Energy (AI 40-63)
AI 40 | Active_Energy_Imp | Import Active Energy | analog-input | kilowatt-hours (19)
AI 41 | Active_Energy_Exp | Export Active Energy | analog-input | kilowatt-hours (19)
AI 42 | Reactive_Energy_Imp | Import Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 43 | Reactive_Energy_Exp | Export Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 44 | Active_Energy_Total | Active Energy Total | analog-input | kilowatt-hours (19)
AI 45 | Active_Energy_Net | Active Energy Net | analog-input | kilowatt-hours (19)
AI 46 | Reactive_Energy_Total | Reactive Energy Total | analog-input | kilovolt-ampere-hours-reactive (158)
AI 47 | Reactive_Energy_Net | Reactive Energy Net | analog-input | kilovolt-ampere-hours-reactive (158)
AI 48 | Apparent_Energy | Apparent Energy | analog-input | kilovolt-ampere-hours (157)
AI 49 | Active_Energy_Imp_A | Phase A Import Active Energy | analog-input | kilowatt-hours (19)
AI 50 | Active_Energy_Exp_A | Phase A Export Active Energy | analog-input | kilowatt-hours (19)
AI 51 | Active_Energy_Imp_B | Phase B Import Active Energy | analog-input | kilowatt-hours (19)
AI 52 | Active_Energy_Exp_B | Phase B Export Active Energy | analog-input | kilowatt-hours (19)
AI 53 | Active_Energy_Imp_C | Phase C Import Active Energy | analog-input | kilowatt-hours (19)
AI 54 | Active_Energy_Exp_C | Phase C Export Active Energy | analog-input | kilowatt-hours (19)
AI 55 | Reactive_Energy_Imp_A | Phase A Import Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 56 | Reactive_Energy_Exp_A | Phase A Export Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 57 | Reactive_Energy_Imp_B | Phase B Import Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 58 | Reactive_Energy_Exp_B | Phase B Export Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 59 | Reactive_Energy_Imp_C | Phase C Import Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 60 | Reactive_Energy_Exp_C | Phase C Export Reactive Energy | analog-input | kilovolt-ampere-hours-reactive (158)
AI 61 | Apparent_Energy_A | Phase A Apparent Energy | analog-input | kilovolt-ampere-hours (157)
AI 62 | Apparent_Energy_B | Phase B Apparent Energy | analog-input | kilovolt-ampere-hours (157)
AI 63 | Apparent_Energy_C | Phase C Apparent Energy | analog-input | kilovolt-ampere-hours (157)
THD (AI 64-71)
AI 64 | V1_thd | Voltage 1 THD | analog-input | volts (5)
AI 65 | V2_thd | Voltage 2 THD | analog-input | volts (5)
AI 66 | V3_thd | Voltage 3 THD | analog-input | volts (5)
AI 67 | V_thd | Average Voltage THD | analog-input | volts (5)
AI 68 | I1_thd | Current 1 THD | analog-input | amperes (3)
AI 69 | I2_thd | Current 2 THD | analog-input | amperes (3)
AI 70 | I3_thd | Current 3 THD | analog-input | amperes (3)
AI 71 | I_thd | Average Current THD | analog-input | amperes (3)
AXM-IO3 analog inputs (AI 72-75)
AI 72 | IO31_ai1 | IO31 Analog Input 1 | analog-input | no-units (95)
AI 73 | IO31_ai2 | IO31 Analog Input 2 | analog-input | no-units (95)
AI 74 | IO32_ai1 | IO32 Analog Input 1 | analog-input | no-units (95)
AI 75 | IO32_ai2 | IO32 Analog Input 2 | analog-input | no-units (95)
AXM-IO pulse counters (AI 76-103)
AI 76 | IO11_pc1 | IO11 Pulse Counter 1 | analog-input | no-units (95)
AI 77 | IO11_pc2 | IO11 Pulse Counter 2 | analog-input | no-units (95)
AI 78 | IO11_pc3 | IO11 Pulse Counter 3 | analog-input | no-units (95)
AI 79 | IO11_pc4 | IO11 Pulse Counter 4 | analog-input | no-units (95)
AI 80 | IO11_pc5 | IO11 Pulse Counter 5 | analog-input | no-units (95)
AI 81 | IO11_pc6 | IO11 Pulse Counter 6 | analog-input | no-units (95)
AI 82 | IO21_pc1 | IO21 Pulse Counter 1 | analog-input | no-units (95)
AI 83 | IO21_pc2 | IO21 Pulse Counter 2 | analog-input | no-units (95)
AI 84 | IO21_pc3 | IO21 Pulse Counter 3 | analog-input | no-units (95)
AI 85 | IO21_pc4 | IO21 Pulse Counter 4 | analog-input | no-units (95)
AI 86 | IO31_pc1 | IO31 Pulse Counter 1 | analog-input | no-units (95)
AI 87 | IO31_pc2 | IO31 Pulse Counter 2 | analog-input | no-units (95)
AI 88 | IO31_pc3 | IO31 Pulse Counter 3 | analog-input | no-units (95)
AI 89 | IO31_pc4 | IO31 Pulse Counter 4 | analog-input | no-units (95)
AI 90 | IO12_pc1 | IO12 Pulse Counter 1 | analog-input | no-units (95)
AI 91 | IO12_pc2 | IO12 Pulse Counter 2 | analog-input | no-units (95)
AI 92 | IO12_pc3 | IO12 Pulse Counter 3 | analog-input | no-units (95)
AI 93 | IO12_pc4 | IO12 Pulse Counter 4 | analog-input | no-units (95)
AI 94 | IO12_pc5 | IO12 Pulse Counter 5 | analog-input | no-units (95)
AI 95 | IO12_pc6 | IO12 Pulse Counter 6 | analog-input | no-units (95)
AI 96 | IO22_pc1 | IO22 Pulse Counter 1 | analog-input | no-units (95)
AI 97 | IO22_pc2 | IO22 Pulse Counter 2 | analog-input | no-units (95)
AI 98 | IO22_pc3 | IO22 Pulse Counter 3 | analog-input | no-units (95)
AI 99 | IO22_pc4 | IO22 Pulse Counter 4 | analog-input | no-units (95)
AI 100 | IO32_pc1 | IO32 Pulse Counter 1 | analog-input | no-units (95)
AI 101 | IO32_pc2 | IO32 Pulse Counter 2 | analog-input | no-units (95)
AI 102 | IO32_pc3 | IO32 Pulse Counter 3 | analog-input | no-units (95)
AI 103 | IO32_pc4 | IO32 Pulse Counter 4 | analog-input | no-units (95)
AXM-IO digital inputs (BI 1-28)
BI 1 | IO11_di1 | IO11 Digital Input 1 | binary-input | no-units (95)
BI 2 | IO11_di2 | IO11 Digital Input 2 | binary-input | no-units (95)
BI 3 | IO11_di3 | IO11 Digital Input 3 | binary-input | no-units (95)
BI 4 | IO11_di4 | IO11 Digital Input 4 | binary-input | no-units (95)
BI 5 | IO11_di5 | IO11 Digital Input 5 | binary-input | no-units (95)
BI 6 | IO11_di6 | IO11 Digital Input 6 | binary-input | no-units (95)
BI 7 | IO21_di1 | IO21 Digital Input 1 | binary-input | no-units (95)
BI 8 | IO21_di2 | IO21 Digital Input 2 | binary-input | no-units (95)
BI 9 | IO21_di3 | IO21 Digital Input 3 | binary-input | no-units (95)
BI 10 | IO21_di4 | IO21 Digital Input 4 | binary-input | no-units (95)
BI 11 | IO31_di1 | IO31 Digital Input 1 | binary-input | no-units (95)
BI 12 | IO31_di2 | IO31 Digital Input 2 | binary-input | no-units (95)
BI 13 | IO31_di3 | IO31 Digital Input 3 | binary-input | no-units (95)
BI 14 | IO31_di4 | IO31 Digital Input 4 | binary-input | no-units (95)
BI 15 | IO12_di1 | IO12 Digital Input 1 | binary-input | no-units (95)
BI 16 | IO12_di2 | IO12 Digital Input 2 | binary-input | no-units (95)
BI 17 | IO12_di3 | IO12 Digital Input 3 | binary-input | no-units (95)
BI 18 | IO12_di4 | IO12 Digital Input 4 | binary-input | no-units (95)
BI 19 | IO12_di5 | IO12 Digital Input 5 | binary-input | no-units (95)
BI 20 | IO12_di6 | IO12 Digital Input 6 | binary-input | no-units (95)
BI 21 | IO22_di1 | IO22 Digital Input 1 | binary-input | no-units (95)
BI 22 | IO22_di2 | IO22 Digital Input 2 | binary-input | no-units (95)
BI 23 | IO22_di3 | IO22 Digital Input 3 | binary-input | no-units (95)
BI 24 | IO22_di4 | IO22 Digital Input 4 | binary-input | no-units (95)
BI 25 | IO32_di1 | IO32 Digital Input 1 | binary-input | no-units (95)
BI 26 | IO32_di2 | IO32 Digital Input 2 | binary-input | no-units (95)
BI 27 | IO32_di3 | IO32 Digital Input 3 | binary-input | no-units (95)
BI 28 | IO32_di4 | IO32 Digital Input 4 | binary-input | no-units (95)
Alarm channel status (BI 29-44, added 2026-07-17, A2V3-1379)
BI 29 | AlarmStatus1 | Alarm Channel 1 Status | binary-input | no-units (95)
BI 30 | AlarmStatus2 | Alarm Channel 2 Status | binary-input | no-units (95)
BI 31 | AlarmStatus3 | Alarm Channel 3 Status | binary-input | no-units (95)
BI 32 | AlarmStatus4 | Alarm Channel 4 Status | binary-input | no-units (95)
BI 33 | AlarmStatus5 | Alarm Channel 5 Status | binary-input | no-units (95)
BI 34 | AlarmStatus6 | Alarm Channel 6 Status | binary-input | no-units (95)
BI 35 | AlarmStatus7 | Alarm Channel 7 Status | binary-input | no-units (95)
BI 36 | AlarmStatus8 | Alarm Channel 8 Status | binary-input | no-units (95)
BI 37 | AlarmStatus9 | Alarm Channel 9 Status | binary-input | no-units (95)
BI 38 | AlarmStatus10 | Alarm Channel 10 Status | binary-input | no-units (95)
BI 39 | AlarmStatus11 | Alarm Channel 11 Status | binary-input | no-units (95)
BI 40 | AlarmStatus12 | Alarm Channel 12 Status | binary-input | no-units (95)
BI 41 | AlarmStatus13 | Alarm Channel 13 Status | binary-input | no-units (95)
BI 42 | AlarmStatus14 | Alarm Channel 14 Status | binary-input | no-units (95)
BI 43 | AlarmStatus15 | Alarm Channel 15 Status | binary-input | no-units (95)
BI 44 | AlarmStatus16 | Alarm Channel 16 Status | binary-input | no-units (95)

## Note
Notes
Source:
Acuvim II V3- firmware v6.39 Date :Oct 05, 2026 BACnet Protocol Version: 1 BACnet Protocol Revision: 26 Objects are defined by the parameter mapping and BACnet mapper tables in the firmware database (createParamDefault).
Object counts:
Analog Input: 103 objects (instances 1-103)
Binary Input : 44 objects (instances 1-44)
Availability:
RealTime Objects( Start 1 -End 39 ),Length :39
Energy Objects( Start 40 -End 63 ),Length :24
THD Objects( Start 64 -End 71 ),Length :8
AXM-IO3 analog inputs Objects( Start 72 -End 75 ),Length :4
AXM-IO pulse counters Objects( Start 76 -End 103 ),Length :28
AXM-IO digital inputs Objects( Start 1 -End 28),Length :28
Alarm Channel status Objects( Start 29 -End 44),Length :16
Device Objects Configurable,Length :1